## Project Overview
Project overview
File name: | C:\Users\28417\Desktop\Greybox Wrapup\MLE3Tanks_Openloop.sumo
Report date: | Wednesday, May 19, 2021 1:29:27 PM
Sumo version: | 20~nb201104
Model: | Sumo1
Scenario: | Default scenario
Model Options: | 1-step nitrification/denitrification
Input gas phase concentrations
Skip pH calculations
Simulation from: | Hot start
Stop time: | 1 | weeks
Data interval: | 10 | minutes

## Notes
Project Notes
What to do here?
-Never lose your files again! Keep them attached to your project. Microsoft documents or any other files can be dragged and dropped to the note section. They stay with the project and can be retrieved at any time.
-Adding schematics - copy and paste figures
-Write information regarding the project - it gets saved with it
----------------------------------------------------------------
Project name -
Start date of project -
Engineer name -
Engineer affiliation -
Utility -
----------------------------------------------------------------
Five Steps of Good Modeling Practice Protocol
----------------------------------------------------------------
PROJECT DEFINITION
----------------------------------------------------------------
DATA COLLECTION AND RECONCILIATION
----------------------------------------------------------------
PLANT MODEL SETUP
----------------------------------------------------------------
CALIBRATION AND VALIDATION
-------------------------------------------------------------------------
SIMULATION AND RESULTS INTERPRETATION

## Modified Parameters
Modified parameters
Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
KNHx,NITO,AS | Half-saturation of NHx for NITOs (AS) | 0.5 | g N/m3
Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KNHx,NITO,AS | Half-saturation of NHx for NITOs (AS) | 0.5 | g N/m3
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
Influent - Influent specifications
Symbol | Name | Value | Unit | Comment
TKN | Total Kjeldahl nitrogen (TKN) | 56.5 | g N/m3
Side flow divider - Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 600 | m3/d
Side flow divider2 - Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 36000 | m3/d
CSTR - Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
CSTR - Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 0 | g O2/m3 | List of Set SVs will appear here.
CSTR2 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
CSTR2 - Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 3 | g O2/m3 | List of Set SVs will appear here.
CSTR2 - Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
CSTR2 - Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
CSTR3 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
CSTR3 - Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 3 | g O2/m3 | List of Set SVs will appear here.
CSTR3 - Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.4 | g O2/m3
CSTR3 - Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.4 | g O2/m3
CSTR4 - Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
CSTR4 - Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 3 | g O2/m3 | List of Set SVs will appear here.
CSTR4 - Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.2 | g O2/m3
CSTR4 - Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.2 | g O2/m3

## SRT
SRT
Time | SRT1
d | d
0 | 6.8642
0.0069444 | 6.8641
0.013889 | 6.8639
0.020833 | 6.8637
0.027778 | 6.8635
0.034722 | 6.8633
0.041667 | 6.8632
0.048611 | 6.863
0.055556 | 6.8628
0.0625 | 6.8628
0.069444 | 6.8628
0.076389 | 6.8629
0.083333 | 6.8629
0.090278 | 6.863
0.097222 | 6.8631
0.10417 | 6.8632
0.11111 | 6.8632
0.11806 | 6.8632
0.125 | 6.8632
0.13194 | 6.8632
0.13889 | 6.8631
0.14583 | 6.8632
0.15278 | 6.8632
0.15972 | 6.8633
0.16667 | 6.8633
0.17361 | 6.8634
0.18056 | 6.8634
0.1875 | 6.8633
0.19444 | 6.8632
0.20139 | 6.8631
0.20833 | 6.8631
0.21528 | 6.8631
0.22222 | 6.8632
0.22917 | 6.8633
0.23611 | 6.8634
0.24306 | 6.8635
0.25 | 6.8636
0.25694 | 6.8636
0.26389 | 6.8636
0.27083 | 6.8637
0.27778 | 6.8637
0.28472 | 6.8637
0.29167 | 6.8637
0.29861 | 6.8638
0.30556 | 6.8637
0.3125 | 6.8638
0.31944 | 6.8638
0.32639 | 6.8638
0.33333 | 6.8637
0.34028 | 6.8635
0.34722 | 6.8634
0.35417 | 6.8632
0.36111 | 6.8631
0.36806 | 6.863
0.375 | 6.8629
0.38194 | 6.8628
0.38889 | 6.8628
0.39583 | 6.8628
0.40278 | 6.8628
0.40972 | 6.8629
0.41667 | 6.863
0.42361 | 6.8631
0.43056 | 6.8632
0.4375 | 6.8632
0.44444 | 6.8632
0.45139 | 6.863
0.45833 | 6.8629
0.46528 | 6.8629
0.47222 | 6.863
0.47917 | 6.8631
0.48611 | 6.8633
0.49306 | 6.8635
0.5 | 6.8635
0.50694 | 6.8634
0.51389 | 6.8634
0.52083 | 6.8633
0.52778 | 6.8633
0.53472 | 6.8633
0.54167 | 6.8633
0.54861 | 6.8633
0.55556 | 6.8633
0.5625 | 6.8633
0.56944 | 6.8633
0.57639 | 6.8635
0.58333 | 6.8635
0.59028 | 6.8636
0.59722 | 6.8637
0.60417 | 6.8637
0.61111 | 6.8638
0.61806 | 6.8639
0.625 | 6.8639
0.63194 | 6.8639
0.63889 | 6.8638
0.64583 | 6.8637
0.65278 | 6.8637
0.65972 | 6.8637
0.66667 | 6.8637
0.67361 | 6.8637
0.68056 | 6.8637
0.6875 | 6.8635
0.69444 | 6.8634
0.70139 | 6.8633
0.70833 | 6.8635
0.71528 | 6.8636
0.72222 | 6.8638
0.72917 | 6.8639
0.73611 | 6.8639
0.74306 | 6.8639
0.75 | 6.8639
0.75694 | 6.864
0.76389 | 6.864
0.77083 | 6.864
0.77778 | 6.8638
0.78472 | 6.8636
0.79167 | 6.8636
0.79861 | 6.8636
0.80556 | 6.8637
0.8125 | 6.8639
0.81944 | 6.8638
0.82639 | 6.8637
0.83333 | 6.8636
0.84028 | 6.8634
0.84722 | 6.8634
0.85417 | 6.8633
0.86111 | 6.8632
0.86806 | 6.8632
0.875 | 6.8632
0.88194 | 6.8633
0.88889 | 6.8632
0.89583 | 6.8631
0.90278 | 6.863
0.90972 | 6.863
0.91667 | 6.8631
0.92361 | 6.8633
0.93056 | 6.8633
0.9375 | 6.8633
0.94444 | 6.8633
0.95139 | 6.8635
0.95833 | 6.8636
0.96528 | 6.8637
0.97222 | 6.8637
0.97917 | 6.8636
0.98611 | 6.8635
0.99306 | 6.8634
1 | 6.8634
1.0069 | 6.8634
1.0139 | 6.8633
1.0208 | 6.8633
1.0278 | 6.8632
1.0347 | 6.863
1.0417 | 6.8628
1.0486 | 6.8627
1.0556 | 6.8627
1.0625 | 6.8628
1.0694 | 6.8629
1.0764 | 6.8629
1.0833 | 6.8628
1.0903 | 6.8629
1.0972 | 6.863
1.1042 | 6.863
1.1111 | 6.8632
1.1181 | 6.8634
1.125 | 6.8636
1.1319 | 6.8637
1.1389 | 6.8638
1.1458 | 6.8637
1.1528 | 6.8636
1.1597 | 6.8635
1.1667 | 6.8634
1.1736 | 6.8633
1.1806 | 6.8633
1.1875 | 6.8633
1.1944 | 6.8634
1.2014 | 6.8633
1.2083 | 6.8632
1.2153 | 6.8632
1.2222 | 6.8634
1.2292 | 6.8636
1.2361 | 6.8636
1.2431 | 6.8636
1.25 | 6.8636
1.2569 | 6.8635
1.2639 | 6.8635
1.2708 | 6.8635
1.2778 | 6.8634
1.2847 | 6.8633
1.2917 | 6.8633
1.2986 | 6.8631
1.3056 | 6.8631
1.3125 | 6.8631
1.3194 | 6.8631
1.3264 | 6.8631
1.3333 | 6.8631
1.3403 | 6.8632
1.3472 | 6.8633
1.3542 | 6.8634
1.3611 | 6.8633
1.3681 | 6.8633
1.375 | 6.8633
1.3819 | 6.8634
1.3889 | 6.8634
1.3958 | 6.8635
1.4028 | 6.8635
1.4097 | 6.8635
1.4167 | 6.8634
1.4236 | 6.8634
1.4306 | 6.8634
1.4375 | 6.8635
1.4444 | 6.8637
1.4514 | 6.8639
1.4583 | 6.8639
1.4653 | 6.8639
1.4722 | 6.8638
1.4792 | 6.8636
1.4861 | 6.8634
1.4931 | 6.8632
1.5 | 6.8631
1.5069 | 6.8631
1.5139 | 6.8632
1.5208 | 6.8632
1.5278 | 6.8632
1.5347 | 6.8632
1.5417 | 6.8632
1.5486 | 6.8632
1.5556 | 6.8633
1.5625 | 6.8633
1.5694 | 6.8634
1.5764 | 6.8633
1.5833 | 6.8633
1.5903 | 6.8633
1.5972 | 6.8634
1.6042 | 6.8635
1.6111 | 6.8636
1.6181 | 6.8636
1.625 | 6.8636
1.6319 | 6.8636
1.6389 | 6.8636
1.6458 | 6.8635
1.6528 | 6.8635
1.6597 | 6.8635
1.6667 | 6.8635
1.6736 | 6.8636
1.6806 | 6.8636
1.6875 | 6.8635
1.6944 | 6.8635
1.7014 | 6.8634
1.7083 | 6.8634
1.7153 | 6.8633
1.7222 | 6.8633
1.7292 | 6.8635
1.7361 | 6.8637
1.7431 | 6.8638
1.75 | 6.8638
1.7569 | 6.8638
1.7639 | 6.8638
1.7708 | 6.8638
1.7778 | 6.8637
1.7847 | 6.8637
1.7917 | 6.8636
1.7986 | 6.8635
1.8056 | 6.8635
1.8125 | 6.8636
1.8194 | 6.8636
1.8264 | 6.8637
1.8333 | 6.8637
1.8403 | 6.8636
1.8472 | 6.8637
1.8542 | 6.8638
1.8611 | 6.8639
1.8681 | 6.8638
1.875 | 6.8637
1.8819 | 6.8635
1.8889 | 6.8632
1.8958 | 6.8631
1.9028 | 6.8632
1.9097 | 6.8633
1.9167 | 6.8634
1.9236 | 6.8635
1.9306 | 6.8636
1.9375 | 6.8635
1.9444 | 6.8636
1.9514 | 6.8637
1.9583 | 6.8638
1.9653 | 6.8639
1.9722 | 6.8639
1.9792 | 6.8639
1.9861 | 6.8639
1.9931 | 6.8639
2 | 6.8638
2.0069 | 6.8637
2.0139 | 6.8637
2.0208 | 6.8637
2.0278 | 6.8637
2.0347 | 6.8637
2.0417 | 6.8636
2.0486 | 6.8635
2.0556 | 6.8633
2.0625 | 6.8631
2.0694 | 6.8631
2.0764 | 6.8631
2.0833 | 6.8631
2.0903 | 6.8632
2.0972 | 6.8632
2.1042 | 6.8633
2.1111 | 6.8633
2.1181 | 6.8633
2.125 | 6.8633
2.1319 | 6.8633
2.1389 | 6.8632
2.1458 | 6.8632
2.1528 | 6.8633
2.1597 | 6.8634
2.1667 | 6.8634
2.1736 | 6.8634
2.1806 | 6.8633
2.1875 | 6.8632
2.1944 | 6.8631
2.2014 | 6.8631
2.2083 | 6.8631
2.2153 | 6.8632
2.2222 | 6.8634
2.2292 | 6.8634
2.2361 | 6.8634
2.2431 | 6.8634
2.25 | 6.8633
2.2569 | 6.8632
2.2639 | 6.8631
2.2708 | 6.863
2.2778 | 6.863
2.2847 | 6.863
2.2917 | 6.8631
2.2986 | 6.8631
2.3056 | 6.863
2.3125 | 6.863
2.3194 | 6.863
2.3264 | 6.8629
2.3333 | 6.8629
2.3403 | 6.863
2.3472 | 6.8631
2.3542 | 6.8633
2.3611 | 6.8633
2.3681 | 6.8634
2.375 | 6.8635
2.3819 | 6.8635
2.3889 | 6.8634
2.3958 | 6.8633
2.4028 | 6.8634
2.4097 | 6.8637
2.4167 | 6.8638
2.4236 | 6.8639
2.4306 | 6.8638
2.4375 | 6.8637
2.4444 | 6.8636
2.4514 | 6.8635
2.4583 | 6.8636
2.4653 | 6.8636
2.4722 | 6.8636
2.4792 | 6.8635
2.4861 | 6.8635
2.4931 | 6.8636
2.5 | 6.8636
2.5069 | 6.8637
2.5139 | 6.8636
2.5208 | 6.8636
2.5278 | 6.8637
2.5347 | 6.8637
2.5417 | 6.8637
2.5486 | 6.8636
2.5556 | 6.8636
2.5625 | 6.8635
2.5694 | 6.8634
2.5764 | 6.8633
2.5833 | 6.8632
2.5903 | 6.8632
2.5972 | 6.8633
2.6042 | 6.8632
2.6111 | 6.8632
2.6181 | 6.8632
2.625 | 6.8632
2.6319 | 6.8632
2.6389 | 6.8633
2.6458 | 6.8633
2.6528 | 6.8634
2.6597 | 6.8634
2.6667 | 6.8634
2.6736 | 6.8634
2.6806 | 6.8633
2.6875 | 6.8632
2.6944 | 6.8631
2.7014 | 6.863
2.7083 | 6.863
2.7153 | 6.863
2.7222 | 6.863
2.7292 | 6.8629
2.7361 | 6.8628
2.7431 | 6.8627
2.75 | 6.8627
2.7569 | 6.8628
2.7639 | 6.8629
2.7708 | 6.8629
2.7778 | 6.863
2.7847 | 6.8632
2.7917 | 6.8633
2.7986 | 6.8635
2.8056 | 6.8636
2.8125 | 6.8637
2.8194 | 6.8637
2.8264 | 6.8637
2.8333 | 6.8637
2.8403 | 6.8636
2.8472 | 6.8635
2.8542 | 6.8633
2.8611 | 6.8633
2.8681 | 6.8632
2.875 | 6.8632
2.8819 | 6.8633
2.8889 | 6.8634
2.8958 | 6.8635
2.9028 | 6.8635
2.9097 | 6.8635
2.9167 | 6.8635
2.9236 | 6.8635
2.9306 | 6.8636
2.9375 | 6.8635
2.9444 | 6.8634
2.9514 | 6.8632
2.9583 | 6.8631
2.9653 | 6.863
2.9722 | 6.8629
2.9792 | 6.863
2.9861 | 6.8631
2.9931 | 6.8633
3 | 6.8634
3.0069 | 6.8635
3.0139 | 6.8637
3.0208 | 6.8638
3.0278 | 6.8638
3.0347 | 6.8638
3.0417 | 6.8638
3.0486 | 6.8638
3.0556 | 6.8636
3.0625 | 6.8634
3.0694 | 6.8633
3.0764 | 6.8632
3.0833 | 6.8632
3.0903 | 6.8633
3.0972 | 6.8634
3.1042 | 6.8634
3.1111 | 6.8635
3.1181 | 6.8635
3.125 | 6.8634
3.1319 | 6.8632
3.1389 | 6.8631
3.1458 | 6.8632
3.1528 | 6.8633
3.1597 | 6.8635
3.1667 | 6.8636
3.1736 | 6.8637
3.1806 | 6.8635
3.1875 | 6.8633
3.1944 | 6.8632
3.2014 | 6.8631
3.2083 | 6.8631
3.2153 | 6.8632
3.2222 | 6.8633
3.2292 | 6.8633
3.2361 | 6.8634
3.2431 | 6.8635
3.25 | 6.8635
3.2569 | 6.8635
3.2639 | 6.8635
3.2708 | 6.8634
3.2778 | 6.8634
3.2847 | 6.8635
3.2917 | 6.8636
3.2986 | 6.8637
3.3056 | 6.8638
3.3125 | 6.8638
3.3194 | 6.8637
3.3264 | 6.8636
3.3333 | 6.8635
3.3403 | 6.8634
3.3472 | 6.8634
3.3542 | 6.8635
3.3611 | 6.8636
3.3681 | 6.8636
3.375 | 6.8635
3.3819 | 6.8634
3.3889 | 6.8633
3.3958 | 6.8632
3.4028 | 6.8633
3.4097 | 6.8634
3.4167 | 6.8635
3.4236 | 6.8636
3.4306 | 6.8636
3.4375 | 6.8636
3.4444 | 6.8637
3.4514 | 6.8636
3.4583 | 6.8636
3.4653 | 6.8635
3.4722 | 6.8633
3.4792 | 6.8633
3.4861 | 6.8632
3.4931 | 6.8631
3.5 | 6.8631
3.5069 | 6.8632
3.5139 | 6.8633
3.5208 | 6.8634
3.5278 | 6.8635
3.5347 | 6.8635
3.5417 | 6.8634
3.5486 | 6.8634
3.5556 | 6.8633
3.5625 | 6.8633
3.5694 | 6.8632
3.5764 | 6.8632
3.5833 | 6.8631
3.5903 | 6.863
3.5972 | 6.8629
3.6042 | 6.8629
3.6111 | 6.863
3.6181 | 6.863
3.625 | 6.8631
3.6319 | 6.8633
3.6389 | 6.8634
3.6458 | 6.8636
3.6528 | 6.8636
3.6597 | 6.8635
3.6667 | 6.8632
3.6736 | 6.863
3.6806 | 6.8629
3.6875 | 6.863
3.6944 | 6.8632
3.7014 | 6.8634
3.7083 | 6.8634
3.7153 | 6.8634
3.7222 | 6.8635
3.7292 | 6.8636
3.7361 | 6.8635
3.7431 | 6.8634
3.75 | 6.8633
3.7569 | 6.8633
3.7639 | 6.8633
3.7708 | 6.8633
3.7778 | 6.8633
3.7847 | 6.8633
3.7917 | 6.8633
3.7986 | 6.8632
3.8056 | 6.8633
3.8125 | 6.8633
3.8194 | 6.8633
3.8264 | 6.8632
3.8333 | 6.8632
3.8403 | 6.8632
3.8472 | 6.8632
3.8542 | 6.8631
3.8611 | 6.8629
3.8681 | 6.8629
3.875 | 6.863
3.8819 | 6.8632
3.8889 | 6.8633
3.8958 | 6.8633
3.9028 | 6.8633
3.9097 | 6.8632
3.9167 | 6.8631
3.9236 | 6.8631
3.9306 | 6.8631
3.9375 | 6.8632
3.9444 | 6.8632
3.9514 | 6.8632
3.9583 | 6.8633
3.9653 | 6.8634
3.9722 | 6.8635
3.9792 | 6.8635
3.9861 | 6.8635
3.9931 | 6.8637
4 | 6.8638
4.0069 | 6.8638
4.0139 | 6.8639
4.0208 | 6.8639
4.0278 | 6.8637
4.0347 | 6.8635
4.0417 | 6.8634
4.0486 | 6.8633
4.0556 | 6.8632
4.0625 | 6.8633
4.0694 | 6.8634
4.0764 | 6.8635
4.0833 | 6.8635
4.0903 | 6.8636
4.0972 | 6.8636
4.1042 | 6.8635
4.1111 | 6.8635
4.1181 | 6.8635
4.125 | 6.8634
4.1319 | 6.8633
4.1389 | 6.8633
4.1458 | 6.8633
4.1528 | 6.8632
4.1597 | 6.8631
4.1667 | 6.8629
4.1736 | 6.8628
4.1806 | 6.8627
4.1875 | 6.8627
4.1944 | 6.8627
4.2014 | 6.8627
4.2083 | 6.8628
4.2153 | 6.863
4.2222 | 6.8631
4.2292 | 6.8633
4.2361 | 6.8634
4.2431 | 6.8636
4.25 | 6.8637
4.2569 | 6.8638
4.2639 | 6.8638
4.2708 | 6.8638
4.2778 | 6.8636
4.2847 | 6.8634
4.2917 | 6.8633
4.2986 | 6.8632
4.3056 | 6.8631
4.3125 | 6.8631
4.3194 | 6.8629
4.3264 | 6.8629
4.3333 | 6.863
4.3403 | 6.863
4.3472 | 6.8631
4.3542 | 6.8632
4.3611 | 6.8633
4.3681 | 6.8633
4.375 | 6.8634
4.3819 | 6.8635
4.3889 | 6.8635
4.3958 | 6.8634
4.4028 | 6.8634
4.4097 | 6.8634
4.4167 | 6.8634
4.4236 | 6.8635
4.4306 | 6.8635
4.4375 | 6.8635
4.4444 | 6.8634
4.4514 | 6.8632
4.4583 | 6.863
4.4653 | 6.8631
4.4722 | 6.8631
4.4792 | 6.8631
4.4861 | 6.863
4.4931 | 6.863
4.5 | 6.8629
4.5069 | 6.8629
4.5139 | 6.8629
4.5208 | 6.8629
4.5278 | 6.8628
4.5347 | 6.8628
4.5417 | 6.8629
4.5486 | 6.8631
4.5556 | 6.8631
4.5625 | 6.8631
4.5694 | 6.863
4.5764 | 6.8629
4.5833 | 6.8629
4.5903 | 6.8629
4.5972 | 6.8629
4.6042 | 6.863
4.6111 | 6.863
4.6181 | 6.863
4.625 | 6.863
4.6319 | 6.8632
4.6389 | 6.8633
4.6458 | 6.8633
4.6528 | 6.8634
4.6597 | 6.8634
4.6667 | 6.8635
4.6736 | 6.8637
4.6806 | 6.8637
4.6875 | 6.8638
4.6944 | 6.8638
4.7014 | 6.8638
4.7083 | 6.8638
4.7153 | 6.8639
4.7222 | 6.8638
4.7292 | 6.8637
4.7361 | 6.8637
4.7431 | 6.8636
4.75 | 6.8636
4.7569 | 6.8636
4.7639 | 6.8636
4.7708 | 6.8637
4.7778 | 6.8638
4.7847 | 6.8637
4.7917 | 6.8637
4.7986 | 6.8637
4.8056 | 6.8636
4.8125 | 6.8635
4.8194 | 6.8634
4.8264 | 6.8632
4.8333 | 6.8631
4.8403 | 6.863
4.8472 | 6.863
4.8542 | 6.863
4.8611 | 6.8629
4.8681 | 6.8628
4.875 | 6.8627
4.8819 | 6.8627
4.8889 | 6.8627
4.8958 | 6.8628
4.9028 | 6.8629
4.9097 | 6.8629
4.9167 | 6.8629
4.9236 | 6.863
4.9306 | 6.863
4.9375 | 6.863
4.9444 | 6.863
4.9514 | 6.8632
4.9583 | 6.8634
4.9653 | 6.8635
4.9722 | 6.8637
4.9792 | 6.8638
4.9861 | 6.8638
4.9931 | 6.8637
5 | 6.8635
5.0069 | 6.8635
5.0139 | 6.8634
5.0208 | 6.8634
5.0278 | 6.8634
5.0347 | 6.8635
5.0417 | 6.8636
5.0486 | 6.8638
5.0556 | 6.8638
5.0625 | 6.8638
5.0694 | 6.8637
5.0764 | 6.8636
5.0833 | 6.8635
5.0903 | 6.8635
5.0972 | 6.8636
5.1042 | 6.8637
5.1111 | 6.8638
5.1181 | 6.8638
5.125 | 6.8637
5.1319 | 6.8636
5.1389 | 6.8635
5.1458 | 6.8633
5.1528 | 6.8633
5.1597 | 6.8633
5.1667 | 6.8634
5.1736 | 6.8635
5.1806 | 6.8637
5.1875 | 6.8637
5.1944 | 6.8637
5.2014 | 6.8638
5.2083 | 6.8638
5.2153 | 6.8637
5.2222 | 6.8637
5.2292 | 6.8638
5.2361 | 6.8638
5.2431 | 6.8638
5.25 | 6.8639
5.2569 | 6.8639
5.2639 | 6.8639
5.2708 | 6.8639
5.2778 | 6.8639
5.2847 | 6.8638
5.2917 | 6.8637
5.2986 | 6.8635
5.3056 | 6.8633
5.3125 | 6.8632
5.3194 | 6.8631
5.3264 | 6.8631
5.3333 | 6.8632
5.3403 | 6.8634
5.3472 | 6.8635
5.3542 | 6.8636
5.3611 | 6.8637
5.3681 | 6.8638
5.375 | 6.8639
5.3819 | 6.8639
5.3889 | 6.8638
5.3958 | 6.8637
5.4028 | 6.8636
5.4097 | 6.8634
5.4167 | 6.8633
5.4236 | 6.8633
5.4306 | 6.8634
5.4375 | 6.8635
5.4444 | 6.8636
5.4514 | 6.8637
5.4583 | 6.8637
5.4653 | 6.8636
5.4722 | 6.8636
5.4792 | 6.8635
5.4861 | 6.8634
5.4931 | 6.8633
5.5 | 6.8632
5.5069 | 6.8632
5.5139 | 6.8632
5.5208 | 6.8631
5.5278 | 6.8632
5.5347 | 6.8633
5.5417 | 6.8633
5.5486 | 6.8634
5.5556 | 6.8636
5.5625 | 6.8637
5.5694 | 6.8637
5.5764 | 6.8637
5.5833 | 6.8638
5.5903 | 6.8639
5.5972 | 6.864
5.6042 | 6.864
5.6111 | 6.864
5.6181 | 6.8637
5.625 | 6.8634
5.6319 | 6.8631
5.6389 | 6.8629
5.6458 | 6.863
5.6528 | 6.8632
5.6597 | 6.8633
5.6667 | 6.8632
5.6736 | 6.8632
5.6806 | 6.8631
5.6875 | 6.8632
5.6944 | 6.8634
5.7014 | 6.8634
5.7083 | 6.8634
5.7153 | 6.8634
5.7222 | 6.8633
5.7292 | 6.8632
5.7361 | 6.8631
5.7431 | 6.8631
5.75 | 6.8631
5.7569 | 6.8631
5.7639 | 6.8632
5.7708 | 6.8632
5.7778 | 6.8632
5.7847 | 6.8632
5.7917 | 6.8632
5.7986 | 6.8633
5.8056 | 6.8633
5.8125 | 6.8634
5.8194 | 6.8634
5.8264 | 6.8634
5.8333 | 6.8632
5.8403 | 6.8631
5.8472 | 6.863
5.8542 | 6.863
5.8611 | 6.8631
5.8681 | 6.8631
5.875 | 6.8632
5.8819 | 6.8631
5.8889 | 6.8629
5.8958 | 6.8629
5.9028 | 6.863
5.9097 | 6.8631
5.9167 | 6.8632
5.9236 | 6.8633
5.9306 | 6.8634
5.9375 | 6.8634
5.9444 | 6.8634
5.9514 | 6.8634
5.9583 | 6.8635
5.9653 | 6.8636
5.9722 | 6.8635
5.9792 | 6.8634
5.9861 | 6.8633
5.9931 | 6.8633
6 | 6.8635
6.0069 | 6.8637
6.0139 | 6.8638
6.0208 | 6.8639
6.0278 | 6.8639
6.0347 | 6.8639
6.0417 | 6.8637
6.0486 | 6.8635
6.0556 | 6.8633
6.0625 | 6.8631
6.0694 | 6.8629
6.0764 | 6.8627
6.0833 | 6.8626
6.0903 | 6.8626
6.0972 | 6.8625
6.1042 | 6.8626
6.1111 | 6.8627
6.1181 | 6.8629
6.125 | 6.863
6.1319 | 6.863
6.1389 | 6.8631
6.1458 | 6.8631
6.1528 | 6.8632
6.1597 | 6.8632
6.1667 | 6.8631
6.1736 | 6.863
6.1806 | 6.863
6.1875 | 6.8629
6.1944 | 6.8628
6.2014 | 6.8628
6.2083 | 6.8629
6.2153 | 6.863
6.2222 | 6.8631
6.2292 | 6.8631
6.2361 | 6.8633
6.2431 | 6.8634
6.25 | 6.8635
6.2569 | 6.8636
6.2639 | 6.8637
6.2708 | 6.8637
6.2778 | 6.8638
6.2847 | 6.8639
6.2917 | 6.8639
6.2986 | 6.8639
6.3056 | 6.8638
6.3125 | 6.8636
6.3194 | 6.8634
6.3264 | 6.8633
6.3333 | 6.8633
6.3403 | 6.8634
6.3472 | 6.8634
6.3542 | 6.8634
6.3611 | 6.8635
6.3681 | 6.8635
6.375 | 6.8634
6.3819 | 6.8634
6.3889 | 6.8634
6.3958 | 6.8634
6.4028 | 6.8634
6.4097 | 6.8634
6.4167 | 6.8634
6.4236 | 6.8634
6.4306 | 6.8634
6.4375 | 6.8634
6.4444 | 6.8634
6.4514 | 6.8632
6.4583 | 6.8631
6.4653 | 6.8631
6.4722 | 6.8632
6.4792 | 6.8631
6.4861 | 6.863
6.4931 | 6.8629
6.5 | 6.8629
6.5069 | 6.8629
6.5139 | 6.8631
6.5208 | 6.8633
6.5278 | 6.8634
6.5347 | 6.8634
6.5417 | 6.8634
6.5486 | 6.8633
6.5556 | 6.8632
6.5625 | 6.8632
6.5694 | 6.8632
6.5764 | 6.8631
6.5833 | 6.8631
6.5903 | 6.8631
6.5972 | 6.8631
6.6042 | 6.863
6.6111 | 6.8629
6.6181 | 6.8629
6.625 | 6.863
6.6319 | 6.863
6.6389 | 6.863
6.6458 | 6.863
6.6528 | 6.8629
6.6597 | 6.8629
6.6667 | 6.863
6.6736 | 6.8631
6.6806 | 6.8632
6.6875 | 6.8633
6.6944 | 6.8633
6.7014 | 6.8633
6.7083 | 6.8633
6.7153 | 6.8633
6.7222 | 6.8634
6.7292 | 6.8634
6.7361 | 6.8634
6.7431 | 6.8635
6.75 | 6.8635
6.7569 | 6.8635
6.7639 | 6.8636
6.7708 | 6.8637
6.7778 | 6.8637
6.7847 | 6.8635
6.7917 | 6.8633
6.7986 | 6.8631
6.8056 | 6.8629
6.8125 | 6.8628
6.8194 | 6.8628
6.8264 | 6.8627
6.8333 | 6.8627
6.8403 | 6.8627
6.8472 | 6.8627
6.8542 | 6.8626
6.8611 | 6.8627
6.8681 | 6.8629
6.875 | 6.8631
6.8819 | 6.8633
6.8889 | 6.8635
6.8958 | 6.8636
6.9028 | 6.8635
6.9097 | 6.8635
6.9167 | 6.8635
6.9236 | 6.8635
6.9306 | 6.8635
6.9375 | 6.8635
6.9444 | 6.8635
6.9514 | 6.8635
6.9583 | 6.8636
6.9653 | 6.8637
6.9722 | 6.8638
6.9792 | 6.8639
6.9861 | 6.8639
6.9931 | 6.8638
7 | 6.8636
6.8625
6.8642
6.8634
0.00030167

## InputD
InputD
Time | Flow rate (Pipe5) | Flow rate (Pipe12) | Flow rate (Pipe14) | Flow rate (Pipe2)
d | m3/d | m3/d | m3/d | m3/d
0 | 82873.0581 | 23400 | 36000 | 23473.0581
0.0069444 | 82873.0581 | 23400 | 36000 | 23473.0581
0.013889 | 82873.0581 | 23400 | 36000 | 23473.0581
0.020833 | 82873.0581 | 23400 | 36000 | 23473.0581
0.027778 | 82873.0581 | 23400 | 36000 | 23473.0581
0.034722 | 82873.0581 | 23400 | 36000 | 23473.0581
0.041667 | 82873.0581 | 23400 | 36000 | 23473.0581
0.048611 | 82873.0581 | 23400 | 36000 | 23473.0581
0.055556 | 82873.0581 | 23400 | 36000 | 23473.0581
0.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
0.069444 | 82873.0581 | 23400 | 36000 | 23473.0581
0.076389 | 82873.0581 | 23400 | 36000 | 23473.0581
0.083333 | 82873.0581 | 23400 | 36000 | 23473.0581
0.090278 | 82873.0581 | 23400 | 36000 | 23473.0581
0.097222 | 82873.0581 | 23400 | 36000 | 23473.0581
0.10417 | 82873.0581 | 23400 | 36000 | 23473.0581
0.11111 | 82873.0581 | 23400 | 36000 | 23473.0581
0.11806 | 82873.0581 | 23400 | 36000 | 23473.0581
0.125 | 82873.0581 | 23400 | 36000 | 23473.0581
0.13194 | 82873.0581 | 23400 | 36000 | 23473.0581
0.13889 | 82873.0581 | 23400 | 36000 | 23473.0581
0.14583 | 82873.0581 | 23400 | 36000 | 23473.0581
0.15278 | 82873.0581 | 23400 | 36000 | 23473.0581
0.15972 | 82873.0581 | 23400 | 36000 | 23473.0581
0.16667 | 82873.0581 | 23400 | 36000 | 23473.0581
0.17361 | 82873.0581 | 23400 | 36000 | 23473.0581
0.18056 | 82873.0581 | 23400 | 36000 | 23473.0581
0.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
0.19444 | 82873.0581 | 23400 | 36000 | 23473.0581
0.20139 | 82873.0581 | 23400 | 36000 | 23473.0581
0.20833 | 82873.0581 | 23400 | 36000 | 23473.0581
0.21528 | 82873.0581 | 23400 | 36000 | 23473.0581
0.22222 | 82873.0581 | 23400 | 36000 | 23473.0581
0.22917 | 82873.0581 | 23400 | 36000 | 23473.0581
0.23611 | 82873.0581 | 23400 | 36000 | 23473.0581
0.24306 | 82873.0581 | 23400 | 36000 | 23473.0581
0.25 | 82873.0581 | 23400 | 36000 | 23473.0581
0.25694 | 82873.0581 | 23400 | 36000 | 23473.0581
0.26389 | 82873.0581 | 23400 | 36000 | 23473.0581
0.27083 | 82873.0581 | 23400 | 36000 | 23473.0581
0.27778 | 82873.0581 | 23400 | 36000 | 23473.0581
0.28472 | 82873.0581 | 23400 | 36000 | 23473.0581
0.29167 | 82873.0581 | 23400 | 36000 | 23473.0581
0.29861 | 82873.0581 | 23400 | 36000 | 23473.0581
0.30556 | 82873.0581 | 23400 | 36000 | 23473.0581
0.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
0.31944 | 82873.0581 | 23400 | 36000 | 23473.0581
0.32639 | 82873.0581 | 23400 | 36000 | 23473.0581
0.33333 | 82873.0581 | 23400 | 36000 | 23473.0581
0.34028 | 82873.0581 | 23400 | 36000 | 23473.0581
0.34722 | 82873.0581 | 23400 | 36000 | 23473.0581
0.35417 | 82873.0581 | 23400 | 36000 | 23473.0581
0.36111 | 82873.0581 | 23400 | 36000 | 23473.0581
0.36806 | 82873.0581 | 23400 | 36000 | 23473.0581
0.375 | 82873.0581 | 23400 | 36000 | 23473.0581
0.38194 | 82873.0581 | 23400 | 36000 | 23473.0581
0.38889 | 82873.0581 | 23400 | 36000 | 23473.0581
0.39583 | 82873.0581 | 23400 | 36000 | 23473.0581
0.40278 | 82873.0581 | 23400 | 36000 | 23473.0581
0.40972 | 82873.0581 | 23400 | 36000 | 23473.0581
0.41667 | 82873.0581 | 23400 | 36000 | 23473.0581
0.42361 | 82873.0581 | 23400 | 36000 | 23473.0581
0.43056 | 82873.0581 | 23400 | 36000 | 23473.0581
0.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
0.44444 | 82873.0581 | 23400 | 36000 | 23473.0581
0.45139 | 82873.0581 | 23400 | 36000 | 23473.0581
0.45833 | 82873.0581 | 23400 | 36000 | 23473.0581
0.46528 | 82873.0581 | 23400 | 36000 | 23473.0581
0.47222 | 82873.0581 | 23400 | 36000 | 23473.0581
0.47917 | 82873.0581 | 23400 | 36000 | 23473.0581
0.48611 | 82873.0581 | 23400 | 36000 | 23473.0581
0.49306 | 82873.0581 | 23400 | 36000 | 23473.0581
0.5 | 82873.0581 | 23400 | 36000 | 23473.0581
0.50694 | 82873.0581 | 23400 | 36000 | 23473.0581
0.51389 | 82873.0581 | 23400 | 36000 | 23473.0581
0.52083 | 82873.0581 | 23400 | 36000 | 23473.0581
0.52778 | 82873.0581 | 23400 | 36000 | 23473.0581
0.53472 | 82873.0581 | 23400 | 36000 | 23473.0581
0.54167 | 82873.0581 | 23400 | 36000 | 23473.0581
0.54861 | 82873.0581 | 23400 | 36000 | 23473.0581
0.55556 | 82873.0581 | 23400 | 36000 | 23473.0581
0.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
0.56944 | 82873.0581 | 23400 | 36000 | 23473.0581
0.57639 | 82873.0581 | 23400 | 36000 | 23473.0581
0.58333 | 82873.0581 | 23400 | 36000 | 23473.0581
0.59028 | 82873.0581 | 23400 | 36000 | 23473.0581
0.59722 | 82873.0581 | 23400 | 36000 | 23473.0581
0.60417 | 82873.0581 | 23400 | 36000 | 23473.0581
0.61111 | 82873.0581 | 23400 | 36000 | 23473.0581
0.61806 | 82873.0581 | 23400 | 36000 | 23473.0581
0.625 | 82873.0581 | 23400 | 36000 | 23473.0581
0.63194 | 82873.0581 | 23400 | 36000 | 23473.0581
0.63889 | 82873.0581 | 23400 | 36000 | 23473.0581
0.64583 | 82873.0581 | 23400 | 36000 | 23473.0581
0.65278 | 82873.0581 | 23400 | 36000 | 23473.0581
0.65972 | 82873.0581 | 23400 | 36000 | 23473.0581
0.66667 | 82873.0581 | 23400 | 36000 | 23473.0581
0.67361 | 82873.0581 | 23400 | 36000 | 23473.0581
0.68056 | 82873.0581 | 23400 | 36000 | 23473.0581
0.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
0.69444 | 82873.0581 | 23400 | 36000 | 23473.0581
0.70139 | 82873.0581 | 23400 | 36000 | 23473.0581
0.70833 | 82873.0581 | 23400 | 36000 | 23473.0581
0.71528 | 82873.0581 | 23400 | 36000 | 23473.0581
0.72222 | 82873.0581 | 23400 | 36000 | 23473.0581
0.72917 | 82873.0581 | 23400 | 36000 | 23473.0581
0.73611 | 82873.0581 | 23400 | 36000 | 23473.0581
0.74306 | 82873.0581 | 23400 | 36000 | 23473.0581
0.75 | 82873.0581 | 23400 | 36000 | 23473.0581
0.75694 | 82873.0581 | 23400 | 36000 | 23473.0581
0.76389 | 82873.0581 | 23400 | 36000 | 23473.0581
0.77083 | 82873.0581 | 23400 | 36000 | 23473.0581
0.77778 | 82873.0581 | 23400 | 36000 | 23473.0581
0.78472 | 82873.0581 | 23400 | 36000 | 23473.0581
0.79167 | 82873.0581 | 23400 | 36000 | 23473.0581
0.79861 | 82873.0581 | 23400 | 36000 | 23473.0581
0.80556 | 82873.0581 | 23400 | 36000 | 23473.0581
0.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
0.81944 | 82873.0581 | 23400 | 36000 | 23473.0581
0.82639 | 82873.0581 | 23400 | 36000 | 23473.0581
0.83333 | 82873.0581 | 23400 | 36000 | 23473.0581
0.84028 | 82873.0581 | 23400 | 36000 | 23473.0581
0.84722 | 82873.0581 | 23400 | 36000 | 23473.0581
0.85417 | 82873.0581 | 23400 | 36000 | 23473.0581
0.86111 | 82873.0581 | 23400 | 36000 | 23473.0581
0.86806 | 82873.0581 | 23400 | 36000 | 23473.0581
0.875 | 82873.0581 | 23400 | 36000 | 23473.0581
0.88194 | 82873.0581 | 23400 | 36000 | 23473.0581
0.88889 | 82873.0581 | 23400 | 36000 | 23473.0581
0.89583 | 82873.0581 | 23400 | 36000 | 23473.0581
0.90278 | 82873.0581 | 23400 | 36000 | 23473.0581
0.90972 | 82873.0581 | 23400 | 36000 | 23473.0581
0.91667 | 82873.0581 | 23400 | 36000 | 23473.0581
0.92361 | 82873.0581 | 23400 | 36000 | 23473.0581
0.93056 | 82873.0581 | 23400 | 36000 | 23473.0581
0.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
0.94444 | 82873.0581 | 23400 | 36000 | 23473.0581
0.95139 | 82873.0581 | 23400 | 36000 | 23473.0581
0.95833 | 82873.0581 | 23400 | 36000 | 23473.0581
0.96528 | 82873.0581 | 23400 | 36000 | 23473.0581
0.97222 | 82873.0581 | 23400 | 36000 | 23473.0581
0.97917 | 82873.0581 | 23400 | 36000 | 23473.0581
0.98611 | 82873.0581 | 23400 | 36000 | 23473.0581
0.99306 | 82873.0581 | 23400 | 36000 | 23473.0581
1 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0069 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0139 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0208 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0278 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0347 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0417 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0486 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0556 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0694 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0764 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0833 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0903 | 82873.0581 | 23400 | 36000 | 23473.0581
1.0972 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1042 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1111 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1181 | 82873.0581 | 23400 | 36000 | 23473.0581
1.125 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1319 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1389 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1458 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1528 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1597 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1667 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1736 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1806 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
1.1944 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2014 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2083 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2153 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2222 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2292 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2361 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2431 | 82873.0581 | 23400 | 36000 | 23473.0581
1.25 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2569 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2639 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2708 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2778 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2847 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2917 | 82873.0581 | 23400 | 36000 | 23473.0581
1.2986 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3056 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3194 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3264 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3333 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3403 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3472 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3542 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3611 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3681 | 82873.0581 | 23400 | 36000 | 23473.0581
1.375 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3819 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3889 | 82873.0581 | 23400 | 36000 | 23473.0581
1.3958 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4028 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4097 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4167 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4236 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4306 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4444 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4514 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4583 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4653 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4722 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4792 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4861 | 82873.0581 | 23400 | 36000 | 23473.0581
1.4931 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5069 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5139 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5208 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5278 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5347 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5417 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5486 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5556 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5694 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5764 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5833 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5903 | 82873.0581 | 23400 | 36000 | 23473.0581
1.5972 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6042 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6111 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6181 | 82873.0581 | 23400 | 36000 | 23473.0581
1.625 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6319 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6389 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6458 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6528 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6597 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6667 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6736 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6806 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
1.6944 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7014 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7083 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7153 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7222 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7292 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7361 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7431 | 82873.0581 | 23400 | 36000 | 23473.0581
1.75 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7569 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7639 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7708 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7778 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7847 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7917 | 82873.0581 | 23400 | 36000 | 23473.0581
1.7986 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8056 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8194 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8264 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8333 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8403 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8472 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8542 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8611 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8681 | 82873.0581 | 23400 | 36000 | 23473.0581
1.875 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8819 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8889 | 82873.0581 | 23400 | 36000 | 23473.0581
1.8958 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9028 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9097 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9167 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9236 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9306 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9444 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9514 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9583 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9653 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9722 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9792 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9861 | 82873.0581 | 23400 | 36000 | 23473.0581
1.9931 | 82873.0581 | 23400 | 36000 | 23473.0581
2 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0069 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0139 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0208 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0278 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0347 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0417 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0486 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0556 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0694 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0764 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0833 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0903 | 82873.0581 | 23400 | 36000 | 23473.0581
2.0972 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1042 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1111 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1181 | 82873.0581 | 23400 | 36000 | 23473.0581
2.125 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1319 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1389 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1458 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1528 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1597 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1667 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1736 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1806 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
2.1944 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2014 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2083 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2153 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2222 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2292 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2361 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2431 | 82873.0581 | 23400 | 36000 | 23473.0581
2.25 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2569 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2639 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2708 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2778 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2847 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2917 | 82873.0581 | 23400 | 36000 | 23473.0581
2.2986 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3056 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3194 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3264 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3333 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3403 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3472 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3542 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3611 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3681 | 82873.0581 | 23400 | 36000 | 23473.0581
2.375 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3819 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3889 | 82873.0581 | 23400 | 36000 | 23473.0581
2.3958 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4028 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4097 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4167 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4236 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4306 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4444 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4514 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4583 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4653 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4722 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4792 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4861 | 82873.0581 | 23400 | 36000 | 23473.0581
2.4931 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5069 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5139 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5208 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5278 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5347 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5417 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5486 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5556 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5694 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5764 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5833 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5903 | 82873.0581 | 23400 | 36000 | 23473.0581
2.5972 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6042 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6111 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6181 | 82873.0581 | 23400 | 36000 | 23473.0581
2.625 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6319 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6389 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6458 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6528 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6597 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6667 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6736 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6806 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
2.6944 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7014 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7083 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7153 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7222 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7292 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7361 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7431 | 82873.0581 | 23400 | 36000 | 23473.0581
2.75 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7569 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7639 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7708 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7778 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7847 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7917 | 82873.0581 | 23400 | 36000 | 23473.0581
2.7986 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8056 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8194 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8264 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8333 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8403 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8472 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8542 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8611 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8681 | 82873.0581 | 23400 | 36000 | 23473.0581
2.875 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8819 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8889 | 82873.0581 | 23400 | 36000 | 23473.0581
2.8958 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9028 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9097 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9167 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9236 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9306 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9444 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9514 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9583 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9653 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9722 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9792 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9861 | 82873.0581 | 23400 | 36000 | 23473.0581
2.9931 | 82873.0581 | 23400 | 36000 | 23473.0581
3 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0069 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0139 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0208 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0278 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0347 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0417 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0486 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0556 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0694 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0764 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0833 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0903 | 82873.0581 | 23400 | 36000 | 23473.0581
3.0972 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1042 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1111 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1181 | 82873.0581 | 23400 | 36000 | 23473.0581
3.125 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1319 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1389 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1458 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1528 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1597 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1667 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1736 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1806 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
3.1944 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2014 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2083 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2153 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2222 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2292 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2361 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2431 | 82873.0581 | 23400 | 36000 | 23473.0581
3.25 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2569 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2639 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2708 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2778 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2847 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2917 | 82873.0581 | 23400 | 36000 | 23473.0581
3.2986 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3056 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3194 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3264 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3333 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3403 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3472 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3542 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3611 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3681 | 82873.0581 | 23400 | 36000 | 23473.0581
3.375 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3819 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3889 | 82873.0581 | 23400 | 36000 | 23473.0581
3.3958 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4028 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4097 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4167 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4236 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4306 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4444 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4514 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4583 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4653 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4722 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4792 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4861 | 82873.0581 | 23400 | 36000 | 23473.0581
3.4931 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5069 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5139 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5208 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5278 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5347 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5417 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5486 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5556 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5694 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5764 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5833 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5903 | 82873.0581 | 23400 | 36000 | 23473.0581
3.5972 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6042 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6111 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6181 | 82873.0581 | 23400 | 36000 | 23473.0581
3.625 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6319 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6389 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6458 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6528 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6597 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6667 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6736 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6806 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
3.6944 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7014 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7083 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7153 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7222 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7292 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7361 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7431 | 82873.0581 | 23400 | 36000 | 23473.0581
3.75 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7569 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7639 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7708 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7778 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7847 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7917 | 82873.0581 | 23400 | 36000 | 23473.0581
3.7986 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8056 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8194 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8264 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8333 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8403 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8472 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8542 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8611 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8681 | 82873.0581 | 23400 | 36000 | 23473.0581
3.875 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8819 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8889 | 82873.0581 | 23400 | 36000 | 23473.0581
3.8958 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9028 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9097 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9167 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9236 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9306 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9444 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9514 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9583 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9653 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9722 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9792 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9861 | 82873.0581 | 23400 | 36000 | 23473.0581
3.9931 | 82873.0581 | 23400 | 36000 | 23473.0581
4 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0069 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0139 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0208 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0278 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0347 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0417 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0486 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0556 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0694 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0764 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0833 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0903 | 82873.0581 | 23400 | 36000 | 23473.0581
4.0972 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1042 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1111 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1181 | 82873.0581 | 23400 | 36000 | 23473.0581
4.125 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1319 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1389 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1458 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1528 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1597 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1667 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1736 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1806 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
4.1944 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2014 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2083 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2153 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2222 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2292 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2361 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2431 | 82873.0581 | 23400 | 36000 | 23473.0581
4.25 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2569 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2639 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2708 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2778 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2847 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2917 | 82873.0581 | 23400 | 36000 | 23473.0581
4.2986 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3056 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3194 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3264 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3333 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3403 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3472 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3542 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3611 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3681 | 82873.0581 | 23400 | 36000 | 23473.0581
4.375 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3819 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3889 | 82873.0581 | 23400 | 36000 | 23473.0581
4.3958 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4028 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4097 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4167 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4236 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4306 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4444 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4514 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4583 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4653 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4722 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4792 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4861 | 82873.0581 | 23400 | 36000 | 23473.0581
4.4931 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5069 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5139 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5208 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5278 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5347 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5417 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5486 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5556 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5694 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5764 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5833 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5903 | 82873.0581 | 23400 | 36000 | 23473.0581
4.5972 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6042 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6111 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6181 | 82873.0581 | 23400 | 36000 | 23473.0581
4.625 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6319 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6389 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6458 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6528 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6597 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6667 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6736 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6806 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
4.6944 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7014 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7083 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7153 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7222 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7292 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7361 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7431 | 82873.0581 | 23400 | 36000 | 23473.0581
4.75 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7569 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7639 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7708 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7778 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7847 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7917 | 82873.0581 | 23400 | 36000 | 23473.0581
4.7986 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8056 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8194 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8264 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8333 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8403 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8472 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8542 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8611 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8681 | 82873.0581 | 23400 | 36000 | 23473.0581
4.875 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8819 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8889 | 82873.0581 | 23400 | 36000 | 23473.0581
4.8958 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9028 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9097 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9167 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9236 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9306 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9444 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9514 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9583 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9653 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9722 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9792 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9861 | 82873.0581 | 23400 | 36000 | 23473.0581
4.9931 | 82873.0581 | 23400 | 36000 | 23473.0581
5 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0069 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0139 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0208 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0278 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0347 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0417 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0486 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0556 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0694 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0764 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0833 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0903 | 82873.0581 | 23400 | 36000 | 23473.0581
5.0972 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1042 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1111 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1181 | 82873.0581 | 23400 | 36000 | 23473.0581
5.125 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1319 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1389 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1458 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1528 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1597 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1667 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1736 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1806 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
5.1944 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2014 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2083 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2153 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2222 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2292 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2361 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2431 | 82873.0581 | 23400 | 36000 | 23473.0581
5.25 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2569 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2639 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2708 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2778 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2847 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2917 | 82873.0581 | 23400 | 36000 | 23473.0581
5.2986 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3056 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3194 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3264 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3333 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3403 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3472 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3542 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3611 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3681 | 82873.0581 | 23400 | 36000 | 23473.0581
5.375 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3819 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3889 | 82873.0581 | 23400 | 36000 | 23473.0581
5.3958 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4028 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4097 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4167 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4236 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4306 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4444 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4514 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4583 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4653 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4722 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4792 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4861 | 82873.0581 | 23400 | 36000 | 23473.0581
5.4931 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5069 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5139 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5208 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5278 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5347 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5417 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5486 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5556 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5694 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5764 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5833 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5903 | 82873.0581 | 23400 | 36000 | 23473.0581
5.5972 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6042 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6111 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6181 | 82873.0581 | 23400 | 36000 | 23473.0581
5.625 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6319 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6389 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6458 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6528 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6597 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6667 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6736 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6806 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
5.6944 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7014 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7083 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7153 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7222 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7292 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7361 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7431 | 82873.0581 | 23400 | 36000 | 23473.0581
5.75 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7569 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7639 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7708 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7778 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7847 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7917 | 82873.0581 | 23400 | 36000 | 23473.0581
5.7986 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8056 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8194 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8264 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8333 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8403 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8472 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8542 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8611 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8681 | 82873.0581 | 23400 | 36000 | 23473.0581
5.875 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8819 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8889 | 82873.0581 | 23400 | 36000 | 23473.0581
5.8958 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9028 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9097 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9167 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9236 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9306 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9444 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9514 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9583 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9653 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9722 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9792 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9861 | 82873.0581 | 23400 | 36000 | 23473.0581
5.9931 | 82873.0581 | 23400 | 36000 | 23473.0581
6 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0069 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0139 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0208 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0278 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0347 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0417 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0486 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0556 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0625 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0694 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0764 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0833 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0903 | 82873.0581 | 23400 | 36000 | 23473.0581
6.0972 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1042 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1111 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1181 | 82873.0581 | 23400 | 36000 | 23473.0581
6.125 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1319 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1389 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1458 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1528 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1597 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1667 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1736 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1806 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1875 | 82873.0581 | 23400 | 36000 | 23473.0581
6.1944 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2014 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2083 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2153 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2222 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2292 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2361 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2431 | 82873.0581 | 23400 | 36000 | 23473.0581
6.25 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2569 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2639 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2708 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2778 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2847 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2917 | 82873.0581 | 23400 | 36000 | 23473.0581
6.2986 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3056 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3125 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3194 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3264 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3333 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3403 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3472 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3542 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3611 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3681 | 82873.0581 | 23400 | 36000 | 23473.0581
6.375 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3819 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3889 | 82873.0581 | 23400 | 36000 | 23473.0581
6.3958 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4028 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4097 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4167 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4236 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4306 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4375 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4444 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4514 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4583 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4653 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4722 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4792 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4861 | 82873.0581 | 23400 | 36000 | 23473.0581
6.4931 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5069 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5139 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5208 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5278 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5347 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5417 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5486 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5556 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5625 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5694 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5764 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5833 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5903 | 82873.0581 | 23400 | 36000 | 23473.0581
6.5972 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6042 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6111 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6181 | 82873.0581 | 23400 | 36000 | 23473.0581
6.625 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6319 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6389 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6458 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6528 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6597 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6667 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6736 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6806 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6875 | 82873.0581 | 23400 | 36000 | 23473.0581
6.6944 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7014 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7083 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7153 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7222 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7292 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7361 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7431 | 82873.0581 | 23400 | 36000 | 23473.0581
6.75 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7569 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7639 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7708 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7778 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7847 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7917 | 82873.0581 | 23400 | 36000 | 23473.0581
6.7986 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8056 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8125 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8194 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8264 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8333 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8403 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8472 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8542 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8611 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8681 | 82873.0581 | 23400 | 36000 | 23473.0581
6.875 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8819 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8889 | 82873.0581 | 23400 | 36000 | 23473.0581
6.8958 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9028 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9097 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9167 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9236 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9306 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9375 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9444 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9514 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9583 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9653 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9722 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9792 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9861 | 82873.0581 | 23400 | 36000 | 23473.0581
6.9931 | 82873.0581 | 23400 | 36000 | 23473.0581
7 | 82873.0581 | 23400 | 36000 | 23473.0581

## DO
DO
Time | Dissolved oxygen (O2) setpoint (CSTR2) | Dissolved oxygen (O2) setpoint (CSTR3) | Dissolved oxygen (O2) setpoint (CSTR4)
d | g O2/m3 | g O2/m3 | g O2/m3
0 | 2 | 0.5 | 1.4452
0.0069444 | 2 | 0.5 | 1.4452
0.013889 | 0.5 | 0.5 | 2.312
0.020833 | 0.5 | 0.5 | 2.8695
0.027778 | 0.5 | 0.5 | 3
0.034722 | 0.5 | 0.5 | 2.8021
0.041667 | 0.5 | 0.5 | 2.5238
0.048611 | 0.5 | 0.5 | 0.78561
0.055556 | 0.5 | 0.5 | 0.5
0.0625 | 0.64037 | 0.52759 | 0.5
0.069444 | 1.3016 | 0.93222 | 0.5
0.076389 | 1.5848 | 0.8046 | 0.5
0.083333 | 1.7194 | 0.60292 | 0.5
0.090278 | 1.4001 | 0.5 | 1.2184
0.097222 | 1.0763 | 0.5 | 1.9349
0.10417 | 1.1126 | 1.1128 | 1.5477
0.11111 | 1.2801 | 2.67 | 0.83427
0.11806 | 0.7673 | 3 | 0.5
0.125 | 0.5 | 3 | 0.5
0.13194 | 0.5 | 2.0856 | 0.5
0.13889 | 0.98167 | 0.5368 | 0.52335
0.14583 | 2.0382 | 0.5 | 0.93964
0.15278 | 2.9797 | 0.5 | 0.72713
0.15972 | 3 | 0.5 | 0.80631
0.16667 | 3 | 0.5 | 1.2023
0.17361 | 3 | 0.5 | 1.2861
0.18056 | 2.0903 | 0.5 | 0.98448
0.1875 | 0.5 | 0.5 | 0.62943
0.19444 | 0.5 | 0.5 | 0.67116
0.20139 | 0.5 | 0.5 | 1.6757
0.20833 | 0.5 | 0.5 | 3
0.21528 | 1.3723 | 0.5 | 3
0.22222 | 2.2029 | 0.8778 | 3
0.22917 | 2.5724 | 1.1068 | 3
0.23611 | 2.8011 | 1.2825 | 2.738
0.24306 | 2.8086 | 1.9081 | 1.4879
0.25 | 2.3535 | 2.1087 | 0.79548
0.25694 | 1.7106 | 1.6484 | 0.57316
0.26389 | 1.6012 | 1.6569 | 0.7703
0.27083 | 2.4223 | 2.0411 | 0.77351
0.27778 | 3 | 2.5442 | 0.5
0.28472 | 3 | 3 | 0.5
0.29167 | 3 | 3 | 0.5
0.29861 | 2.3632 | 3 | 0.5
0.30556 | 0.80073 | 1.878 | 0.71107
0.3125 | 1.0144 | 1.2641 | 1.7612
0.31944 | 1.6084 | 1.1749 | 2.3374
0.32639 | 1.591 | 1.7604 | 2.0722
0.33333 | 0.83808 | 2.9874 | 1.1117
0.34028 | 0.5 | 3 | 0.5
0.34722 | 0.5 | 2.9095 | 0.5
0.35417 | 0.5 | 1.5402 | 0.5
0.36111 | 0.5 | 1.055 | 0.5
0.36806 | 0.5 | 0.91612 | 0.5
0.375 | 0.5 | 0.88469 | 0.5
0.38194 | 0.5 | 0.5 | 0.5
0.38889 | 0.5 | 0.5 | 1.3651
0.39583 | 0.5 | 0.5 | 2.7672
0.40278 | 0.70736 | 0.5637 | 3
0.40972 | 0.99094 | 3 | 3
0.41667 | 0.87736 | 3 | 2.8247
0.42361 | 1.1439 | 3 | 2.0274
0.43056 | 1.0177 | 3 | 1.5201
0.4375 | 0.5 | 1.6075 | 1.3216
0.44444 | 0.5 | 0.73133 | 1.1143
0.45139 | 0.5 | 0.5 | 0.5
0.45833 | 0.61556 | 0.5 | 0.5
0.46528 | 1.9256 | 0.5 | 0.5
0.47222 | 3 | 1.1659 | 0.5
0.47917 | 3 | 1.6642 | 1.2138
0.48611 | 3 | 1.9319 | 2.3763
0.49306 | 2.0514 | 1.2359 | 2.8688
0.5 | 1.0226 | 0.5 | 2.864
0.50694 | 0.5 | 0.5 | 3
0.51389 | 0.5 | 1.6961 | 2.1872
0.52083 | 1.0485 | 2.4464 | 0.5
0.52778 | 1.5924 | 2.1901 | 0.5
0.53472 | 1.6114 | 1.3811 | 0.5
0.54167 | 2.493 | 0.57582 | 0.5
0.54861 | 3 | 0.5 | 0.5
0.55556 | 3 | 0.50245 | 0.5
0.5625 | 3 | 0.61685 | 0.5
0.56944 | 3 | 0.5 | 0.5
0.57639 | 2.2239 | 0.5385 | 1.7606
0.58333 | 1.4233 | 0.93404 | 2.9749
0.59028 | 1.3367 | 0.8518 | 3
0.59722 | 2.1655 | 0.93147 | 2.7898
0.60417 | 3 | 1.6528 | 2.2823
0.61111 | 3 | 2.1825 | 2.7102
0.61806 | 2.9472 | 1.6811 | 3
0.625 | 2.3117 | 0.5 | 3
0.63194 | 1.919 | 0.5 | 3
0.63889 | 1.9152 | 0.5 | 3
0.64583 | 1.9711 | 0.69962 | 3
0.65278 | 1.5279 | 1.2682 | 3
0.65972 | 1.3876 | 1.5434 | 3
0.66667 | 1.6052 | 1.3116 | 3
0.67361 | 1.5516 | 1.0703 | 2.9558
0.68056 | 1.3072 | 1.9742 | 1.5757
0.6875 | 0.67418 | 2.5297 | 0.5
0.69444 | 0.5 | 2.1397 | 0.5
0.70139 | 0.90652 | 2.2243 | 0.5
0.70833 | 2.0726 | 2.8318 | 2.3215
0.71528 | 3 | 3 | 3
0.72222 | 3 | 3 | 3
0.72917 | 2.5162 | 3 | 3
0.73611 | 1.7403 | 2.6501 | 1.7324
0.74306 | 2.1377 | 2.2984 | 1.0324
0.75 | 3 | 1.9173 | 1.7099
0.75694 | 3 | 1.6678 | 3
0.76389 | 2.6839 | 1.738 | 3
0.77083 | 1.8434 | 1.4393 | 2.6811
0.77778 | 1.3208 | 1.4893 | 0.5
0.78472 | 1.1188 | 2.1931 | 0.5
0.79167 | 1.652 | 2.8602 | 0.5
0.79861 | 2.2633 | 2.9273 | 0.5
0.80556 | 2.7662 | 2.6444 | 1.3563
0.8125 | 3 | 2.1635 | 1.7557
0.81944 | 3 | 1.3402 | 0.62263
0.82639 | 2.3924 | 1.0527 | 0.5
0.83333 | 0.5 | 1.7052 | 0.5
0.84028 | 0.5 | 2.1841 | 0.5
0.84722 | 0.5 | 1.4246 | 1.387
0.85417 | 0.5 | 0.5 | 1.8045
0.86111 | 0.5 | 0.5 | 1.8856
0.86806 | 1.8689 | 0.5 | 2.1599
0.875 | 3 | 0.5 | 2.6355
0.88194 | 2.9208 | 0.5 | 2.5366
0.88889 | 1.3033 | 0.5 | 0.96147
0.89583 | 0.55139 | 0.5 | 0.5
0.90278 | 1.2033 | 0.5 | 0.5
0.90972 | 1.9357 | 0.5 | 0.5
0.91667 | 2.4693 | 0.5 | 2.0758
0.92361 | 2.2864 | 0.5 | 3
0.93056 | 1.2567 | 0.5 | 2.1356
0.9375 | 0.66051 | 1.3054 | 1.0576
0.94444 | 1.1759 | 3 | 1.3265
0.95139 | 2.3087 | 3 | 1.7685
0.95833 | 3 | 2.6652 | 1.918
0.96528 | 3 | 1.227 | 1.7299
0.97222 | 3 | 0.5 | 1.0424
0.97917 | 1.4217 | 0.5 | 0.86016
0.98611 | 0.5 | 0.90845 | 1.1885
0.99306 | 0.5 | 1.5705 | 1.488
1 | 0.5 | 2.2055 | 1.8599
1.0069 | 0.5 | 2.9931 | 2.5712
1.0139 | 0.5 | 2.5097 | 3
1.0208 | 0.5 | 1.5887 | 3
1.0278 | 0.60978 | 0.86842 | 2.4133
1.0347 | 0.5 | 0.5 | 0.64632
1.0417 | 0.5 | 0.5 | 0.5
1.0486 | 0.5 | 0.5 | 0.5
1.0556 | 0.86484 | 0.5 | 0.66611
1.0625 | 1.4488 | 0.5 | 1.5426
1.0694 | 1.2931 | 0.5 | 2.8589
1.0764 | 0.5 | 0.5 | 3
1.0833 | 0.5 | 0.5 | 3
1.0903 | 1.7622 | 0.5 | 3
1.0972 | 3 | 0.5 | 1.4183
1.1042 | 3 | 1.0567 | 0.5
1.1111 | 3 | 2.105 | 0.95087
1.1181 | 2.5154 | 2.2578 | 2.9069
1.125 | 2.096 | 1.7787 | 3
1.1319 | 1.989 | 1.688 | 3
1.1389 | 1.3283 | 2.1248 | 2.542
1.1458 | 0.5 | 2.5747 | 2.3879
1.1528 | 0.5 | 2.4995 | 2.1597
1.1597 | 0.5 | 1.8294 | 1.5691
1.1667 | 0.5 | 0.78494 | 1.3506
1.1736 | 1.2944 | 0.5 | 1.4538
1.1806 | 2.4222 | 0.85922 | 1.8311
1.1875 | 2.839 | 0.9257 | 2.2946
1.1944 | 2.5865 | 0.5 | 1.9512
1.2014 | 2.4129 | 0.5 | 0.60598
1.2083 | 2.4848 | 0.5 | 0.5
1.2153 | 2.5011 | 0.69828 | 0.5
1.2222 | 2.3551 | 2.6138 | 1.3505
1.2292 | 1.5442 | 3 | 1.9517
1.2361 | 0.5 | 3 | 2.2254
1.2431 | 0.5 | 3 | 2.8478
1.25 | 0.5 | 2.5139 | 2.9642
1.2569 | 0.70681 | 2.2732 | 2.7778
1.2639 | 1.0023 | 2.4907 | 3
1.2708 | 0.5 | 2.7327 | 3
1.2778 | 0.5 | 3 | 3
1.2847 | 0.5 | 3 | 3
1.2917 | 0.50152 | 3 | 1.8598
1.2986 | 1.4482 | 1.8734 | 0.5
1.3056 | 2.544 | 0.5 | 0.5
1.3125 | 2.4335 | 0.5 | 0.5
1.3194 | 1.6924 | 0.5 | 0.5
1.3264 | 0.93592 | 0.5 | 1.1617
1.3333 | 0.71334 | 1.1009 | 1.7088
1.3403 | 2.0245 | 0.67837 | 2.5843
1.3472 | 3 | 0.5 | 2.9389
1.3542 | 3 | 0.5 | 1.9982
1.3611 | 2.5889 | 1.2539 | 0.5
1.3681 | 0.67837 | 2.8325 | 0.5
1.375 | 0.5 | 3 | 0.65425
1.3819 | 1.9106 | 3 | 0.8417
1.3889 | 3 | 3 | 0.5
1.3958 | 3 | 2.2012 | 0.5
1.4028 | 3 | 0.5 | 0.5
1.4097 | 3 | 0.5 | 0.5
1.4167 | 2.5296 | 0.5 | 0.5
1.4236 | 1.8157 | 0.5 | 0.5
1.4306 | 1.3343 | 1.9134 | 0.5
1.4375 | 2.1025 | 3 | 1.3487
1.4444 | 3 | 3 | 2.1671
1.4514 | 3 | 3 | 2.2006
1.4583 | 3 | 3 | 1.3681
1.4653 | 3 | 3 | 0.52294
1.4722 | 1.8275 | 2.8355 | 0.5
1.4792 | 0.5 | 0.56163 | 0.50909
1.4861 | 0.5 | 0.5 | 0.5
1.4931 | 0.5 | 0.83053 | 0.5
1.5 | 0.5 | 2.1041 | 0.5
1.5069 | 1.5822 | 2.7083 | 0.5
1.5139 | 2.2391 | 3 | 0.5
1.5208 | 1.7123 | 2.9505 | 0.5
1.5278 | 0.5 | 2.6231 | 0.5
1.5347 | 0.5 | 3 | 0.5
1.5417 | 0.5 | 3 | 0.60769
1.5486 | 0.5 | 2.1138 | 2.2913
1.5556 | 1.5036 | 0.89961 | 3
1.5625 | 2.6148 | 0.5 | 3
1.5694 | 3 | 0.5 | 1.9801
1.5764 | 3 | 0.5 | 0.5
1.5833 | 3 | 1.081 | 0.5
1.5903 | 3 | 2.9979 | 0.5
1.5972 | 3 | 3 | 0.5
1.6042 | 3 | 3 | 0.5
1.6111 | 2.3444 | 2.4401 | 0.5
1.6181 | 1.8768 | 1.0619 | 0.5
1.625 | 1.7106 | 0.5 | 0.55898
1.6319 | 0.92885 | 1.1571 | 1.7911
1.6389 | 0.5 | 2.4103 | 2.065
1.6458 | 0.5 | 3 | 1.2422
1.6528 | 0.80305 | 3 | 1.0275
1.6597 | 1.3845 | 2.8282 | 1.2183
1.6667 | 2.5879 | 1.661 | 1.2862
1.6736 | 2.9436 | 1.3322 | 1.5997
1.6806 | 2.3231 | 1.2884 | 1.3048
1.6875 | 2.1938 | 0.73307 | 0.5
1.6944 | 2.1833 | 1.2439 | 0.5
1.7014 | 1.3242 | 2.2196 | 0.5
1.7083 | 0.55955 | 2.3011 | 0.5
1.7153 | 0.9111 | 2.9109 | 0.5
1.7222 | 1.1916 | 3 | 0.5
1.7292 | 1.5826 | 2.5686 | 2.0098
1.7361 | 2.37 | 2.1761 | 3
1.7431 | 2.4567 | 2.1823 | 3
1.75 | 2.3247 | 1.4032 | 3
1.7569 | 2.9224 | 0.84069 | 3
1.7639 | 3 | 0.68704 | 2.5667
1.7708 | 3 | 0.5 | 2.5292
1.7778 | 3 | 0.5 | 2.1631
1.7847 | 2.6689 | 0.5 | 1.4241
1.7917 | 1.6785 | 0.5 | 1.2909
1.7986 | 1.5431 | 0.5 | 1.6198
1.8056 | 2.233 | 0.5 | 2.1679
1.8125 | 3 | 0.94512 | 2.4941
1.8194 | 3 | 0.76144 | 2.7496
1.8264 | 3 | 0.5 | 2.5514
1.8333 | 3 | 0.5 | 1.7132
1.8403 | 3 | 0.61993 | 1.1745
1.8472 | 2.4488 | 2.538 | 1.4829
1.8542 | 1.6656 | 3 | 2.4918
1.8611 | 1.083 | 3 | 2.8555
1.8681 | 0.73658 | 3 | 2.7449
1.875 | 0.5 | 1.3272 | 2.4398
1.8819 | 0.5 | 0.5 | 1.3326
1.8889 | 0.6573 | 0.5 | 0.52055
1.8958 | 1.8266 | 0.5 | 0.68792
1.9028 | 3 | 1.4295 | 0.78434
1.9097 | 3 | 2.004 | 0.86925
1.9167 | 2.3102 | 2.8428 | 1.7573
1.9236 | 0.99996 | 3 | 2.4758
1.9306 | 0.5 | 3 | 1.8639
1.9375 | 1.3525 | 3 | 1.0409
1.9444 | 3 | 3 | 1.0003
1.9514 | 3 | 3 | 1.6233
1.9583 | 3 | 3 | 2.9476
1.9653 | 2.5716 | 3 | 3
1.9722 | 1.21 | 3 | 3
1.9792 | 0.98287 | 3 | 3
1.9861 | 1.8364 | 2.4783 | 3
1.9931 | 3 | 0.81478 | 3
2 | 3 | 0.5 | 3
2.0069 | 3 | 0.5 | 2.7008
2.0139 | 3 | 1.7246 | 1.5569
2.0208 | 3 | 2.7106 | 0.6589
2.0278 | 2.9197 | 3 | 0.63627
2.0347 | 2.2401 | 3 | 0.5
2.0417 | 1.0359 | 1.626 | 0.5
2.0486 | 0.5 | 0.60882 | 0.5
2.0556 | 0.5 | 0.5 | 0.5
2.0625 | 0.5 | 0.5 | 0.5
2.0694 | 0.5 | 0.5 | 2.1855
2.0764 | 1.2771 | 0.5 | 3
2.0833 | 2.7043 | 0.5 | 3
2.0903 | 3 | 0.5 | 2.9758
2.0972 | 3 | 0.5 | 2.236
2.1042 | 3 | 0.5 | 1.6593
2.1111 | 1.9438 | 0.5 | 1.6675
2.1181 | 0.5 | 1.8828 | 2.3928
2.125 | 0.5 | 2.0756 | 2.9001
2.1319 | 0.5 | 1.1002 | 2.7846
2.1389 | 0.5 | 0.60494 | 2.85
2.1458 | 1.019 | 1.2752 | 2.8049
2.1528 | 2.6957 | 2.2136 | 2.0791
2.1597 | 3 | 3 | 1.0603
2.1667 | 2.6729 | 3 | 0.5
2.1736 | 0.84422 | 3 | 0.5
2.1806 | 0.5 | 2.5122 | 0.5
2.1875 | 0.5 | 1.7534 | 0.5
2.1944 | 0.5 | 1.4109 | 0.5
2.2014 | 0.84416 | 2.0846 | 0.5
2.2083 | 1.1468 | 3 | 0.5
2.2153 | 1.24 | 2.5407 | 1.1126
2.2222 | 1.6376 | 1.1197 | 2.4664
2.2292 | 1.8831 | 0.5 | 3
2.2361 | 1.0287 | 0.78423 | 3
2.2431 | 0.5 | 1.7186 | 3
2.25 | 0.5 | 1.7609 | 2.9068
2.2569 | 0.5 | 0.52563 | 2.5634
2.2639 | 0.5 | 0.5 | 1.9658
2.2708 | 1.0268 | 0.5 | 2.2458
2.2778 | 1.3599 | 0.5 | 2.7546
2.2847 | 1.5316 | 0.5 | 2.4029
2.2917 | 1.7578 | 0.5 | 2.3544
2.2986 | 1.1628 | 0.5 | 2.5781
2.3056 | 0.87294 | 0.5 | 1.7138
2.3125 | 1.3771 | 0.5 | 1.146
2.3194 | 1.2016 | 0.5 | 1.2107
2.3264 | 0.5 | 0.64768 | 0.5
2.3333 | 0.66446 | 1.2131 | 0.5
2.3403 | 1.4263 | 1.2445 | 1.0385
2.3472 | 2.2638 | 0.88684 | 1.8783
2.3542 | 3 | 0.5 | 2.4905
2.3611 | 3 | 0.5 | 3
2.3681 | 3 | 0.5 | 3
2.375 | 3 | 0.5 | 2.9756
2.3819 | 3 | 0.5 | 1.8337
2.3889 | 3 | 0.5 | 0.5
2.3958 | 1.9123 | 1.019 | 0.5
2.4028 | 1.9201 | 2.0926 | 0.86501
2.4097 | 2.5215 | 2.5498 | 2.9808
2.4167 | 2.6137 | 2.3839 | 3
2.4236 | 2.2617 | 2.0303 | 2.8987
2.4306 | 2.0485 | 1.6376 | 0.5
2.4375 | 1.7027 | 1.6006 | 0.5
2.4444 | 1.3305 | 2.4028 | 0.5
2.4514 | 1.1306 | 3 | 0.5
2.4583 | 0.61415 | 3 | 1.4839
2.4653 | 0.67189 | 3 | 2.2969
2.4722 | 1.5076 | 2.9804 | 1.3302
2.4792 | 2.5256 | 2.072 | 0.5
2.4861 | 3 | 1.2777 | 0.5
2.4931 | 3 | 0.61864 | 1.6164
2.5 | 2.6494 | 0.78977 | 3
2.5069 | 1.8224 | 0.80539 | 3
2.5139 | 1.4113 | 0.5 | 3
2.5208 | 1.853 | 1.0783 | 2.2114
2.5278 | 3 | 1.4694 | 1.9274
2.5347 | 3 | 0.86975 | 1.9047
2.5417 | 3 | 0.66708 | 1.297
2.5486 | 3 | 1.0599 | 0.5
2.5556 | 2.8545 | 1.6819 | 0.5
2.5625 | 1.1915 | 2.0057 | 0.5
2.5694 | 0.5 | 1.9115 | 0.5
2.5764 | 0.5 | 1.9394 | 0.5
2.5833 | 0.5 | 2.5049 | 0.5
2.5903 | 0.5 | 2.8984 | 0.82196
2.5972 | 0.5 | 2.4384 | 1.9792
2.6042 | 0.5 | 1.0733 | 2.0941
2.6111 | 1.6767 | 0.5 | 1.7506
2.6181 | 2.6134 | 0.5 | 1.5523
2.625 | 3 | 0.5 | 0.93591
2.6319 | 2.1799 | 1.9511 | 0.74238
2.6389 | 1.2105 | 2.0601 | 1.0749
2.6458 | 1.5514 | 1.352 | 1.0126
2.6528 | 2.1736 | 0.91651 | 0.99401
2.6597 | 2.0209 | 0.5601 | 1.1542
2.6667 | 1.0953 | 0.63022 | 1.2549
2.6736 | 0.5 | 0.87378 | 1.5349
2.6806 | 0.5 | 0.5 | 2.211
2.6875 | 0.62088 | 0.5 | 2.5029
2.6944 | 0.65646 | 0.5 | 2.6429
2.7014 | 0.5 | 0.77253 | 2.9905
2.7083 | 0.5 | 1.1109 | 3
2.7153 | 0.56241 | 1.8878 | 3
2.7222 | 0.5 | 1.8679 | 2.6252
2.7292 | 0.5 | 0.70513 | 1.285
2.7361 | 0.52097 | 0.5 | 0.5
2.7431 | 1.0245 | 0.5 | 0.5
2.75 | 2.1469 | 0.5 | 0.5
2.7569 | 2.8568 | 0.5 | 0.5
2.7639 | 2.4459 | 0.5 | 0.5
2.7708 | 2.768 | 0.5 | 0.5
2.7778 | 3 | 0.5 | 0.95133
2.7847 | 3 | 0.5 | 2.0396
2.7917 | 2.5079 | 1.1403 | 3
2.7986 | 1.9523 | 1.2416 | 3
2.8056 | 1.8073 | 1.0896 | 2.8257
2.8125 | 2.1749 | 1.3213 | 2.4529
2.8194 | 2.1366 | 2.0151 | 1.935
2.8264 | 0.90619 | 3 | 2.0024
2.8333 | 0.5 | 3 | 3
2.8403 | 0.5 | 3 | 3
2.8472 | 0.5 | 1.1858 | 3
2.8542 | 0.5 | 0.5 | 3
2.8611 | 2.0259 | 0.5 | 3
2.8681 | 3 | 0.5 | 1.9938
2.875 | 3 | 0.81432 | 1.7339
2.8819 | 3 | 1.1651 | 2.0297
2.8889 | 2.5914 | 1.2456 | 1.942
2.8958 | 2.6923 | 1.841 | 0.87213
2.9028 | 3 | 2.5795 | 0.5
2.9097 | 2.8641 | 3 | 0.5
2.9167 | 1.4276 | 3 | 0.5
2.9236 | 0.5 | 3 | 0.62851
2.9306 | 0.5 | 3 | 1.7089
2.9375 | 0.5 | 3 | 1.6189
2.9444 | 0.5 | 2.7093 | 1.0841
2.9514 | 0.5 | 1.9463 | 0.5
2.9583 | 0.5 | 1.6705 | 0.5
2.9653 | 0.5 | 1.331 | 0.5
2.9722 | 0.76557 | 1.9038 | 0.5
2.9792 | 1.9683 | 2.971 | 0.5
2.9861 | 2.3911 | 2.851 | 0.5
2.9931 | 1.7346 | 2.4244 | 1.4332
3 | 1.3384 | 2.7559 | 3
3.0069 | 1.4112 | 2.6092 | 3
3.0139 | 1.9958 | 2.6031 | 3
3.0208 | 2.6417 | 3 | 2.9655
3.0278 | 2.5829 | 3 | 1.6947
3.0347 | 2.0571 | 3 | 0.98056
3.0417 | 1.3658 | 2.1877 | 1.8171
3.0486 | 0.77028 | 1.1134 | 2.5825
3.0556 | 0.5 | 0.50383 | 2.3511
3.0625 | 0.5 | 0.70164 | 2.1042
3.0694 | 0.5 | 1.7574 | 2.3665
3.0764 | 0.5 | 2.4965 | 3
3.0833 | 1.0394 | 1.9854 | 3
3.0903 | 3 | 1.2871 | 3
3.0972 | 3 | 0.98191 | 2.3502
3.1042 | 3 | 0.81011 | 1.8181
3.1111 | 2.8525 | 1.0024 | 2.5042
3.1181 | 0.5 | 0.94219 | 3
3.125 | 0.5 | 0.5 | 3
3.1319 | 0.5 | 0.5 | 2.5504
3.1389 | 2.1187 | 0.50528 | 1.1255
3.1458 | 3 | 2.0493 | 1.1188
3.1528 | 3 | 3 | 1.4277
3.1597 | 3 | 3 | 1.125
3.1667 | 3 | 1.9542 | 1.1784
3.1736 | 3 | 0.51641 | 1.4275
3.1806 | 1.2279 | 0.5 | 0.58073
3.1875 | 0.5 | 1.372 | 0.5
3.1944 | 0.5 | 2.6448 | 0.5
3.2014 | 0.5 | 3 | 0.5
3.2083 | 0.5 | 3 | 0.7248
3.2153 | 0.52774 | 2.9741 | 2.4068
3.2222 | 1.0078 | 2.661 | 2.39
3.2292 | 1.6422 | 3 | 1.6025
3.2361 | 2.4819 | 2.7622 | 1.3704
3.2431 | 2.4064 | 1.817 | 1.366
3.25 | 1.6608 | 0.69686 | 1.9553
3.2569 | 1.5963 | 0.5 | 3
3.2639 | 1.6219 | 0.5 | 2.9436
3.2708 | 1.5976 | 0.5 | 1.8411
3.2778 | 1.9513 | 1.9708 | 1.5188
3.2847 | 2.0979 | 2.7593 | 2.1281
3.2917 | 1.5637 | 3 | 2.9604
3.2986 | 1.8202 | 3 | 3
3.3056 | 2.4597 | 3 | 2.5241
3.3125 | 2.0164 | 2.6325 | 1.3736
3.3194 | 1.2777 | 2.9576 | 0.5
3.3264 | 1.0095 | 3 | 0.5
3.3333 | 0.83495 | 3 | 0.5
3.3403 | 1.2629 | 3 | 0.5
3.3472 | 2.514 | 2.7385 | 0.5
3.3542 | 3 | 1.4739 | 0.61345
3.3611 | 3 | 1.4116 | 1.047
3.3681 | 2.0809 | 1.5366 | 0.94651
3.375 | 0.73202 | 1.881 | 0.5
3.3819 | 0.5 | 2.4165 | 0.5
3.3889 | 0.5 | 2.8022 | 0.5
3.3958 | 0.5 | 2.8076 | 0.5
3.4028 | 1.1657 | 2.525 | 1.1775
3.4097 | 2.4561 | 2.3575 | 2.8847
3.4167 | 2.1329 | 2.2202 | 3
3.4236 | 1.3234 | 2.2801 | 3
3.4306 | 1.0926 | 2.2137 | 2.6595
3.4375 | 1.724 | 1.6374 | 2.4935
3.4444 | 3 | 0.68344 | 2.6209
3.4514 | 3 | 0.5 | 2.1673
3.4583 | 3 | 0.50139 | 1.4635
3.4653 | 3 | 0.86692 | 0.73043
3.4722 | 0.65803 | 0.55003 | 0.5
3.4792 | 0.5 | 0.5 | 1.2601
3.4861 | 0.5 | 0.5 | 2.1659
3.4931 | 0.5 | 1.1958 | 2.2497
3.5 | 0.5 | 3 | 2.5422
3.5069 | 1.0946 | 3 | 3
3.5139 | 1.7431 | 3 | 2.9393
3.5208 | 1.9785 | 3 | 2.857
3.5278 | 1.5988 | 1.839 | 2.5795
3.5347 | 1.2642 | 1.4239 | 1.1519
3.5417 | 0.98328 | 1.7481 | 0.5
3.5486 | 0.5 | 2.1037 | 1.3072
3.5556 | 0.5 | 2.217 | 1.8557
3.5625 | 0.5 | 1.7154 | 1.9072
3.5694 | 0.5 | 1.4987 | 2.1863
3.5764 | 0.77658 | 1.5584 | 1.674
3.5833 | 1.1651 | 1.0769 | 0.64647
3.5903 | 0.97605 | 0.5 | 0.5
3.5972 | 1.3148 | 0.5 | 0.5
3.6042 | 2.3622 | 0.55307 | 0.5
3.6111 | 3 | 0.5539 | 0.5
3.6181 | 3 | 0.59484 | 0.5
3.625 | 3 | 0.62837 | 0.5
3.6319 | 3 | 0.59576 | 2.1885
3.6389 | 3 | 0.90277 | 3
3.6458 | 1.6838 | 1.6244 | 3
3.6528 | 0.5 | 1.5375 | 3
3.6597 | 0.5 | 0.5 | 2.292
3.6667 | 0.5 | 0.5 | 0.66448
3.6736 | 0.5 | 0.5 | 0.5
3.6806 | 1.3337 | 0.5 | 0.5
3.6875 | 2.385 | 1.4872 | 1.231
3.6944 | 3 | 3 | 1.8185
3.7014 | 3 | 3 | 1.4321
3.7083 | 3 | 2.1867 | 0.5
3.7153 | 3 | 0.5 | 0.5
3.7222 | 3 | 0.5 | 1.6629
3.7292 | 1.9227 | 0.5 | 3
3.7361 | 0.5 | 0.5 | 3
3.7431 | 0.5 | 1.2529 | 3
3.75 | 0.5 | 1.0591 | 3
3.7569 | 1.1179 | 0.67975 | 2.9261
3.7639 | 2.2468 | 0.5 | 1.9263
3.7708 | 1.6477 | 0.83203 | 1.6959
3.7778 | 0.5 | 2.5847 | 2.4496
3.7847 | 0.5 | 3 | 2.9982
3.7917 | 0.5 | 3 | 2.531
3.7986 | 0.80459 | 2.3283 | 1.6964
3.8056 | 2.0627 | 0.92005 | 1.3617
3.8125 | 2.0537 | 0.5 | 1.6186
3.8194 | 1.3767 | 0.5 | 2.0961
3.8264 | 1.3374 | 0.5 | 2.4539
3.8333 | 1.5373 | 0.5 | 2.5546
3.8403 | 1.4969 | 0.5 | 2.7067
3.8472 | 0.92101 | 0.5 | 2.2446
3.8542 | 0.5 | 0.5 | 1.2419
3.8611 | 0.5 | 1.0067 | 0.5
3.8681 | 1.5092 | 2.2498 | 0.5
3.875 | 2.259 | 2.3449 | 0.56873
3.8819 | 1.2771 | 2.1989 | 1.5218
3.8889 | 0.5 | 2.1094 | 2.6335
3.8958 | 0.5 | 1.4545 | 3
3.9028 | 0.5 | 0.71562 | 3
3.9097 | 0.77873 | 0.5 | 2.3144
3.9167 | 1.6169 | 0.5 | 2.1752
3.9236 | 1.6031 | 0.5 | 1.7425
3.9306 | 2.4132 | 0.5 | 1.5993
3.9375 | 3 | 0.5 | 2.1472
3.9444 | 2.6879 | 0.5 | 2.0993
3.9514 | 1.3546 | 0.69282 | 2.054
3.9583 | 1.093 | 1.5305 | 2.1553
3.9653 | 1.5335 | 1.6557 | 1.9402
3.9722 | 2.7957 | 1.3933 | 1.4528
3.9792 | 3 | 1.4335 | 0.88002
3.9861 | 3 | 1.4732 | 0.62558
3.9931 | 2.6566 | 1.8608 | 1.1912
4 | 1.695 | 2.8438 | 2.5272
4.0069 | 1.3471 | 3 | 3
4.0139 | 1.4056 | 2.3932 | 3
4.0208 | 1.8655 | 1.1593 | 3
4.0278 | 2.1896 | 0.5 | 1.1205
4.0347 | 1.9573 | 0.5 | 0.5
4.0417 | 1.6158 | 0.5 | 0.5
4.0486 | 1.567 | 0.5 | 0.5
4.0556 | 1.7299 | 1.9226 | 0.5
4.0625 | 2.3863 | 3 | 0.5
4.0694 | 2.4066 | 3 | 0.5
4.0764 | 1.8353 | 3 | 0.5
4.0833 | 1.319 | 3 | 0.71234
4.0903 | 0.84091 | 1.3262 | 1.7308
4.0972 | 1.1847 | 1.0264 | 1.5106
4.1042 | 2.2732 | 2.3032 | 0.5
4.1111 | 2.6552 | 3 | 0.5
4.1181 | 1.7862 | 3 | 0.5
4.125 | 0.5 | 3 | 0.5
4.1319 | 0.5 | 3 | 0.5
4.1389 | 0.5 | 2.0472 | 1.1661
4.1458 | 0.5 | 1.743 | 1.7237
4.1528 | 0.5 | 1.595 | 1.4579
4.1597 | 0.5 | 0.70556 | 0.7983
4.1667 | 0.5 | 0.5 | 0.5
4.1736 | 0.98579 | 0.5 | 0.5
4.1806 | 0.98841 | 0.5 | 0.5
4.1875 | 0.5 | 0.5 | 0.5
4.1944 | 0.5 | 0.62836 | 1.4984
4.2014 | 0.64228 | 0.5 | 3
4.2083 | 2.217 | 0.5 | 3
4.2153 | 2.9847 | 0.89292 | 3
4.2222 | 2.699 | 1.7098 | 3
4.2292 | 1.9797 | 2.5863 | 3
4.2361 | 2.239 | 3 | 2.1674
4.2431 | 3 | 3 | 1.6311
4.25 | 3 | 3 | 1.135
4.2569 | 2.7086 | 3 | 1.1168
4.2639 | 2.2054 | 1.2993 | 2.0314
4.2708 | 1.3942 | 0.5 | 2.5472
4.2778 | 0.515 | 0.5 | 2.1696
4.2847 | 0.5 | 0.5 | 1.9883
4.2917 | 0.5 | 1.178 | 2.0384
4.2986 | 0.5 | 1.6182 | 2.2458
4.3056 | 0.5 | 1.8566 | 2.1828
4.3125 | 0.5 | 1.7431 | 1.3793
4.3194 | 0.67298 | 1.2448 | 0.55535
4.3264 | 1.4625 | 0.5 | 0.5
4.3333 | 1.7197 | 0.5 | 1.3863
4.3403 | 1.6242 | 0.5 | 2.7206
4.3472 | 1.9634 | 0.59007 | 2.7965
4.3542 | 2.3609 | 1.4918 | 1.7533
4.3611 | 2.5381 | 1.9185 | 0.91048
4.3681 | 2.4909 | 2.1578 | 0.5
4.375 | 2.2719 | 1.5236 | 0.58587
4.3819 | 2.3133 | 0.98834 | 0.76907
4.3889 | 2.902 | 0.5 | 0.5
4.3958 | 3 | 0.5 | 0.5
4.4028 | 3 | 0.5 | 0.5
4.4097 | 2.1306 | 0.5 | 0.5
4.4167 | 1.1881 | 1.6702 | 0.60914
4.4236 | 0.80515 | 2.4862 | 1.9268
4.4306 | 0.5 | 2.6193 | 2.9224
4.4375 | 0.5 | 1.4613 | 3
4.4444 | 0.5 | 0.5 | 3
4.4514 | 0.5 | 0.5 | 2.2516
4.4583 | 1.3541 | 1.3962 | 0.5
4.4653 | 1.9841 | 2.7515 | 0.5
4.4722 | 1.6589 | 2.9541 | 0.5
4.4792 | 0.5 | 1.7393 | 0.5
4.4861 | 0.5 | 0.5 | 0.55072
4.4931 | 0.5 | 0.5 | 1.8079
4.5 | 0.5 | 0.77472 | 2.4649
4.5069 | 0.5 | 1.1974 | 1.9615
4.5139 | 0.5 | 1.5342 | 1.3539
4.5208 | 0.5 | 1.5095 | 1.0408
4.5278 | 0.5 | 1.3285 | 0.5
4.5347 | 0.81442 | 1.5158 | 0.5
4.5417 | 1.6981 | 1.4906 | 1.7688
4.5486 | 1.6873 | 0.95998 | 2.6467
4.5556 | 1.0373 | 0.71834 | 3
4.5625 | 0.64737 | 0.5 | 3
4.5694 | 0.5 | 0.5 | 3
4.5764 | 0.5 | 0.5 | 1.3854
4.5833 | 1.2499 | 0.5 | 0.82521
4.5903 | 1.4797 | 0.65544 | 1.1805
4.5972 | 1.1282 | 1.1739 | 1.0709
4.6042 | 0.66723 | 1.2103 | 1.4612
4.6111 | 0.77742 | 0.82743 | 1.6488
4.6181 | 1.1477 | 1.0101 | 0.75459
4.625 | 1.8952 | 1.2073 | 0.5
4.6319 | 2.2194 | 0.80507 | 1.428
4.6389 | 1.7147 | 0.61414 | 2.3384
4.6458 | 1.302 | 0.83225 | 2.5337
4.6528 | 1.3696 | 1.343 | 2.5674
4.6597 | 1.6927 | 2.3103 | 1.8832
4.6667 | 1.9333 | 3 | 1.7029
4.6736 | 2.7427 | 2.4891 | 2.1238
4.6806 | 3 | 1.3584 | 2.1212
4.6875 | 3 | 1.1343 | 1.7339
4.6944 | 2.5004 | 2.227 | 1.4134
4.7014 | 1.4341 | 3 | 1.3067
4.7083 | 1.3937 | 3 | 1.9099
4.7153 | 2.248 | 3 | 2.1399
4.7222 | 3 | 1.1576 | 1.242
4.7292 | 3 | 0.5 | 0.93393
4.7361 | 3 | 0.74785 | 1.1011
4.7431 | 2.7081 | 2.4406 | 0.62577
4.75 | 2.7056 | 3 | 0.5
4.7569 | 3 | 2.8553 | 0.5
4.7639 | 3 | 1.2379 | 0.5
4.7708 | 3 | 0.5 | 1.6353
4.7778 | 2.7947 | 0.5 | 3
4.7847 | 1.4972 | 0.6383 | 3
4.7917 | 0.8787 | 2.4131 | 2.5563
4.7986 | 1.6648 | 3 | 1.0321
4.8056 | 2.1795 | 2.527 | 0.5
4.8125 | 1.7948 | 1.7515 | 0.5
4.8194 | 0.63894 | 0.77223 | 0.5
4.8264 | 0.5 | 0.5 | 0.5
4.8333 | 0.5 | 0.85018 | 0.5
4.8403 | 0.80334 | 0.75042 | 0.5
4.8472 | 1.9904 | 0.5 | 0.5
4.8542 | 1.5757 | 0.5 | 0.5
4.8611 | 0.5 | 0.5 | 0.5
4.8681 | 0.5 | 0.5 | 0.5
4.875 | 0.5 | 0.5 | 0.5
4.8819 | 0.5 | 0.5 | 0.78651
4.8889 | 0.90689 | 0.5 | 1.8619
4.8958 | 1.5595 | 0.5 | 2.4126
4.9028 | 1.7952 | 0.5 | 1.6909
4.9097 | 1.9985 | 0.5 | 0.5
4.9167 | 2.0349 | 0.87713 | 0.5
4.9236 | 1.4525 | 1.0357 | 0.5
4.9306 | 0.69041 | 2.1374 | 0.5
4.9375 | 0.5 | 3 | 0.5
4.9444 | 0.5313 | 3 | 0.62658
4.9514 | 1.2203 | 3 | 1.9135
4.9583 | 2.262 | 2.0413 | 3
4.9653 | 3 | 1.8593 | 3
4.9722 | 3 | 2.5478 | 3
4.9792 | 2.9768 | 3 | 3
4.9861 | 1.7488 | 3 | 2.38
4.9931 | 0.90818 | 2.4314 | 0.87435
5 | 0.88463 | 1.0284 | 0.51673
5.0069 | 1.5814 | 0.5 | 1.1659
5.0139 | 2.7556 | 0.77777 | 0.99422
5.0208 | 3 | 1.718 | 0.5
5.0278 | 3 | 3 | 0.5
5.0347 | 2.812 | 3 | 0.5
5.0417 | 1.8646 | 3 | 1.2862
5.0486 | 1.3206 | 2.1921 | 2.3421
5.0556 | 1.8334 | 1.1765 | 2.8346
5.0625 | 2.1573 | 0.6068 | 2.4434
5.0694 | 2.1516 | 0.71238 | 1.4701
5.0764 | 2.4076 | 1.4033 | 0.5
5.0833 | 1.8618 | 1.7688 | 0.5
5.0903 | 1.0909 | 2.231 | 0.63383
5.0972 | 1.5458 | 2.7616 | 1.769
5.1042 | 2.5046 | 2.4486 | 2.9935
5.1111 | 3 | 1.2136 | 3
5.1181 | 3 | 0.5 | 2.0054
5.125 | 3 | 0.5 | 1.171
5.1319 | 2.8567 | 0.5 | 1.0443
5.1389 | 1.5554 | 0.5 | 0.58978
5.1458 | 0.68229 | 1.3869 | 0.5
5.1528 | 0.8079 | 2.5857 | 0.5
5.1597 | 0.77065 | 2.9653 | 0.83483
5.1667 | 1.0083 | 2.4494 | 2.3008
5.1736 | 2.267 | 2.1036 | 3
5.1806 | 2.8021 | 2.6384 | 3
5.1875 | 2.3291 | 3 | 1.9723
5.1944 | 2.5076 | 3 | 1.0718
5.2014 | 1.8512 | 3 | 1.3002
5.2083 | 0.75772 | 2.7966 | 1.874
5.2153 | 1.2943 | 2.1852 | 1.7757
5.2222 | 2.2795 | 2.8295 | 1.5894
5.2292 | 2.886 | 2.8546 | 1.6672
5.2361 | 3 | 2.0273 | 1.7411
5.2431 | 3 | 2.0979 | 1.543
5.25 | 3 | 2.0027 | 1.6124
5.2569 | 2.4342 | 1.7366 | 2.172
5.2639 | 1.7956 | 2.1195 | 2.4767
5.2708 | 1.094 | 2.2339 | 2.5674
5.2778 | 1.3121 | 1.96 | 2.9382
5.2847 | 1.6003 | 1.3084 | 2.5122
5.2917 | 1.2823 | 0.5 | 1.5044
5.2986 | 0.5 | 0.5 | 1.801
5.3056 | 0.5 | 0.61695 | 2.3848
5.3125 | 0.5 | 0.80096 | 1.8087
5.3194 | 0.5 | 1.6202 | 1.3412
5.3264 | 1.0139 | 2.2537 | 1.8291
5.3333 | 2.5576 | 2.3836 | 2.1513
5.3403 | 3 | 2.85 | 1.9267
5.3472 | 3 | 2.7012 | 1.886
5.3542 | 3 | 1.8463 | 1.6453
5.3611 | 3 | 1.9485 | 1.4754
5.3681 | 3 | 3 | 2.3414
5.375 | 2.2915 | 3 | 3
5.3819 | 0.92954 | 3 | 3
5.3889 | 0.5 | 3 | 3
5.3958 | 0.5 | 3 | 2.4726
5.4028 | 0.5 | 3 | 1.9981
5.4097 | 0.5 | 3 | 1.6943
5.4167 | 0.5 | 3 | 1.0625
5.4236 | 1.4253 | 3 | 1.0256
5.4306 | 2.7186 | 3 | 1.7557
5.4375 | 3 | 3 | 2.0229
5.4444 | 3 | 2.8979 | 2.0786
5.4514 | 3 | 1.7202 | 1.9828
5.4583 | 3 | 0.5 | 1.2718
5.4653 | 2.4083 | 0.5 | 1.0822
5.4722 | 2.2504 | 0.5 | 1.4517
5.4792 | 2.2717 | 0.5 | 1.4773
5.4861 | 1.481 | 0.5 | 0.5
5.4931 | 1.043 | 1.1976 | 0.5
5.5 | 0.97749 | 1.7291 | 0.5
5.5069 | 0.77115 | 1.3223 | 0.5
5.5139 | 1.1841 | 0.5 | 0.5
5.5208 | 1.7018 | 0.5 | 0.5251
5.5278 | 1.5668 | 0.5 | 1.5978
5.5347 | 1.2943 | 0.5 | 2.5656
5.5417 | 1.9207 | 0.74698 | 3
5.5486 | 2.8359 | 1.6638 | 3
5.5556 | 3 | 1.7138 | 3
5.5625 | 2.9399 | 1.5822 | 2.1846
5.5694 | 2.591 | 1.9018 | 0.89205
5.5764 | 2.3525 | 1.985 | 0.77696
5.5833 | 2.7767 | 1.9639 | 2.1789
5.5903 | 3 | 2.375 | 3
5.5972 | 2.9132 | 2.6157 | 3
5.6042 | 2.5252 | 2.04 | 3
5.6111 | 1.9277 | 1.3096 | 2.5184
5.6181 | 0.51182 | 0.5 | 0.5
5.625 | 0.5 | 0.5 | 0.5
5.6319 | 0.5 | 0.5 | 0.5
5.6389 | 0.53963 | 0.5 | 0.5
5.6458 | 2.0888 | 1.6162 | 0.61642
5.6528 | 2.7875 | 1.6719 | 2.6405
5.6597 | 1.6356 | 0.53565 | 3
5.6667 | 0.5 | 0.5 | 3
5.6736 | 0.5 | 0.90353 | 3
5.6806 | 0.5 | 2.3887 | 2.933
5.6875 | 1.7454 | 2.9371 | 2.3885
5.6944 | 2.6704 | 2.1976 | 2.7814
5.7014 | 2.7147 | 0.5 | 2.6604
5.7083 | 1.806 | 0.5 | 2.4455
5.7153 | 0.80892 | 0.5 | 2.8032
5.7222 | 0.55067 | 0.5 | 2.8728
5.7292 | 0.5 | 1.3089 | 2.3172
5.7361 | 0.5 | 2.6788 | 1.8045
5.7431 | 0.5 | 3 | 1.3173
5.75 | 0.5 | 3 | 0.98745
5.7569 | 1.3894 | 1.9018 | 1.1211
5.7639 | 2.72 | 0.5 | 1.5129
5.7708 | 2.7797 | 0.5 | 2.1233
5.7778 | 1.1951 | 0.72072 | 2.2073
5.7847 | 0.5 | 2.0962 | 2.1021
5.7917 | 0.5 | 3 | 2.4967
5.7986 | 0.74021 | 2.8306 | 3
5.8056 | 1.4021 | 1.8322 | 3
5.8125 | 1.6631 | 1.6117 | 3
5.8194 | 1.0724 | 1.6819 | 2.8005
5.8264 | 0.5 | 0.97434 | 1.8793
5.8333 | 0.5 | 0.5 | 2.0961
5.8403 | 0.5 | 0.5 | 2.5637
5.8472 | 0.5 | 0.5 | 2.9448
5.8542 | 1.2036 | 0.80307 | 3
5.8611 | 2.6456 | 1.1431 | 3
5.8681 | 3 | 0.69783 | 2.2901
5.875 | 2.5393 | 0.5 | 1.062
5.8819 | 1.0062 | 0.5 | 0.5
5.8889 | 0.5 | 0.5 | 0.5
5.8958 | 0.5 | 0.5 | 0.92738
5.9028 | 1.7381 | 0.5 | 1.9102
5.9097 | 2.8619 | 2.0593 | 1.5108
5.9167 | 2.588 | 3 | 0.70207
5.9236 | 1.5676 | 3 | 0.5
5.9306 | 1.2946 | 2.0927 | 0.84541
5.9375 | 2.3883 | 0.5 | 1.0507
5.9444 | 3 | 0.5 | 0.67973
5.9514 | 3 | 0.5 | 0.87372
5.9583 | 3 | 0.62521 | 2.1562
5.9653 | 1.7709 | 0.95043 | 2.6997
5.9722 | 1.0256 | 0.80183 | 1.7064
5.9792 | 1.1083 | 0.67112 | 0.5
5.9861 | 1.5418 | 0.63525 | 0.5
5.9931 | 2.0117 | 1.2969 | 0.5
6 | 2.6091 | 2.1986 | 2.605
6.0069 | 3 | 2.5651 | 3
6.0139 | 3 | 2.7803 | 3
6.0208 | 3 | 2.1818 | 2.5125
6.0278 | 2.9369 | 0.61059 | 2.5752
6.0347 | 2.0322 | 0.5 | 2.3883
6.0417 | 0.88377 | 0.5 | 2.1933
6.0486 | 0.5 | 0.5 | 1.9762
6.0556 | 0.5 | 0.5 | 1.351
6.0625 | 0.5 | 0.5 | 0.68019
6.0694 | 0.5 | 0.5 | 0.5
6.0764 | 0.5 | 0.5 | 0.5
6.0833 | 0.5 | 0.5 | 0.5
6.0903 | 0.5 | 0.5 | 0.5
6.0972 | 0.5 | 0.5 | 0.5
6.1042 | 0.998 | 1.0129 | 0.5
6.1111 | 1.5118 | 1.3662 | 1.7213
6.1181 | 1.4012 | 0.91433 | 3
6.125 | 0.92835 | 0.5 | 3
6.1319 | 1.1136 | 0.5 | 2.6133
6.1389 | 2.1772 | 0.5 | 1.3369
6.1458 | 2.4768 | 0.5 | 1.1599
6.1528 | 1.609 | 0.5 | 2.5535
6.1597 | 0.91195 | 0.5 | 3
6.1667 | 0.5 | 0.5 | 3
6.1736 | 0.5 | 0.5 | 3
6.1806 | 0.5 | 0.5 | 3
6.1875 | 0.5 | 0.5 | 3
6.1944 | 0.5 | 0.5 | 2.0575
6.2014 | 1.0372 | 0.5 | 2.224
6.2083 | 2.1592 | 0.5 | 2.7431
6.2153 | 2.7329 | 0.5 | 3
6.2222 | 3 | 0.5 | 3
6.2292 | 3 | 0.5 | 3
6.2361 | 2.912 | 0.90959 | 3
6.2431 | 2.445 | 1.6021 | 3
6.25 | 1.9215 | 2.3202 | 3
6.2569 | 1.0976 | 2.2351 | 3
6.2639 | 1.2086 | 2.0954 | 2.716
6.2708 | 1.8525 | 2.4325 | 2.4259
6.2778 | 2.3883 | 2.597 | 3
6.2847 | 2.7096 | 2.3154 | 3
6.2917 | 2.7245 | 1.9521 | 3
6.2986 | 1.7833 | 1.5288 | 3
6.3056 | 0.64447 | 0.86916 | 3
6.3125 | 0.5 | 0.64711 | 1.4784
6.3194 | 0.5 | 1.2361 | 1.1643
6.3264 | 0.5 | 2.086 | 1.6393
6.3333 | 1.1518 | 3 | 2.0165
6.3403 | 2.9496 | 3 | 2.041
6.3472 | 3 | 3 | 1.0037
6.3542 | 3 | 3 | 0.5
6.3611 | 3 | 2.3204 | 0.5
6.3681 | 3 | 0.5 | 0.5
6.375 | 2.7684 | 0.5 | 0.5
6.3819 | 2.1608 | 0.5 | 0.86691
6.3889 | 0.78454 | 1.2433 | 1.094
6.3958 | 0.5 | 2.6224 | 1.281
6.4028 | 0.5 | 2.9079 | 1.8065
6.4097 | 0.5 | 1.8824 | 2.4446
6.4167 | 0.92639 | 1.3219 | 3
6.4236 | 2.1256 | 0.92178 | 3
6.4306 | 2.8768 | 0.5 | 3
6.4375 | 2.8099 | 0.5 | 2.2981
6.4444 | 2.0611 | 0.68363 | 1.3389
6.4514 | 0.8208 | 0.84715 | 0.5
6.4583 | 0.5 | 1.4334 | 0.53198
6.4653 | 0.5 | 2.1533 | 1.2974
6.4722 | 0.5 | 1.9317 | 1.5432
6.4792 | 0.5 | 1.3504 | 1.5508
6.4861 | 0.5 | 0.51151 | 1.0895
6.4931 | 1.2338 | 0.5 | 0.5
6.5 | 1.909 | 0.5 | 0.5
6.5069 | 2.2921 | 1.0787 | 0.5
6.5139 | 2.2572 | 2.5825 | 1.3769
6.5208 | 1.7814 | 3 | 2.0024
6.5278 | 0.9153 | 2.7104 | 2.4137
6.5347 | 0.5 | 2.0608 | 2.3379
6.5417 | 0.5 | 1.95 | 2.145
6.5486 | 0.5 | 1.9188 | 1.783
6.5556 | 1.2619 | 1.4426 | 0.72315
6.5625 | 2.1096 | 0.5 | 0.5
6.5694 | 1.2805 | 0.5 | 1.2402
6.5764 | 0.5 | 0.82248 | 3
6.5833 | 0.5 | 2.164 | 3
6.5903 | 0.5 | 3 | 3
6.5972 | 0.5 | 3 | 1.5638
6.6042 | 0.5 | 2.2503 | 0.5
6.6111 | 0.5 | 2.5578 | 0.5
6.6181 | 0.5 | 3 | 0.81786
6.625 | 0.5 | 3 | 2.1526
6.6319 | 0.5 | 2.9772 | 2.8757
6.6389 | 0.5 | 2.7188 | 2.4804
6.6458 | 0.5 | 2.2406 | 1.4075
6.6528 | 0.69717 | 1.6229 | 0.5
6.6597 | 1.7745 | 1.1976 | 0.5
6.6667 | 2.756 | 0.5 | 0.6009
6.6736 | 3 | 0.5 | 1.3863
6.6806 | 3 | 0.5 | 2.1793
6.6875 | 3 | 0.5 | 2.6917
6.6944 | 1.9372 | 0.5 | 3
6.7014 | 0.5 | 1.4957 | 3
6.7083 | 0.5 | 3 | 3
6.7153 | 0.5 | 3 | 3
6.7222 | 1.3487 | 3 | 2.2218
6.7292 | 2.6682 | 2.4759 | 1.3639
6.7361 | 3 | 1.4183 | 0.62769
6.7431 | 3 | 1.0437 | 0.9498
6.75 | 3 | 2.2592 | 0.83239
6.7569 | 3 | 3 | 0.5
6.7639 | 2.1161 | 3 | 0.65599
6.7708 | 0.83514 | 2.5013 | 1.8275
6.7778 | 0.5 | 1.3444 | 2.8698
6.7847 | 0.5 | 0.5 | 3
6.7917 | 0.5 | 0.5 | 2.4445
6.7986 | 0.6071 | 0.5 | 1.3558
6.8056 | 0.5 | 0.5 | 0.75106
6.8125 | 0.5 | 0.5 | 1.1512
6.8194 | 0.5 | 0.5 | 2.4812
6.8264 | 0.5 | 0.5 | 3
6.8333 | 1.0908 | 0.5 | 2.4266
6.8403 | 1.2953 | 0.5 | 0.95844
6.8472 | 0.5 | 0.5 | 0.5
6.8542 | 0.66835 | 0.5 | 0.65726
6.8611 | 2.05 | 0.5 | 2.3515
6.8681 | 3 | 1.1025 | 3
6.875 | 3 | 2.0935 | 3
6.8819 | 3 | 2.5651 | 3
6.8889 | 2.0023 | 3 | 3
6.8958 | 0.78112 | 3 | 2.8544
6.9028 | 1.2884 | 2.5467 | 0.77248
6.9097 | 2.2737 | 1.7254 | 0.5
6.9167 | 2.6623 | 1.555 | 0.5
6.9236 | 2.5209 | 1.941 | 0.5
6.9306 | 1.959 | 2.9516 | 0.5
6.9375 | 1.3868 | 3 | 0.5
6.9444 | 1.8588 | 3 | 0.5
6.9514 | 2.8384 | 2.6337 | 0.5
6.9583 | 3 | 1.5888 | 0.5
6.9653 | 3 | 1.953 | 0.79719
6.9722 | 3 | 3 | 1.9135
6.9792 | 1.4684 | 3 | 2.7362
6.9861 | 0.5 | 2.9655 | 3
6.9931 | 0.5 | 1.9591 | 3
7 | 0.5 | 0.5 | 2.6662

## SNH
SNH
Time | Total ammonia (NHx) (Influent) | Total ammonia (NHx) (CSTR2) | Total ammonia (NHx) (CSTR3) | Total ammonia (NHx) (CSTR4)
d | g N/m3 | g N/m3 | g N/m3 | g N/m3
0 | 39.4186 | 4.7099 | 0.64088 | 0.080084
0.0069444 | 39.4186 | 4.839 | 1.0072 | 0.10688
0.013889 | 39.4186 | 5.58 | 1.3053 | 0.12252
0.020833 | 39.4186 | 6.1241 | 1.6225 | 0.14441
0.027778 | 39.4186 | 6.5255 | 1.9296 | 0.17008
0.034722 | 39.4186 | 6.8241 | 2.2128 | 0.1979
0.041667 | 39.4186 | 7.048 | 2.4656 | 0.22637
0.048611 | 39.4186 | 7.2179 | 2.6865 | 0.3031
0.055556 | 39.4186 | 7.3499 | 2.8764 | 0.38452
0.0625 | 39.4186 | 7.3228 | 2.9952 | 0.42229
0.069444 | 39.4186 | 6.9543 | 2.7769 | 0.41622
0.076389 | 39.4186 | 6.6033 | 2.6022 | 0.38524
0.083333 | 39.4186 | 6.3151 | 2.5321 | 0.36226
0.090278 | 39.4186 | 6.1891 | 2.5213 | 0.27791
0.097222 | 39.4186 | 6.2138 | 2.5028 | 0.24865
0.10417 | 39.4186 | 6.2123 | 2.1631 | 0.2279
0.11111 | 39.4186 | 6.143 | 1.7064 | 0.20802
0.11806 | 39.4186 | 6.3395 | 1.4344 | 0.20046
0.125 | 39.4186 | 6.7069 | 1.3478 | 0.1829
0.13194 | 39.4186 | 6.9738 | 1.4304 | 0.18504
0.13889 | 39.4186 | 6.8152 | 1.9063 | 0.2235
0.14583 | 39.4186 | 6.3814 | 2.1724 | 0.22883
0.15278 | 39.4186 | 5.9419 | 2.2463 | 0.25958
0.15972 | 39.4186 | 5.6214 | 2.207 | 0.25522
0.16667 | 39.4186 | 5.3889 | 2.1156 | 0.22506
0.17361 | 39.4186 | 5.2194 | 2.0072 | 0.20933
0.18056 | 39.4186 | 5.2099 | 1.9157 | 0.20894
0.1875 | 39.4186 | 5.87 | 1.9409 | 0.23098
0.19444 | 39.4186 | 6.3539 | 2.0893 | 0.24151
0.20139 | 39.4186 | 6.7095 | 2.2858 | 0.21949
0.20833 | 39.4186 | 6.9714 | 2.4917 | 0.22556
0.21528 | 39.4186 | 6.6543 | 2.6189 | 0.24309
0.22222 | 39.4186 | 6.2365 | 2.3733 | 0.23049
0.22917 | 39.4186 | 5.8813 | 2.0359 | 0.19893
0.23611 | 39.4186 | 5.5959 | 1.7005 | 0.1678
0.24306 | 39.4186 | 5.3859 | 1.343 | 0.14685
0.25 | 39.4186 | 5.2865 | 1.0976 | 0.13915
0.25694 | 39.4186 | 5.3275 | 1.0192 | 0.13967
0.26389 | 39.4186 | 5.3813 | 0.99051 | 0.12446
0.27083 | 39.4186 | 5.2664 | 0.93035 | 0.11941
0.27778 | 39.4186 | 5.1164 | 0.84533 | 0.12771
0.28472 | 39.4186 | 5.0066 | 0.76835 | 0.12022
0.29167 | 39.4186 | 4.9258 | 0.72358 | 0.11485
0.29861 | 39.4186 | 4.9382 | 0.70388 | 0.11214
0.30556 | 39.4186 | 5.408 | 0.80775 | 0.10682
0.3125 | 39.4186 | 5.6316 | 0.98573 | 0.10271
0.31944 | 39.4186 | 5.5872 | 1.1001 | 0.10956
0.32639 | 39.4186 | 5.56 | 1.0587 | 0.1107
0.33333 | 39.4186 | 5.8385 | 0.98554 | 0.11539
0.34028 | 39.4186 | 6.314 | 1.0309 | 0.14237
0.34722 | 39.4186 | 6.6645 | 1.1368 | 0.15191
0.35417 | 39.4186 | 6.9239 | 1.369 | 0.17216
0.36111 | 39.4186 | 7.1169 | 1.652 | 0.20224
0.36806 | 39.4186 | 7.262 | 1.9092 | 0.23528
0.375 | 39.4186 | 7.3725 | 2.1148 | 0.26601
0.38194 | 39.4186 | 7.4579 | 2.5131 | 0.3139
0.38889 | 39.4186 | 7.5249 | 2.8044 | 0.28767
0.39583 | 39.4186 | 7.577 | 3.0213 | 0.28831
0.40278 | 39.4186 | 7.4322 | 3.103 | 0.30193
0.40972 | 39.4186 | 7.1544 | 2.545 | 0.26274
0.41667 | 39.4186 | 7.0126 | 2.1311 | 0.2131
0.42361 | 39.4186 | 6.7759 | 1.8253 | 0.18495
0.43056 | 39.4186 | 6.6564 | 1.6023 | 0.16754
0.4375 | 39.4186 | 6.9369 | 1.6241 | 0.16609
0.44444 | 39.4186 | 7.1411 | 1.9439 | 0.19438
0.45139 | 39.4186 | 7.2915 | 2.3524 | 0.2865
0.45833 | 39.4186 | 7.2943 | 2.645 | 0.34272
0.46528 | 39.4186 | 6.7597 | 2.7753 | 0.38
0.47222 | 39.4186 | 6.2255 | 2.3831 | 0.35574
0.47917 | 39.4186 | 5.8369 | 1.9099 | 0.22272
0.48611 | 39.4186 | 5.5497 | 1.5047 | 0.153
0.49306 | 39.4186 | 5.4573 | 1.3422 | 0.13074
0.5 | 39.4186 | 5.6813 | 1.5768 | 0.14212
0.50694 | 39.4186 | 6.2116 | 1.8141 | 0.1609
0.51389 | 39.4186 | 6.5995 | 1.6437 | 0.15993
0.52083 | 39.4186 | 6.4994 | 1.4891 | 0.19998
0.52778 | 39.4186 | 6.2385 | 1.382 | 0.189
0.53472 | 39.4186 | 6.0435 | 1.3793 | 0.18341
0.54167 | 39.4186 | 5.7408 | 1.6092 | 0.2008
0.54861 | 39.4186 | 5.4643 | 1.7431 | 0.22034
0.55556 | 39.4186 | 5.2641 | 1.7712 | 0.22878
0.5625 | 39.4186 | 5.1192 | 1.6645 | 0.22127
0.56944 | 39.4186 | 5.014 | 1.6535 | 0.21539
0.57639 | 39.4186 | 5.0296 | 1.6069 | 0.15724
0.58333 | 39.4186 | 5.2098 | 1.3991 | 0.13364
0.59028 | 39.4186 | 5.3654 | 1.3452 | 0.12724
0.59722 | 39.4186 | 5.2859 | 1.2908 | 0.12467
0.60417 | 39.4186 | 5.1248 | 1.0843 | 0.114
0.61111 | 39.4186 | 5.0074 | 0.90615 | 0.099022
0.61806 | 39.4186 | 4.9266 | 0.85397 | 0.093249
0.625 | 39.4186 | 4.9421 | 1.1447 | 0.10878
0.63194 | 39.4186 | 5.0186 | 1.3182 | 0.12296
0.63889 | 39.4186 | 5.0751 | 1.4347 | 0.13276
0.64583 | 39.4186 | 5.1061 | 1.3872 | 0.13186
0.65278 | 39.4186 | 5.2285 | 1.1936 | 0.11914
0.65972 | 39.4186 | 5.3582 | 1.0728 | 0.10904
0.66667 | 39.4186 | 5.3906 | 1.0654 | 0.10714
0.67361 | 39.4186 | 5.4277 | 1.1208 | 0.11047
0.68056 | 39.4186 | 5.5286 | 1.027 | 0.11302
0.6875 | 39.4186 | 5.9288 | 0.99924 | 0.14121
0.69444 | 39.4186 | 6.3814 | 1.0999 | 0.14804
0.70139 | 39.4186 | 6.4015 | 1.1828 | 0.15703
0.70833 | 39.4186 | 6.0531 | 1.1451 | 0.11514
0.71528 | 39.4186 | 5.679 | 1.0448 | 0.10652
0.72222 | 39.4186 | 5.4069 | 0.93663 | 0.099619
0.72917 | 39.4186 | 5.2615 | 0.85249 | 0.093847
0.73611 | 39.4186 | 5.2861 | 0.82549 | 0.096377
0.74306 | 39.4186 | 5.2274 | 0.82867 | 0.10425
0.75 | 39.4186 | 5.0775 | 0.83523 | 0.096695
0.75694 | 39.4186 | 4.9687 | 0.8371 | 0.091659
0.76389 | 39.4186 | 4.9222 | 0.81684 | 0.090709
0.77083 | 39.4186 | 5.0161 | 0.84947 | 0.093032
0.77778 | 39.4186 | 5.2213 | 0.88751 | 0.12931
0.78472 | 39.4186 | 5.4472 | 0.87934 | 0.12954
0.79167 | 39.4186 | 5.4413 | 0.85705 | 0.1271
0.79861 | 39.4186 | 5.3201 | 0.83152 | 0.12439
0.80556 | 39.4186 | 5.1675 | 0.80771 | 0.096403
0.8125 | 39.4186 | 5.0322 | 0.79858 | 0.092649
0.81944 | 39.4186 | 4.9338 | 0.85491 | 0.11717
0.82639 | 39.4186 | 4.932 | 0.92457 | 0.13146
0.83333 | 39.4186 | 5.6444 | 0.93631 | 0.13226
0.84028 | 39.4186 | 6.1665 | 1.0171 | 0.1382
0.84722 | 39.4186 | 6.5499 | 1.2294 | 0.12334
0.85417 | 39.4186 | 6.8325 | 1.7618 | 0.15638
0.86111 | 39.4186 | 7.043 | 2.1588 | 0.19537
0.86806 | 39.4186 | 6.5604 | 2.3823 | 0.2217
0.875 | 39.4186 | 6.0531 | 2.4163 | 0.22761
0.88194 | 39.4186 | 5.6951 | 2.3389 | 0.22396
0.88889 | 39.4186 | 5.7364 | 2.2542 | 0.24843
0.89583 | 39.4186 | 6.2018 | 2.263 | 0.29558
0.90278 | 39.4186 | 6.1481 | 2.3103 | 0.30735
0.90972 | 39.4186 | 5.9112 | 2.3049 | 0.31022
0.91667 | 39.4186 | 5.6545 | 2.2421 | 0.22097
0.92361 | 39.4186 | 5.4912 | 2.1509 | 0.19976
0.93056 | 39.4186 | 5.6082 | 2.0878 | 0.19888
0.9375 | 39.4186 | 6.012 | 1.7457 | 0.19343
0.94444 | 39.4186 | 6.0154 | 1.3935 | 0.15271
0.95139 | 39.4186 | 5.7417 | 1.1697 | 0.12439
0.95833 | 39.4186 | 5.4585 | 1.0189 | 0.11026
0.96528 | 39.4186 | 5.2507 | 1.0471 | 0.11118
0.97222 | 39.4186 | 5.0987 | 1.3024 | 0.1372
0.97917 | 39.4186 | 5.2545 | 1.4569 | 0.15854
0.98611 | 39.4186 | 5.8877 | 1.4267 | 0.14916
0.99306 | 39.4186 | 6.3515 | 1.3717 | 0.13948
1 | 39.4186 | 6.6917 | 1.3542 | 0.13347
1.0069 | 39.4186 | 6.9421 | 1.3556 | 0.12922
1.0139 | 39.4186 | 7.127 | 1.4316 | 0.13269
1.0208 | 39.4186 | 7.2641 | 1.6062 | 0.1453
1.0278 | 39.4186 | 7.26 | 1.9103 | 0.17192
1.0347 | 39.4186 | 7.367 | 2.3478 | 0.26207
1.0417 | 39.4186 | 7.4515 | 2.667 | 0.34013
1.0486 | 39.4186 | 7.5204 | 2.9059 | 0.39053
1.0556 | 39.4186 | 7.2856 | 3.049 | 0.3919
1.0625 | 39.4186 | 6.8699 | 3.0689 | 0.33471
1.0694 | 39.4186 | 6.617 | 3.0045 | 0.29982
1.0764 | 39.4186 | 6.9172 | 2.9728 | 0.28989
1.0833 | 39.4186 | 7.1369 | 3.012 | 0.29183
1.0903 | 39.4186 | 6.678 | 3.0009 | 0.29445
1.0972 | 39.4186 | 6.1605 | 2.8739 | 0.31133
1.1042 | 39.4186 | 5.7853 | 2.3594 | 0.34654
1.1111 | 39.4186 | 5.5128 | 1.7452 | 0.2207
1.1181 | 39.4186 | 5.3633 | 1.3171 | 0.13437
1.125 | 39.4186 | 5.3092 | 1.1125 | 0.11285
1.1319 | 39.4186 | 5.2828 | 1.0126 | 0.10443
1.1389 | 39.4186 | 5.4228 | 0.93868 | 0.10034
1.1458 | 39.4186 | 6.0133 | 0.95732 | 0.10059
1.1528 | 39.4186 | 6.4441 | 1.0677 | 0.10842
1.1597 | 39.4186 | 6.7598 | 1.2497 | 0.12549
1.1667 | 39.4186 | 6.9926 | 1.6429 | 0.15715
1.1736 | 39.4186 | 6.678 | 2.0494 | 0.19344
1.1806 | 39.4186 | 6.203 | 1.9963 | 0.19531
1.1875 | 39.4186 | 5.8088 | 1.8352 | 0.17784
1.1944 | 39.4186 | 5.5512 | 1.9049 | 0.18126
1.2014 | 39.4186 | 5.3872 | 1.9016 | 0.23009
1.2083 | 39.4186 | 5.2604 | 1.8648 | 0.24503
1.2153 | 39.4186 | 5.1676 | 1.6772 | 0.22794
1.2222 | 39.4186 | 5.1187 | 1.1865 | 0.13643
1.2292 | 39.4186 | 5.2368 | 0.93011 | 0.10314
1.2361 | 39.4186 | 5.8741 | 0.90204 | 0.096561
1.2431 | 39.4186 | 6.3384 | 0.99349 | 0.1
1.25 | 39.4186 | 6.6781 | 1.1371 | 0.10958
1.2569 | 39.4186 | 6.7431 | 1.2612 | 0.12009
1.2639 | 39.4186 | 6.6123 | 1.2995 | 0.12404
1.2708 | 39.4186 | 6.8829 | 1.3266 | 0.12587
1.2778 | 39.4186 | 7.0829 | 1.3758 | 0.12947
1.2847 | 39.4186 | 7.2304 | 1.4388 | 0.13431
1.2917 | 39.4186 | 7.3388 | 1.5008 | 0.14599
1.2986 | 39.4186 | 6.8825 | 1.5782 | 0.20274
1.3056 | 39.4186 | 6.3372 | 1.9532 | 0.23969
1.3125 | 39.4186 | 5.9571 | 2.0918 | 0.26784
1.3194 | 39.4186 | 5.8157 | 2.1246 | 0.27835
1.3264 | 39.4186 | 5.9828 | 2.1531 | 0.22535
1.3333 | 39.4186 | 6.2438 | 1.9075 | 0.19113
1.3403 | 39.4186 | 5.9531 | 1.9192 | 0.17755
1.3472 | 39.4186 | 5.6115 | 1.981 | 0.18023
1.3542 | 39.4186 | 5.3631 | 1.953 | 0.187
1.3611 | 39.4186 | 5.2276 | 1.5462 | 0.21606
1.3681 | 39.4186 | 5.7131 | 1.1813 | 0.17293
1.375 | 39.4186 | 6.2284 | 1.0933 | 0.13927
1.3819 | 39.4186 | 5.9557 | 1.0623 | 0.12665
1.3889 | 39.4186 | 5.6053 | 0.9845 | 0.1402
1.3958 | 39.4186 | 5.3503 | 0.93629 | 0.13519
1.4028 | 39.4186 | 5.1646 | 1.2553 | 0.1566
1.4097 | 39.4186 | 5.0301 | 1.4039 | 0.17711
1.4167 | 39.4186 | 4.9843 | 1.4731 | 0.18772
1.4236 | 39.4186 | 5.0675 | 1.521 | 0.19376
1.4306 | 39.4186 | 5.2552 | 1.1641 | 0.16694
1.4375 | 39.4186 | 5.2082 | 0.92448 | 0.10733
1.4444 | 39.4186 | 5.0579 | 0.80269 | 0.091041
1.4514 | 39.4186 | 4.9473 | 0.73415 | 0.086602
1.4583 | 39.4186 | 4.8662 | 0.69429 | 0.089309
1.4653 | 39.4186 | 4.8075 | 0.66974 | 0.10856
1.4722 | 39.4186 | 4.9292 | 0.67676 | 0.10965
1.4792 | 39.4186 | 5.6381 | 1.0989 | 0.13642
1.4861 | 39.4186 | 6.1582 | 1.5014 | 0.17786
1.4931 | 39.4186 | 6.5423 | 1.6511 | 0.2042
1.5 | 39.4186 | 6.828 | 1.5501 | 0.20303
1.5069 | 39.4186 | 6.4646 | 1.4269 | 0.19117
1.5139 | 39.4186 | 6.0675 | 1.2624 | 0.17357
1.5208 | 39.4186 | 5.8788 | 1.1234 | 0.15667
1.5278 | 39.4186 | 6.3439 | 1.113 | 0.15007
1.5347 | 39.4186 | 6.6842 | 1.1687 | 0.15395
1.5417 | 39.4186 | 6.9337 | 1.2553 | 0.15282
1.5486 | 39.4186 | 7.117 | 1.4041 | 0.13052
1.5556 | 39.4186 | 6.6958 | 1.6821 | 0.14853
1.5625 | 39.4186 | 6.1822 | 1.9775 | 0.1743
1.5694 | 39.4186 | 5.769 | 2.0635 | 0.19518
1.5764 | 39.4186 | 5.4719 | 2.0376 | 0.26339
1.5833 | 39.4186 | 5.2602 | 1.6592 | 0.2362
1.5903 | 39.4186 | 5.1077 | 1.1606 | 0.17691
1.5972 | 39.4186 | 4.9954 | 0.88805 | 0.13661
1.6042 | 39.4186 | 4.9106 | 0.75715 | 0.11872
1.6111 | 39.4186 | 4.9216 | 0.72841 | 0.11341
1.6181 | 39.4186 | 5.0054 | 0.87059 | 0.12252
1.625 | 39.4186 | 5.1001 | 1.1767 | 0.14253
1.6319 | 39.4186 | 5.4429 | 1.127 | 0.1149
1.6389 | 39.4186 | 6.0154 | 1.048 | 0.10768
1.6458 | 39.4186 | 6.4349 | 1.0773 | 0.11676
1.6528 | 39.4186 | 6.4915 | 1.1334 | 0.12589
1.6597 | 39.4186 | 6.2696 | 1.1477 | 0.12457
1.6667 | 39.4186 | 5.8704 | 1.1834 | 0.12634
1.6736 | 39.4186 | 5.5419 | 1.1778 | 0.12264
1.6806 | 39.4186 | 5.3779 | 1.1339 | 0.1234
1.6875 | 39.4186 | 5.2792 | 1.2479 | 0.16257
1.6944 | 39.4186 | 5.2104 | 1.1343 | 0.15808
1.7014 | 39.4186 | 5.3592 | 0.96939 | 0.14106
1.7083 | 39.4186 | 5.8985 | 0.96465 | 0.13477
1.7153 | 39.4186 | 6.0371 | 0.9888 | 0.13671
1.7222 | 39.4186 | 6.007 | 1.0033 | 0.13872
1.7292 | 39.4186 | 5.8591 | 1.0116 | 0.10483
1.7361 | 39.4186 | 5.5988 | 0.9985 | 0.10119
1.7431 | 39.4186 | 5.3974 | 0.94748 | 0.098935
1.75 | 39.4186 | 5.2693 | 0.97529 | 0.10023
1.7569 | 39.4186 | 5.1051 | 1.0885 | 0.10719
1.7639 | 39.4186 | 4.9794 | 1.1806 | 0.11545
1.7708 | 39.4186 | 4.8893 | 1.3219 | 0.1252
1.7778 | 39.4186 | 4.8253 | 1.3878 | 0.13331
1.7847 | 39.4186 | 4.8143 | 1.4189 | 0.1435
1.7917 | 39.4186 | 4.9701 | 1.4565 | 0.14835
1.7986 | 39.4186 | 5.1176 | 1.5138 | 0.14755
1.8056 | 39.4186 | 5.0844 | 1.5596 | 0.14666
1.8125 | 39.4186 | 4.9682 | 1.3344 | 0.13163
1.8194 | 39.4186 | 4.884 | 1.2554 | 0.1219
1.8264 | 39.4186 | 4.8228 | 1.3465 | 0.12692
1.8333 | 39.4186 | 4.7786 | 1.3888 | 0.13681
1.8403 | 39.4186 | 4.747 | 1.3235 | 0.14138
1.8472 | 39.4186 | 4.7854 | 0.9282 | 0.10975
1.8542 | 39.4186 | 4.9506 | 0.75879 | 0.08808
1.8611 | 39.4186 | 5.2576 | 0.74316 | 0.084686
1.8681 | 39.4186 | 5.6733 | 0.8057 | 0.088449
1.875 | 39.4186 | 6.1826 | 1.0529 | 0.1038
1.8819 | 39.4186 | 6.5575 | 1.5786 | 0.14825
1.8889 | 39.4186 | 6.6897 | 1.9594 | 0.23033
1.8958 | 39.4186 | 6.3047 | 2.1717 | 0.24828
1.9028 | 39.4186 | 5.8598 | 1.8146 | 0.21928
1.9097 | 39.4186 | 5.538 | 1.4283 | 0.17138
1.9167 | 39.4186 | 5.3845 | 1.1052 | 0.12005
1.9236 | 39.4186 | 5.6204 | 0.95772 | 0.10138
1.9306 | 39.4186 | 6.151 | 0.97338 | 0.10341
1.9375 | 39.4186 | 6.0329 | 1.0086 | 0.11655
1.9444 | 39.4186 | 5.6533 | 0.97038 | 0.11609
1.9514 | 39.4186 | 5.3777 | 0.89226 | 0.10179
1.9583 | 39.4186 | 5.1774 | 0.81677 | 0.090701
1.9653 | 39.4186 | 5.0776 | 0.76225 | 0.08706
1.9722 | 39.4186 | 5.2977 | 0.75969 | 0.086284
1.9792 | 39.4186 | 5.5564 | 0.80289 | 0.088672
1.9861 | 39.4186 | 5.468 | 0.85122 | 0.092193
1.9931 | 39.4186 | 5.2399 | 1.0693 | 0.10492
2 | 39.4186 | 5.0759 | 1.3071 | 0.12132
2.0069 | 39.4186 | 4.9588 | 1.415 | 0.13239
2.0139 | 39.4186 | 4.8753 | 1.0729 | 0.12063
2.0208 | 39.4186 | 4.8154 | 0.82129 | 0.1186
2.0278 | 39.4186 | 4.7794 | 0.7039 | 0.10645
2.0347 | 39.4186 | 4.8354 | 0.66825 | 0.10898
2.0417 | 39.4186 | 5.1945 | 0.77791 | 0.11504
2.0486 | 39.4186 | 5.8315 | 1.1696 | 0.14387
2.0556 | 39.4186 | 6.2991 | 1.5788 | 0.18554
2.0625 | 39.4186 | 6.6451 | 1.9249 | 0.22891
2.0694 | 39.4186 | 6.9028 | 2.2214 | 0.20008
2.0764 | 39.4186 | 6.6117 | 2.4097 | 0.21528
2.0833 | 39.4186 | 6.1117 | 2.4414 | 0.22479
2.0903 | 39.4186 | 5.7195 | 2.3588 | 0.22081
2.0972 | 39.4186 | 5.4365 | 2.2239 | 0.21466
2.1042 | 39.4186 | 5.2323 | 2.0761 | 0.20761
2.1111 | 39.4186 | 5.2268 | 1.955 | 0.19385
2.1181 | 39.4186 | 5.8704 | 1.5044 | 0.1507
2.125 | 39.4186 | 6.3399 | 1.3446 | 0.12903
2.1319 | 39.4186 | 6.6827 | 1.5013 | 0.1365
2.1389 | 39.4186 | 6.9344 | 1.8754 | 0.16304
2.1458 | 39.4186 | 6.7455 | 1.8407 | 0.17014
2.1528 | 39.4186 | 6.2111 | 1.5915 | 0.15863
2.1597 | 39.4186 | 5.7904 | 1.2924 | 0.1485
2.1667 | 39.4186 | 5.5189 | 1.0674 | 0.15472
2.1736 | 39.4186 | 5.8047 | 0.97314 | 0.14022
2.1806 | 39.4186 | 6.2888 | 1.035 | 0.14068
2.1875 | 39.4186 | 6.6426 | 1.2099 | 0.1549
2.1944 | 39.4186 | 6.9022 | 1.4143 | 0.17568
2.2014 | 39.4186 | 6.8144 | 1.4498 | 0.18638
2.2083 | 39.4186 | 6.5984 | 1.3697 | 0.18213
2.2153 | 39.4186 | 6.4037 | 1.3104 | 0.14139
2.2222 | 39.4186 | 6.1382 | 1.416 | 0.13191
2.2292 | 39.4186 | 5.8879 | 1.7102 | 0.1503
2.2361 | 39.4186 | 5.9712 | 1.7002 | 0.15561
2.2431 | 39.4186 | 6.4096 | 1.5162 | 0.14348
2.25 | 39.4186 | 6.7314 | 1.4867 | 0.13875
2.2569 | 39.4186 | 6.9683 | 1.9343 | 0.16833
2.2639 | 39.4186 | 7.1447 | 2.2963 | 0.20898
2.2708 | 39.4186 | 6.8979 | 2.5264 | 0.23469
2.2778 | 39.4186 | 6.5876 | 2.617 | 0.24483
2.2847 | 39.4186 | 6.3116 | 2.6103 | 0.25084
2.2917 | 39.4186 | 6.0555 | 2.5424 | 0.2464
2.2986 | 39.4186 | 6.0497 | 2.4677 | 0.23571
2.3056 | 39.4186 | 6.1874 | 2.4341 | 0.24106
2.3125 | 39.4186 | 6.0691 | 2.4094 | 0.25505
2.3194 | 39.4186 | 6.0454 | 2.3765 | 0.24956
2.3264 | 39.4186 | 6.4812 | 2.2933 | 0.30155
2.3333 | 39.4186 | 6.6501 | 2.064 | 0.2847
2.3403 | 39.4186 | 6.3942 | 1.8928 | 0.20923
2.3472 | 39.4186 | 6.0226 | 1.8268 | 0.17659
2.3542 | 39.4186 | 5.6598 | 1.9311 | 0.17621
2.3611 | 39.4186 | 5.3941 | 1.9259 | 0.17567
2.3681 | 39.4186 | 5.2002 | 1.8684 | 0.17187
2.375 | 39.4186 | 5.0584 | 1.7915 | 0.16555
2.3819 | 39.4186 | 4.9546 | 1.7129 | 0.16656
2.3889 | 39.4186 | 4.8793 | 1.6415 | 0.21263
2.3958 | 39.4186 | 4.9732 | 1.3377 | 0.18789
2.4028 | 39.4186 | 5.038 | 1.0142 | 0.12769
2.4097 | 39.4186 | 4.9869 | 0.83468 | 0.091022
2.4167 | 39.4186 | 4.9349 | 0.7628 | 0.085856
2.4236 | 39.4186 | 4.9419 | 0.75535 | 0.08559
2.4306 | 39.4186 | 4.9805 | 0.79114 | 0.11944
2.4375 | 39.4186 | 5.0784 | 0.82323 | 0.12229
2.4444 | 39.4186 | 5.2532 | 0.80027 | 0.12033
2.4514 | 39.4186 | 5.4544 | 0.80016 | 0.11928
2.4583 | 39.4186 | 5.9112 | 0.86624 | 0.096587
2.4653 | 39.4186 | 6.1968 | 0.96002 | 0.098557
2.4722 | 39.4186 | 6.0099 | 1.0019 | 0.11056
2.4792 | 39.4186 | 5.6815 | 1.0214 | 0.14211
2.4861 | 39.4186 | 5.3927 | 1.0679 | 0.14648
2.4931 | 39.4186 | 5.1841 | 1.256 | 0.12393
2.5 | 39.4186 | 5.0699 | 1.2428 | 0.11833
2.5069 | 39.4186 | 5.1164 | 1.2234 | 0.11728
2.5139 | 39.4186 | 5.2548 | 1.4044 | 0.1278
2.5208 | 39.4186 | 5.2444 | 1.2548 | 0.12557
2.5278 | 39.4186 | 5.0767 | 1.0727 | 0.11413
2.5347 | 39.4186 | 4.9556 | 1.0885 | 0.11229
2.5417 | 39.4186 | 4.8682 | 1.1591 | 0.12284
2.5486 | 39.4186 | 4.8057 | 1.0398 | 0.14682
2.5556 | 39.4186 | 4.7756 | 0.86925 | 0.13138
2.5625 | 39.4186 | 5.0842 | 0.80111 | 0.12069
2.5694 | 39.4186 | 5.7502 | 0.88072 | 0.12359
2.5764 | 39.4186 | 6.2371 | 1.0206 | 0.13549
2.5833 | 39.4186 | 6.595 | 1.1249 | 0.14699
2.5903 | 39.4186 | 6.8591 | 1.2155 | 0.13658
2.5972 | 39.4186 | 7.0542 | 1.3363 | 0.12703
2.6042 | 39.4186 | 7.1988 | 1.6371 | 0.14776
2.6111 | 39.4186 | 6.703 | 2.0645 | 0.18778
2.6181 | 39.4186 | 6.1823 | 2.2266 | 0.21513
2.625 | 39.4186 | 5.765 | 2.2253 | 0.24205
2.6319 | 39.4186 | 5.5671 | 1.6722 | 0.21241
2.6389 | 39.4186 | 5.6644 | 1.3266 | 0.15179
2.6458 | 39.4186 | 5.6232 | 1.2376 | 0.13791
2.6528 | 39.4186 | 5.4608 | 1.2752 | 0.13909
2.6597 | 39.4186 | 5.3674 | 1.441 | 0.14668
2.6667 | 39.4186 | 5.559 | 1.5098 | 0.1522
2.6736 | 39.4186 | 6.1046 | 1.5203 | 0.14914
2.6806 | 39.4186 | 6.5046 | 1.8481 | 0.16408
2.6875 | 39.4186 | 6.6826 | 2.1253 | 0.18848
2.6944 | 39.4186 | 6.786 | 2.3428 | 0.21046
2.7014 | 39.4186 | 7.0119 | 2.3401 | 0.21452
2.7083 | 39.4186 | 7.1806 | 2.2462 | 0.20827
2.7153 | 39.4186 | 7.2426 | 2.0521 | 0.19249
2.7222 | 39.4186 | 7.3528 | 1.9537 | 0.18286
2.7292 | 39.4186 | 7.4347 | 2.2391 | 0.21848
2.7361 | 39.4186 | 7.4753 | 2.5964 | 0.3208
2.7431 | 39.4186 | 7.1522 | 2.8028 | 0.37253
2.75 | 39.4186 | 6.6002 | 2.8376 | 0.396
2.7569 | 39.4186 | 6.1073 | 2.7366 | 0.39202
2.7639 | 39.4186 | 5.7996 | 2.5725 | 0.36886
2.7708 | 39.4186 | 5.537 | 2.391 | 0.3382
2.7778 | 39.4186 | 5.3206 | 2.2096 | 0.25349
2.7847 | 39.4186 | 5.159 | 2.0423 | 0.19835
2.7917 | 39.4186 | 5.0909 | 1.5855 | 0.15439
2.7986 | 39.4186 | 5.1227 | 1.2857 | 0.12639
2.8056 | 39.4186 | 5.17 | 1.1656 | 0.11509
2.8125 | 39.4186 | 5.1323 | 1.0524 | 0.1084
2.8194 | 39.4186 | 5.1084 | 0.90722 | 0.10107
2.8264 | 39.4186 | 5.4611 | 0.82929 | 0.093987
2.8333 | 39.4186 | 6.0291 | 0.88956 | 0.09291
2.8403 | 39.4186 | 6.4443 | 1.0058 | 0.10035
2.8472 | 39.4186 | 6.7494 | 1.3102 | 0.11941
2.8542 | 39.4186 | 6.9753 | 1.8437 | 0.15677
2.8611 | 39.4186 | 6.466 | 2.1436 | 0.18904
2.8681 | 39.4186 | 5.968 | 2.2243 | 0.21071
2.875 | 39.4186 | 5.6091 | 1.9709 | 0.19873
2.8819 | 39.4186 | 5.3499 | 1.6133 | 0.16308
2.8889 | 39.4186 | 5.2051 | 1.3368 | 0.13706
2.8958 | 39.4186 | 5.0867 | 1.0647 | 0.13154
2.9028 | 39.4186 | 4.9674 | 0.85614 | 0.13129
2.9097 | 39.4186 | 4.8929 | 0.73711 | 0.11733
2.9167 | 39.4186 | 5.0892 | 0.71143 | 0.11179
2.9236 | 39.4186 | 5.7543 | 0.78869 | 0.10789
2.9306 | 39.4186 | 6.2395 | 0.91983 | 0.097684
2.9375 | 39.4186 | 6.5947 | 1.0531 | 0.10857
2.9444 | 39.4186 | 6.8566 | 1.1894 | 0.12704
2.9514 | 39.4186 | 7.0516 | 1.3634 | 0.17147
2.9583 | 39.4186 | 7.1984 | 1.5288 | 0.19126
2.9653 | 39.4186 | 7.3097 | 1.713 | 0.21197
2.9722 | 39.4186 | 7.1645 | 1.7218 | 0.22094
2.9792 | 39.4186 | 6.6214 | 1.5559 | 0.20922
2.9861 | 39.4186 | 6.1558 | 1.3603 | 0.18665
2.9931 | 39.4186 | 5.9334 | 1.2133 | 0.12873
3 | 39.4186 | 5.8785 | 1.0925 | 0.1086
3.0069 | 39.4186 | 5.8121 | 1.0302 | 0.10414
3.0139 | 39.4186 | 5.6213 | 0.97404 | 0.10085
3.0208 | 39.4186 | 5.3858 | 0.88833 | 0.095805
3.0278 | 39.4186 | 5.2214 | 0.81689 | 0.096108
3.0347 | 39.4186 | 5.1789 | 0.77293 | 0.10089
3.0417 | 39.4186 | 5.3122 | 0.80748 | 0.092648
3.0486 | 39.4186 | 5.6866 | 1.0026 | 0.10021
3.0556 | 39.4186 | 6.1903 | 1.4478 | 0.12925
3.0625 | 39.4186 | 6.5613 | 1.6819 | 0.15343
3.0694 | 39.4186 | 6.8363 | 1.605 | 0.15166
3.0764 | 39.4186 | 7.0406 | 1.5384 | 0.14294
3.0833 | 39.4186 | 6.8054 | 1.5373 | 0.14235
3.0903 | 39.4186 | 6.2128 | 1.5494 | 0.14385
3.0972 | 39.4186 | 5.782 | 1.5285 | 0.14579
3.1042 | 39.4186 | 5.4696 | 1.4999 | 0.14754
3.1111 | 39.4186 | 5.2576 | 1.3542 | 0.13263
3.1181 | 39.4186 | 5.8827 | 1.3489 | 0.12634
3.125 | 39.4186 | 6.34 | 1.6966 | 0.14749
3.1319 | 39.4186 | 6.6763 | 2.0074 | 0.17684
3.1389 | 39.4186 | 6.2325 | 2.1833 | 0.22083
3.1458 | 39.4186 | 5.7992 | 1.7064 | 0.19253
3.1528 | 39.4186 | 5.4855 | 1.274 | 0.14126
3.1597 | 39.4186 | 5.2565 | 0.99624 | 0.11877
3.1667 | 39.4186 | 5.0883 | 0.89608 | 0.10664
3.1736 | 39.4186 | 4.9643 | 1.1669 | 0.11788
3.1806 | 39.4186 | 5.2072 | 1.3492 | 0.16124
3.1875 | 39.4186 | 5.843 | 1.2265 | 0.16509
3.1944 | 39.4186 | 6.3093 | 1.1443 | 0.15512
3.2014 | 39.4186 | 6.6514 | 1.1671 | 0.15393
3.2083 | 39.4186 | 6.903 | 1.2389 | 0.14331
3.2153 | 39.4186 | 7.0588 | 1.3183 | 0.12355
3.2222 | 39.4186 | 6.8307 | 1.3639 | 0.12889
3.2292 | 39.4186 | 6.44 | 1.301 | 0.13287
3.2361 | 39.4186 | 6.002 | 1.1933 | 0.12841
3.2431 | 39.4186 | 5.6935 | 1.1379 | 0.1229
3.25 | 39.4186 | 5.6062 | 1.3342 | 0.12767
3.2569 | 39.4186 | 5.5587 | 1.5594 | 0.13937
3.2639 | 39.4186 | 5.5179 | 1.688 | 0.15182
3.2708 | 39.4186 | 5.4954 | 1.7619 | 0.16677
3.2778 | 39.4186 | 5.4013 | 1.3419 | 0.14474
3.2847 | 39.4186 | 5.3061 | 1.0377 | 0.11178
3.2917 | 39.4186 | 5.3494 | 0.88442 | 0.095305
3.2986 | 39.4186 | 5.318 | 0.82187 | 0.090383
3.3056 | 39.4186 | 5.1865 | 0.7813 | 0.08913
3.3125 | 39.4186 | 5.1591 | 0.76909 | 0.09441
3.3194 | 39.4186 | 5.3264 | 0.76805 | 0.11812
3.3264 | 39.4186 | 5.5598 | 0.80386 | 0.12011
3.3333 | 39.4186 | 5.8257 | 0.86409 | 0.12419
3.3403 | 39.4186 | 5.8169 | 0.9069 | 0.12862
3.3472 | 39.4186 | 5.5399 | 0.90341 | 0.12968
3.3542 | 39.4186 | 5.2849 | 0.95337 | 0.12492
3.3611 | 39.4186 | 5.0999 | 0.94211 | 0.11002
3.3681 | 39.4186 | 5.0831 | 0.90219 | 0.10952
3.375 | 39.4186 | 5.5433 | 0.89968 | 0.12808
3.3819 | 39.4186 | 6.0829 | 0.95754 | 0.13221
3.3889 | 39.4186 | 6.479 | 1.0511 | 0.14018
3.3958 | 39.4186 | 6.7708 | 1.1614 | 0.1508
3.4028 | 39.4186 | 6.5447 | 1.2297 | 0.12922
3.4097 | 39.4186 | 6.0768 | 1.1996 | 0.11567
3.4167 | 39.4186 | 5.785 | 1.1194 | 0.11075
3.4236 | 39.4186 | 5.7663 | 1.0492 | 0.10584
3.4306 | 39.4186 | 5.8422 | 1.0286 | 0.10492
3.4375 | 39.4186 | 5.6952 | 1.0636 | 0.10767
3.4444 | 39.4186 | 5.398 | 1.2722 | 0.11996
3.4514 | 39.4186 | 5.1836 | 1.4517 | 0.13622
3.4583 | 39.4186 | 5.0299 | 1.5176 | 0.1506
3.4653 | 39.4186 | 4.9203 | 1.3232 | 0.16029
3.4722 | 39.4186 | 5.4871 | 1.4349 | 0.18077
3.4792 | 39.4186 | 6.0483 | 1.6693 | 0.16167
3.4861 | 39.4186 | 6.4599 | 1.9283 | 0.17157
3.4931 | 39.4186 | 6.7632 | 1.8401 | 0.17167
3.5 | 39.4186 | 6.9877 | 1.6259 | 0.15435
3.5069 | 39.4186 | 6.7412 | 1.4938 | 0.14057
3.5139 | 39.4186 | 6.3531 | 1.3506 | 0.13007
3.5208 | 39.4186 | 6.0206 | 1.2002 | 0.11912
3.5278 | 39.4186 | 5.8619 | 1.1605 | 0.11542
3.5347 | 39.4186 | 5.8485 | 1.181 | 0.12846
3.5417 | 39.4186 | 5.9594 | 1.1577 | 0.15664
3.5486 | 39.4186 | 6.3966 | 1.1722 | 0.12398
3.5556 | 39.4186 | 6.7164 | 1.2466 | 0.12233
3.5625 | 39.4186 | 6.9509 | 1.395 | 0.13273
3.5694 | 39.4186 | 7.1241 | 1.5536 | 0.14371
3.5764 | 39.4186 | 7.0154 | 1.6382 | 0.15775
3.5833 | 39.4186 | 6.7325 | 1.7509 | 0.20279
3.5903 | 39.4186 | 6.6155 | 2.0781 | 0.253
3.5972 | 39.4186 | 6.3903 | 2.2528 | 0.28573
3.6042 | 39.4186 | 5.9954 | 2.2478 | 0.29674
3.6111 | 39.4186 | 5.6353 | 2.1543 | 0.28906
3.6181 | 39.4186 | 5.3749 | 1.9884 | 0.26859
3.625 | 39.4186 | 5.1858 | 1.8045 | 0.24282
3.6319 | 39.4186 | 5.0465 | 1.6705 | 0.16
3.6389 | 39.4186 | 4.9415 | 1.4037 | 0.13401
3.6458 | 39.4186 | 5.0595 | 1.0949 | 0.11123
3.6528 | 39.4186 | 5.7362 | 1.044 | 0.10367
3.6597 | 39.4186 | 6.2296 | 1.4811 | 0.1314
3.6667 | 39.4186 | 6.5923 | 1.8438 | 0.20017
3.6736 | 39.4186 | 6.8626 | 2.1515 | 0.26033
3.6806 | 39.4186 | 6.5606 | 2.3458 | 0.29703
3.6875 | 39.4186 | 6.1128 | 1.964 | 0.21551
3.6944 | 39.4186 | 5.7147 | 1.4764 | 0.15426
3.7014 | 39.4186 | 5.4231 | 1.1349 | 0.12575
3.7083 | 39.4186 | 5.209 | 0.96605 | 0.14035
3.7153 | 39.4186 | 5.0522 | 1.2382 | 0.15616
3.7222 | 39.4186 | 4.9373 | 1.364 | 0.13215
3.7292 | 39.4186 | 4.9989 | 1.4345 | 0.13035
3.7361 | 39.4186 | 5.6879 | 1.5718 | 0.13944
3.7431 | 39.4186 | 6.1923 | 1.4604 | 0.1357
3.75 | 39.4186 | 6.5627 | 1.542 | 0.13921
3.7569 | 39.4186 | 6.4144 | 1.767 | 0.15611
3.7639 | 39.4186 | 6.0156 | 1.9719 | 0.18206
3.7708 | 39.4186 | 5.8456 | 1.8317 | 0.18056
3.7778 | 39.4186 | 6.3154 | 1.4751 | 0.14536
3.7847 | 39.4186 | 6.6596 | 1.3379 | 0.12754
3.7917 | 39.4186 | 6.9114 | 1.3274 | 0.12666
3.7986 | 39.4186 | 6.8403 | 1.3785 | 0.13601
3.8056 | 39.4186 | 6.3591 | 1.581 | 0.15544
3.8125 | 39.4186 | 6.0106 | 1.8485 | 0.17362
3.8194 | 39.4186 | 5.9208 | 1.9736 | 0.18244
3.8264 | 39.4186 | 5.8693 | 2.0391 | 0.18692
3.8333 | 39.4186 | 5.7714 | 2.0637 | 0.18962
3.8403 | 39.4186 | 5.712 | 2.0617 | 0.18906
3.8472 | 39.4186 | 5.8975 | 2.0786 | 0.19311
3.8542 | 39.4186 | 6.3573 | 2.1699 | 0.21618
3.8611 | 39.4186 | 6.6966 | 2.0339 | 0.26484
3.8681 | 39.4186 | 6.3883 | 1.7133 | 0.23834
3.875 | 39.4186 | 6.0065 | 1.438 | 0.1914
3.8819 | 39.4186 | 5.9573 | 1.2574 | 0.13129
3.8889 | 39.4186 | 6.3999 | 1.2206 | 0.11693
3.8958 | 39.4186 | 6.7217 | 1.3613 | 0.12422
3.9028 | 39.4186 | 6.9567 | 1.7249 | 0.14928
3.9097 | 39.4186 | 6.8914 | 2.1176 | 0.18693
3.9167 | 39.4186 | 6.4945 | 2.3192 | 0.21357
3.9236 | 39.4186 | 6.2111 | 2.3763 | 0.23005
3.9306 | 39.4186 | 5.8529 | 2.3377 | 0.23252
3.9375 | 39.4186 | 5.5259 | 2.2303 | 0.21485
3.9444 | 39.4186 | 5.3217 | 2.0961 | 0.20165
3.9514 | 39.4186 | 5.4318 | 1.8593 | 0.18097
3.9583 | 39.4186 | 5.6099 | 1.4781 | 0.14839
3.9653 | 39.4186 | 5.5835 | 1.2547 | 0.1283
3.9722 | 39.4186 | 5.3439 | 1.1448 | 0.12257
3.9792 | 39.4186 | 5.1479 | 1.0377 | 0.12506
3.9861 | 39.4186 | 5.0049 | 0.9467 | 0.12746
3.9931 | 39.4186 | 4.9361 | 0.84244 | 0.10179
4 | 39.4186 | 5.0432 | 0.74913 | 0.086056
4.0069 | 39.4186 | 5.2155 | 0.73656 | 0.08374
4.0139 | 39.4186 | 5.3204 | 0.78216 | 0.08654
4.0208 | 39.4186 | 5.2798 | 0.93121 | 0.095388
4.0278 | 39.4186 | 5.1923 | 1.2417 | 0.12846
4.0347 | 39.4186 | 5.1713 | 1.4085 | 0.17687
4.0417 | 39.4186 | 5.2338 | 1.5142 | 0.19123
4.0486 | 39.4186 | 5.2937 | 1.5931 | 0.20051
4.0556 | 39.4186 | 5.298 | 1.2174 | 0.17321
4.0625 | 39.4186 | 5.1831 | 0.94 | 0.13978
4.0694 | 39.4186 | 5.0952 | 0.80259 | 0.12178
4.0764 | 39.4186 | 5.1262 | 0.74865 | 0.11459
4.0833 | 39.4186 | 5.2845 | 0.74939 | 0.10238
4.0903 | 39.4186 | 5.6156 | 0.92367 | 0.096936
4.0972 | 39.4186 | 5.6867 | 1.0999 | 0.11226
4.1042 | 39.4186 | 5.4725 | 0.99129 | 0.14077
4.1111 | 39.4186 | 5.2679 | 0.86578 | 0.12965
4.1181 | 39.4186 | 5.2595 | 0.79969 | 0.12082
4.125 | 39.4186 | 5.8736 | 0.84295 | 0.1209
4.1319 | 39.4186 | 6.3232 | 0.95681 | 0.12995
4.1389 | 39.4186 | 6.6531 | 1.1387 | 0.11879
4.1458 | 39.4186 | 6.8962 | 1.3187 | 0.12626
4.1528 | 39.4186 | 7.0765 | 1.4807 | 0.14354
4.1597 | 39.4186 | 7.212 | 1.8712 | 0.19386
4.1667 | 39.4186 | 7.3162 | 2.2968 | 0.27358
4.1736 | 39.4186 | 7.0369 | 2.5577 | 0.32464
4.1806 | 39.4186 | 6.8373 | 2.6807 | 0.35539
4.1875 | 39.4186 | 7.0591 | 2.775 | 0.37428
4.1944 | 39.4186 | 7.2255 | 2.7793 | 0.29166
4.2014 | 39.4186 | 7.2117 | 2.9062 | 0.27162
4.2083 | 39.4186 | 6.6226 | 2.9142 | 0.27715
4.2153 | 39.4186 | 6.0961 | 2.526 | 0.2487
4.2222 | 39.4186 | 5.7424 | 1.9473 | 0.19378
4.2292 | 39.4186 | 5.588 | 1.4423 | 0.1445
4.2361 | 39.4186 | 5.4272 | 1.1064 | 0.11772
4.2431 | 39.4186 | 5.2133 | 0.90703 | 0.10429
4.25 | 39.4186 | 5.055 | 0.78958 | 0.10002
4.2569 | 39.4186 | 4.9678 | 0.72503 | 0.094576
4.2639 | 39.4186 | 4.9691 | 0.81929 | 0.091251
4.2708 | 39.4186 | 5.1481 | 1.1466 | 0.10818
4.2778 | 39.4186 | 5.7787 | 1.4254 | 0.13039
4.2847 | 39.4186 | 6.2571 | 1.7174 | 0.15511
4.2917 | 39.4186 | 6.6098 | 1.6722 | 0.15806
4.2986 | 39.4186 | 6.871 | 1.6236 | 0.15256
4.3056 | 39.4186 | 7.0646 | 1.6126 | 0.15147
4.3125 | 39.4186 | 7.2086 | 1.6593 | 0.16396
4.3194 | 39.4186 | 7.1553 | 1.7879 | 0.21458
4.3264 | 39.4186 | 6.7317 | 2.1589 | 0.26215
4.3333 | 39.4186 | 6.3563 | 2.3124 | 0.2295
4.3403 | 39.4186 | 6.1065 | 2.3431 | 0.21532
4.3472 | 39.4186 | 5.8492 | 2.2279 | 0.20734
4.3542 | 39.4186 | 5.5956 | 1.7494 | 0.18086
4.3611 | 39.4186 | 5.3864 | 1.3471 | 0.15994
4.3681 | 39.4186 | 5.2391 | 1.0697 | 0.15507
4.375 | 39.4186 | 5.1608 | 0.98047 | 0.13308
4.3819 | 39.4186 | 5.0951 | 1.0269 | 0.12357
4.3889 | 39.4186 | 4.9738 | 1.249 | 0.15675
4.3958 | 39.4186 | 4.8761 | 1.3522 | 0.17154
4.4028 | 39.4186 | 4.8055 | 1.394 | 0.1779
4.4097 | 39.4186 | 4.8636 | 1.4189 | 0.18069
4.4167 | 39.4186 | 5.145 | 1.0952 | 0.14584
4.4236 | 39.4186 | 5.5396 | 0.93766 | 0.10012
4.4306 | 39.4186 | 6.0788 | 0.95641 | 0.095808
4.4375 | 39.4186 | 6.4731 | 1.1614 | 0.10829
4.4444 | 39.4186 | 6.7634 | 1.6908 | 0.14293
4.4514 | 39.4186 | 6.9797 | 2.0833 | 0.18306
4.4583 | 39.4186 | 6.6292 | 1.9216 | 0.2504
4.4653 | 39.4186 | 6.2194 | 1.5759 | 0.22134
4.4722 | 39.4186 | 5.9933 | 1.302 | 0.18287
4.4792 | 39.4186 | 6.425 | 1.2878 | 0.16877
4.4861 | 39.4186 | 6.7406 | 1.7634 | 0.19812
4.4931 | 39.4186 | 6.972 | 2.1293 | 0.19158
4.5 | 39.4186 | 7.1427 | 2.228 | 0.2012
4.5069 | 39.4186 | 7.2698 | 2.165 | 0.20565
4.5139 | 39.4186 | 7.3652 | 2.0735 | 0.2091
4.5208 | 39.4186 | 7.4373 | 2.0399 | 0.21476
4.5278 | 39.4186 | 7.4925 | 2.0722 | 0.2634
4.5347 | 39.4186 | 7.2718 | 2.0302 | 0.26687
4.5417 | 39.4186 | 6.7608 | 1.9202 | 0.18993
4.5486 | 39.4186 | 6.3878 | 1.894 | 0.17403
4.5556 | 39.4186 | 6.3345 | 1.9431 | 0.17461
4.5625 | 39.4186 | 6.5399 | 2.151 | 0.1896
4.5694 | 39.4186 | 6.8303 | 2.3491 | 0.20862
4.5764 | 39.4186 | 7.0447 | 2.542 | 0.24961
4.5833 | 39.4186 | 6.7272 | 2.6545 | 0.2977
4.5903 | 39.4186 | 6.4219 | 2.5325 | 0.27397
4.5972 | 39.4186 | 6.3252 | 2.1743 | 0.2429
4.6042 | 39.4186 | 6.5245 | 1.9483 | 0.19924
4.6111 | 39.4186 | 6.5867 | 1.968 | 0.18944
4.6181 | 39.4186 | 6.4328 | 1.8926 | 0.21526
4.625 | 39.4186 | 6.1019 | 1.7272 | 0.2293
4.6319 | 39.4186 | 5.8016 | 1.693 | 0.17021
4.6389 | 39.4186 | 5.6778 | 1.7309 | 0.15921
4.6458 | 39.4186 | 5.7034 | 1.6268 | 0.15203
4.6528 | 39.4186 | 5.6971 | 1.4121 | 0.1366
4.6597 | 39.4186 | 5.6003 | 1.1592 | 0.12159
4.6667 | 39.4186 | 5.4759 | 0.97231 | 0.10775
4.6736 | 39.4186 | 5.2641 | 0.88108 | 0.097383
4.6806 | 39.4186 | 5.0824 | 0.91035 | 0.09801
4.6875 | 39.4186 | 4.95 | 0.9336 | 0.10198
4.6944 | 39.4186 | 4.9088 | 0.79978 | 0.097094
4.7014 | 39.4186 | 5.0881 | 0.72916 | 0.092023
4.7083 | 39.4186 | 5.2294 | 0.73263 | 0.086917
4.7153 | 39.4186 | 5.143 | 0.73441 | 0.086442
4.7222 | 39.4186 | 4.9891 | 0.86151 | 0.10028
4.7292 | 39.4186 | 4.8787 | 1.1358 | 0.1243
4.7361 | 39.4186 | 4.8 | 1.1257 | 0.12426
4.7431 | 39.4186 | 4.7741 | 0.83838 | 0.12093
4.75 | 39.4186 | 4.7556 | 0.69603 | 0.11302
4.7569 | 39.4186 | 4.711 | 0.64816 | 0.10641
4.7639 | 39.4186 | 4.6778 | 0.74462 | 0.1117
4.7708 | 39.4186 | 4.6527 | 1.0177 | 0.10285
4.7778 | 39.4186 | 4.6545 | 1.1591 | 0.10864
4.7847 | 39.4186 | 4.8806 | 1.1784 | 0.112
4.7917 | 39.4186 | 5.2945 | 0.92835 | 0.099467
4.7986 | 39.4186 | 5.3004 | 0.82613 | 0.10314
4.8056 | 39.4186 | 5.2034 | 0.798 | 0.12037
4.8125 | 39.4186 | 5.2062 | 0.8353 | 0.12204
4.8194 | 39.4186 | 5.701 | 1.1016 | 0.14007
4.8264 | 39.4186 | 6.1956 | 1.505 | 0.17646
4.8333 | 39.4186 | 6.5605 | 1.6398 | 0.20103
4.8403 | 39.4186 | 6.5762 | 1.8069 | 0.22154
4.8472 | 39.4186 | 6.1736 | 2.0324 | 0.24916
4.8542 | 39.4186 | 5.9768 | 2.1141 | 0.26737
4.8611 | 39.4186 | 6.4129 | 2.206 | 0.27915
4.8681 | 39.4186 | 6.7354 | 2.3563 | 0.29812
4.875 | 39.4186 | 6.975 | 2.5243 | 0.3229
4.8819 | 39.4186 | 7.1547 | 2.6896 | 0.30624
4.8889 | 39.4186 | 6.9687 | 2.7987 | 0.27385
4.8958 | 39.4186 | 6.5756 | 2.8027 | 0.26843
4.9028 | 39.4186 | 6.2311 | 2.718 | 0.27407
4.9097 | 39.4186 | 5.9401 | 2.5838 | 0.34695
4.9167 | 39.4186 | 5.7242 | 2.1856 | 0.31507
4.9236 | 39.4186 | 5.7033 | 1.8385 | 0.25952
4.9306 | 39.4186 | 6.0521 | 1.4668 | 0.20602
4.9375 | 39.4186 | 6.4774 | 1.2837 | 0.17398
4.9444 | 39.4186 | 6.7523 | 1.2593 | 0.15349
4.9514 | 39.4186 | 6.517 | 1.2423 | 0.12221
4.9583 | 39.4186 | 6.0871 | 1.2261 | 0.11663
4.9653 | 39.4186 | 5.6816 | 1.1493 | 0.11273
4.9722 | 39.4186 | 5.3856 | 0.98676 | 0.1027
4.9792 | 39.4186 | 5.1719 | 0.84511 | 0.092925
4.9861 | 39.4186 | 5.1977 | 0.77657 | 0.089227
4.9931 | 39.4186 | 5.514 | 0.81334 | 0.10427
5 | 39.4186 | 5.7579 | 1.0453 | 0.13644
5.0069 | 39.4186 | 5.6633 | 1.4102 | 0.13915
5.0139 | 39.4186 | 5.3938 | 1.4147 | 0.15126
5.0208 | 39.4186 | 5.1746 | 1.1382 | 0.16083
5.0278 | 39.4186 | 5.0168 | 0.8736 | 0.13358
5.0347 | 39.4186 | 4.9207 | 0.74409 | 0.1167
5.0417 | 39.4186 | 4.9888 | 0.69945 | 0.088056
5.0486 | 39.4186 | 5.1788 | 0.74616 | 0.084343
5.0556 | 39.4186 | 5.1778 | 0.88646 | 0.091822
5.0625 | 39.4186 | 5.1167 | 1.1288 | 0.1085
5.0694 | 39.4186 | 5.0745 | 1.193 | 0.12266
5.0764 | 39.4186 | 5.0072 | 1.0215 | 0.14568
5.0833 | 39.4186 | 5.0515 | 0.89297 | 0.13184
5.0903 | 39.4186 | 5.3153 | 0.83509 | 0.11436
5.0972 | 39.4186 | 5.3481 | 0.80785 | 0.091486
5.1042 | 39.4186 | 5.1903 | 0.79767 | 0.087045
5.1111 | 39.4186 | 5.0204 | 0.88397 | 0.092254
5.1181 | 39.4186 | 4.8981 | 1.1521 | 0.11207
5.125 | 39.4186 | 4.8111 | 1.2785 | 0.133
5.1319 | 39.4186 | 4.7641 | 1.3368 | 0.14189
5.1389 | 39.4186 | 4.9478 | 1.3899 | 0.16762
5.1458 | 39.4186 | 5.4801 | 1.1701 | 0.16099
5.1528 | 39.4186 | 5.7802 | 1.0199 | 0.14325
5.1597 | 39.4186 | 6.0237 | 0.98657 | 0.1178
5.1667 | 39.4186 | 6.0626 | 1.0238 | 0.10255
5.1736 | 39.4186 | 5.7439 | 1.0316 | 0.10244
5.1806 | 39.4186 | 5.4433 | 0.93914 | 0.0981
5.1875 | 39.4186 | 5.2848 | 0.84225 | 0.09553
5.1944 | 39.4186 | 5.1456 | 0.7775 | 0.09918
5.2014 | 39.4186 | 5.1521 | 0.74492 | 0.09291
5.2083 | 39.4186 | 5.5702 | 0.78758 | 0.08997
5.2153 | 39.4186 | 5.6099 | 0.87059 | 0.096197
5.2222 | 39.4186 | 5.4117 | 0.84909 | 0.097718
5.2292 | 39.4186 | 5.1933 | 0.80047 | 0.094123
5.2361 | 39.4186 | 5.0243 | 0.79254 | 0.09255
5.2431 | 39.4186 | 4.9023 | 0.75853 | 0.091916
5.25 | 39.4186 | 4.8143 | 0.73399 | 0.089537
5.2569 | 39.4186 | 4.8144 | 0.74005 | 0.086526
5.2639 | 39.4186 | 4.9227 | 0.72489 | 0.084722
5.2708 | 39.4186 | 5.2167 | 0.75235 | 0.085692
5.2778 | 39.4186 | 5.3456 | 0.81655 | 0.088715
5.2847 | 39.4186 | 5.3536 | 0.9275 | 0.096755
5.2917 | 39.4186 | 5.457 | 1.278 | 0.12434
5.2986 | 39.4186 | 6.0166 | 1.5631 | 0.14402
5.3056 | 39.4186 | 6.4288 | 1.7623 | 0.15774
5.3125 | 39.4186 | 6.7338 | 1.8656 | 0.17406
5.3194 | 39.4186 | 6.9608 | 1.7612 | 0.17743
5.3264 | 39.4186 | 6.7537 | 1.6177 | 0.15856
5.3333 | 39.4186 | 6.2164 | 1.4374 | 0.14133
5.3403 | 39.4186 | 5.7757 | 1.2056 | 0.12508
5.3472 | 39.4186 | 5.4549 | 1.0215 | 0.11034
5.3542 | 39.4186 | 5.2208 | 0.94449 | 0.10485
5.3611 | 39.4186 | 5.05 | 0.86258 | 0.10041
5.3681 | 39.4186 | 4.9251 | 0.74437 | 0.087573
5.375 | 39.4186 | 4.9176 | 0.69311 | 0.081925
5.3819 | 39.4186 | 5.2955 | 0.71641 | 0.082518
5.3889 | 39.4186 | 5.8966 | 0.81603 | 0.087883
5.3958 | 39.4186 | 6.3372 | 0.94751 | 0.097678
5.4028 | 39.4186 | 6.6617 | 1.0757 | 0.10877
5.4097 | 39.4186 | 6.9019 | 1.1908 | 0.11962
5.4167 | 39.4186 | 7.0808 | 1.2903 | 0.13715
5.4236 | 39.4186 | 6.6763 | 1.308 | 0.14219
5.4306 | 39.4186 | 6.1371 | 1.216 | 0.12512
5.4375 | 39.4186 | 5.7151 | 1.0732 | 0.11272
5.4444 | 39.4186 | 5.4083 | 0.94094 | 0.10261
5.4514 | 39.4186 | 5.1848 | 0.91404 | 0.099869
5.4583 | 39.4186 | 5.0224 | 1.2014 | 0.12274
5.4653 | 39.4186 | 4.9729 | 1.3416 | 0.14008
5.4722 | 39.4186 | 4.9605 | 1.417 | 0.14048
5.4792 | 39.4186 | 4.9485 | 1.459 | 0.14394
5.4861 | 39.4186 | 5.105 | 1.5032 | 0.18908
5.4931 | 39.4186 | 5.3809 | 1.2738 | 0.17425
5.5 | 39.4186 | 5.614 | 1.1152 | 0.15386
5.5069 | 39.4186 | 5.905 | 1.1525 | 0.151
5.5139 | 39.4186 | 5.9019 | 1.5165 | 0.17955
5.5208 | 39.4186 | 5.7407 | 1.7186 | 0.20526
5.5278 | 39.4186 | 5.6587 | 1.82 | 0.17226
5.5347 | 39.4186 | 5.6828 | 1.8803 | 0.16858
5.5417 | 39.4186 | 5.5351 | 1.7356 | 0.15922
5.5486 | 39.4186 | 5.2954 | 1.3498 | 0.13261
5.5556 | 39.4186 | 5.1046 | 1.088 | 0.11069
5.5625 | 39.4186 | 4.9714 | 0.94442 | 0.10184
5.5694 | 39.4186 | 4.9123 | 0.8296 | 0.10723
5.5764 | 39.4186 | 4.9002 | 0.77109 | 0.1048
5.5833 | 39.4186 | 4.8375 | 0.74298 | 0.086316
5.5903 | 39.4186 | 4.7683 | 0.69562 | 0.081541
5.5972 | 39.4186 | 4.7258 | 0.65973 | 0.079647
5.6042 | 39.4186 | 4.7382 | 0.67637 | 0.080407
5.6111 | 39.4186 | 4.8401 | 0.76468 | 0.086344
5.6181 | 39.4186 | 5.5492 | 1.1538 | 0.14336
5.625 | 39.4186 | 6.0828 | 1.5051 | 0.17997
5.6319 | 39.4186 | 6.4773 | 1.8245 | 0.21687
5.6389 | 39.4186 | 6.7301 | 2.105 | 0.25404
5.6458 | 39.4186 | 6.2694 | 1.8186 | 0.22929
5.6528 | 39.4186 | 5.8379 | 1.536 | 0.14788
5.6597 | 39.4186 | 5.7145 | 1.6942 | 0.14922
5.6667 | 39.4186 | 6.2141 | 1.8767 | 0.16368
5.6736 | 39.4186 | 6.5806 | 1.8521 | 0.16677
5.6806 | 39.4186 | 6.8503 | 1.6342 | 0.15293
5.6875 | 39.4186 | 6.4255 | 1.4437 | 0.14042
5.6944 | 39.4186 | 5.9626 | 1.2945 | 0.12611
5.7014 | 39.4186 | 5.6206 | 1.5744 | 0.14094
5.7083 | 39.4186 | 5.5153 | 1.6999 | 0.15485
5.7153 | 39.4186 | 5.8114 | 1.8068 | 0.16173
5.7222 | 39.4186 | 6.2336 | 1.9612 | 0.1734
5.7292 | 39.4186 | 6.5962 | 1.784 | 0.16865
5.7361 | 39.4186 | 6.8633 | 1.5757 | 0.15572
5.7431 | 39.4186 | 7.0602 | 1.4883 | 0.15243
5.75 | 39.4186 | 7.2056 | 1.477 | 0.158
5.7569 | 39.4186 | 6.7854 | 1.5188 | 0.15771
5.7639 | 39.4186 | 6.2216 | 1.8768 | 0.17494
5.7708 | 39.4186 | 5.8048 | 1.9958 | 0.18388
5.7778 | 39.4186 | 5.832 | 1.8778 | 0.17747
5.7847 | 39.4186 | 6.304 | 1.5369 | 0.15214
5.7917 | 39.4186 | 6.6491 | 1.3646 | 0.13194
5.7986 | 39.4186 | 6.689 | 1.3176 | 0.12456
5.8056 | 39.4186 | 6.4004 | 1.3422 | 0.12594
5.8125 | 39.4186 | 6.1162 | 1.3235 | 0.12543
5.8194 | 39.4186 | 6.1072 | 1.2769 | 0.12276
5.8264 | 39.4186 | 6.5018 | 1.4479 | 0.13687
5.8333 | 39.4186 | 6.7918 | 1.8768 | 0.16565
5.8403 | 39.4186 | 7.0062 | 2.2126 | 0.19436
5.8472 | 39.4186 | 7.1665 | 2.4815 | 0.2198
5.8542 | 39.4186 | 6.8266 | 2.4252 | 0.22467
5.8611 | 39.4186 | 6.2658 | 2.1445 | 0.20393
5.8681 | 39.4186 | 5.8198 | 2.0349 | 0.19331
5.875 | 39.4186 | 5.5471 | 2.025 | 0.21184
5.8819 | 39.4186 | 5.733 | 2.0136 | 0.25705
5.8889 | 39.4186 | 6.2386 | 2.0911 | 0.26616
5.8958 | 39.4186 | 6.6101 | 2.2438 | 0.23748
5.9028 | 39.4186 | 6.2615 | 2.3389 | 0.22034
5.9097 | 39.4186 | 5.831 | 1.8014 | 0.19049
5.9167 | 39.4186 | 5.5484 | 1.3299 | 0.17037
5.9236 | 39.4186 | 5.5268 | 1.0539 | 0.15251
5.9306 | 39.4186 | 5.5919 | 0.98503 | 0.11944
5.9375 | 39.4186 | 5.3927 | 1.3248 | 0.13397
5.9444 | 39.4186 | 5.1757 | 1.4763 | 0.16688
5.9514 | 39.4186 | 5.0188 | 1.5259 | 0.16479
5.9583 | 39.4186 | 4.9049 | 1.4366 | 0.13743
5.9653 | 39.4186 | 4.9999 | 1.2388 | 0.1206
5.9722 | 39.4186 | 5.3097 | 1.231 | 0.12283
5.9792 | 39.4186 | 5.4971 | 1.3404 | 0.16906
5.9861 | 39.4186 | 5.4852 | 1.4406 | 0.18193
5.9931 | 39.4186 | 5.3723 | 1.251 | 0.17027
6 | 39.4186 | 5.2009 | 1.0074 | 0.10432
6.0069 | 39.4186 | 5.0324 | 0.84085 | 0.091017
6.0139 | 39.4186 | 4.9087 | 0.73953 | 0.084579
6.0208 | 39.4186 | 4.8182 | 0.7148 | 0.083948
6.0278 | 39.4186 | 4.7584 | 0.96483 | 0.097028
6.0347 | 39.4186 | 4.8354 | 1.1626 | 0.11167
6.0417 | 39.4186 | 5.2594 | 1.3341 | 0.12495
6.0486 | 39.4186 | 5.8706 | 1.5555 | 0.14237
6.0556 | 39.4186 | 6.3203 | 1.813 | 0.17178
6.0625 | 39.4186 | 6.6537 | 2.0698 | 0.22691
6.0694 | 39.4186 | 6.9037 | 2.309 | 0.28375
6.0764 | 39.4186 | 7.0932 | 2.5235 | 0.31982
6.0833 | 39.4186 | 7.2383 | 2.7111 | 0.35227
6.0903 | 39.4186 | 7.3503 | 2.8723 | 0.38258
6.0972 | 39.4186 | 7.4381 | 3.0094 | 0.4105
6.1042 | 39.4186 | 7.1378 | 2.7606 | 0.40109
6.1111 | 39.4186 | 6.7234 | 2.3996 | 0.2576
6.1181 | 39.4186 | 6.4503 | 2.2251 | 0.2077
6.125 | 39.4186 | 6.4445 | 2.3383 | 0.20935
6.1319 | 39.4186 | 6.3464 | 2.4003 | 0.22012
6.1389 | 39.4186 | 5.9885 | 2.3833 | 0.2416
6.1458 | 39.4186 | 5.6833 | 2.2927 | 0.24145
6.1528 | 39.4186 | 5.6215 | 2.1906 | 0.20562
6.1597 | 39.4186 | 5.8393 | 2.1439 | 0.19469
6.1667 | 39.4186 | 6.3162 | 2.198 | 0.19654
6.1736 | 39.4186 | 6.6649 | 2.3301 | 0.2074
6.1806 | 39.4186 | 6.921 | 2.4905 | 0.2228
6.1875 | 39.4186 | 7.1105 | 2.6532 | 0.2399
6.1944 | 39.4186 | 7.2525 | 2.8056 | 0.26672
6.2014 | 39.4186 | 6.9704 | 2.8896 | 0.27878
6.2083 | 39.4186 | 6.4475 | 2.8485 | 0.27409
6.2153 | 39.4186 | 5.9881 | 2.7029 | 0.25912
6.2222 | 39.4186 | 5.6259 | 2.5047 | 0.23872
6.2292 | 39.4186 | 5.3623 | 2.2948 | 0.21648
6.2361 | 39.4186 | 5.1776 | 1.848 | 0.17872
6.2431 | 39.4186 | 5.0951 | 1.3657 | 0.13653
6.25 | 39.4186 | 5.1162 | 1.0222 | 0.10717
6.2569 | 39.4186 | 5.3689 | 0.89964 | 0.095445
6.2639 | 39.4186 | 5.5035 | 0.89285 | 0.094658
6.2708 | 39.4186 | 5.416 | 0.86829 | 0.094516
6.2778 | 39.4186 | 5.2593 | 0.8255 | 0.090454
6.2847 | 39.4186 | 5.1042 | 0.79534 | 0.08848
6.2917 | 39.4186 | 4.9894 | 0.78432 | 0.08762
6.2986 | 39.4186 | 5.0534 | 0.81966 | 0.089232
6.3056 | 39.4186 | 5.5841 | 1.0316 | 0.10047
6.3125 | 39.4186 | 6.1088 | 1.3457 | 0.1298
6.3194 | 39.4186 | 6.4952 | 1.41 | 0.14495
6.3264 | 39.4186 | 6.7808 | 1.3906 | 0.13743
6.3333 | 39.4186 | 6.553 | 1.3146 | 0.12951
6.3403 | 39.4186 | 6.019 | 1.1905 | 0.12105
6.3472 | 39.4186 | 5.6261 | 1.0375 | 0.12252
6.3542 | 39.4186 | 5.3412 | 0.90343 | 0.13368
6.3611 | 39.4186 | 5.1347 | 0.83616 | 0.12535
6.3681 | 39.4186 | 4.9845 | 1.1482 | 0.14479
6.375 | 39.4186 | 4.8995 | 1.2958 | 0.16342
6.3819 | 39.4186 | 4.9188 | 1.375 | 0.14888
6.3889 | 39.4186 | 5.3838 | 1.175 | 0.12924
6.3958 | 39.4186 | 5.9621 | 1.0324 | 0.1132
6.4028 | 39.4186 | 6.3851 | 1.0501 | 0.10733
6.4097 | 39.4186 | 6.6955 | 1.2036 | 0.11366
6.4167 | 39.4186 | 6.5944 | 1.3807 | 0.12532
6.4236 | 39.4186 | 6.1535 | 1.5244 | 0.13774
6.4306 | 39.4186 | 5.7342 | 1.749 | 0.15454
6.4375 | 39.4186 | 5.4389 | 1.8109 | 0.16686
6.4444 | 39.4186 | 5.3299 | 1.6754 | 0.17081
6.4514 | 39.4186 | 5.6666 | 1.5434 | 0.20112
6.4583 | 39.4186 | 6.1786 | 1.4001 | 0.18231
6.4653 | 39.4186 | 6.5537 | 1.3223 | 0.1367
6.4722 | 39.4186 | 6.8277 | 1.3707 | 0.13412
6.4792 | 39.4186 | 7.0288 | 1.5355 | 0.14611
6.4861 | 39.4186 | 7.1776 | 2.0251 | 0.19306
6.4931 | 39.4186 | 6.817 | 2.3251 | 0.28216
6.5 | 39.4186 | 6.3706 | 2.4305 | 0.31495
6.5069 | 39.4186 | 5.9826 | 2.0817 | 0.29189
6.5139 | 39.4186 | 5.7063 | 1.5526 | 0.17183
6.5208 | 39.4186 | 5.5897 | 1.1879 | 0.12358
6.5278 | 39.4186 | 5.8045 | 1.0359 | 0.10619
6.5347 | 39.4186 | 6.2793 | 1.0827 | 0.1073
6.5417 | 39.4186 | 6.6253 | 1.197 | 0.11602
6.5486 | 39.4186 | 6.8789 | 1.3195 | 0.12796
6.5556 | 39.4186 | 6.583 | 1.4381 | 0.16316
6.5625 | 39.4186 | 6.1545 | 1.7934 | 0.21474
6.5694 | 39.4186 | 6.0514 | 1.9642 | 0.19364
6.5764 | 39.4186 | 6.4633 | 1.9104 | 0.17207
6.5833 | 39.4186 | 6.7652 | 1.666 | 0.15508
6.5903 | 39.4186 | 6.9863 | 1.5187 | 0.14141
6.5972 | 39.4186 | 7.1487 | 1.4775 | 0.14633
6.6042 | 39.4186 | 7.2691 | 1.5366 | 0.19374
6.6111 | 39.4186 | 7.3598 | 1.5686 | 0.20069
6.6181 | 39.4186 | 7.4278 | 1.5766 | 0.17475
6.625 | 39.4186 | 7.4775 | 1.5941 | 0.14868
6.6319 | 39.4186 | 7.5131 | 1.6147 | 0.14642
6.6389 | 39.4186 | 7.5389 | 1.649 | 0.15159
6.6458 | 39.4186 | 7.5583 | 1.7116 | 0.16792
6.6528 | 39.4186 | 7.3924 | 1.8059 | 0.22557
6.6597 | 39.4186 | 6.8206 | 1.8626 | 0.23897
6.6667 | 39.4186 | 6.2472 | 2.1074 | 0.24722
6.6736 | 39.4186 | 5.8045 | 2.1507 | 0.21397
6.6806 | 39.4186 | 5.4819 | 2.0894 | 0.19626
6.6875 | 39.4186 | 5.2467 | 1.9828 | 0.18302
6.6944 | 39.4186 | 5.2202 | 1.8835 | 0.17186
6.7014 | 39.4186 | 5.8539 | 1.5021 | 0.1439
6.7083 | 39.4186 | 6.3163 | 1.2599 | 0.12225
6.7153 | 39.4186 | 6.6537 | 1.2166 | 0.11616
6.7222 | 39.4186 | 6.3876 | 1.193 | 0.11823
6.7292 | 39.4186 | 5.9298 | 1.1333 | 0.12209
6.7361 | 39.4186 | 5.5617 | 1.131 | 0.14275
6.7431 | 39.4186 | 5.2949 | 1.1444 | 0.12941
6.75 | 39.4186 | 5.101 | 0.93536 | 0.11886
6.7569 | 39.4186 | 4.9597 | 0.77667 | 0.1209
6.7639 | 39.4186 | 4.9684 | 0.70957 | 0.10353
6.7708 | 39.4186 | 5.3852 | 0.75277 | 0.086495
6.7778 | 39.4186 | 5.9602 | 0.96655 | 0.095077
6.7847 | 39.4186 | 6.3814 | 1.4736 | 0.12639
6.7917 | 39.4186 | 6.6925 | 1.8628 | 0.16175
6.7986 | 39.4186 | 6.8194 | 2.1635 | 0.20507
6.8056 | 39.4186 | 7.0235 | 2.4056 | 0.2624
6.8125 | 39.4186 | 7.1791 | 2.6137 | 0.26705
6.8194 | 39.4186 | 7.2976 | 2.7904 | 0.25946
6.8264 | 39.4186 | 7.3877 | 2.9389 | 0.27159
6.8333 | 39.4186 | 7.0421 | 3.0066 | 0.28968
6.8403 | 39.4186 | 6.7101 | 2.9731 | 0.33629
6.8472 | 39.4186 | 6.9667 | 2.9491 | 0.40371
6.8542 | 39.4186 | 7.002 | 2.9647 | 0.38314
6.8611 | 39.4186 | 6.4989 | 2.9115 | 0.29371
6.8681 | 39.4186 | 6.0032 | 2.4113 | 0.2387
6.875 | 39.4186 | 5.6391 | 1.7938 | 0.17822
6.8819 | 39.4186 | 5.3698 | 1.3124 | 0.13226
6.8889 | 39.4186 | 5.3023 | 1.0029 | 0.1054
6.8958 | 39.4186 | 5.6778 | 0.901 | 0.095606
6.9028 | 39.4186 | 5.7 | 0.91101 | 0.11554
6.9097 | 39.4186 | 5.4848 | 0.95503 | 0.13428
6.9167 | 39.4186 | 5.2757 | 0.95293 | 0.13473
6.9236 | 39.4186 | 5.1405 | 0.87822 | 0.12839
6.9306 | 39.4186 | 5.1288 | 0.77801 | 0.11881
6.9375 | 39.4186 | 5.2594 | 0.75303 | 0.1144
6.9444 | 39.4186 | 5.231 | 0.75027 | 0.11383
6.9514 | 39.4186 | 5.0643 | 0.74362 | 0.11353
6.9583 | 39.4186 | 4.9268 | 0.78686 | 0.11633
6.9653 | 39.4186 | 4.8269 | 0.74843 | 0.10038
6.9722 | 39.4186 | 4.7536 | 0.66718 | 0.082141
6.9792 | 39.4186 | 4.9547 | 0.65795 | 0.078653
6.9861 | 39.4186 | 5.6402 | 0.7427 | 0.082544
6.9931 | 39.4186 | 6.1422 | 0.93264 | 0.093891
7 | 39.4186 | 6.5121 | 1.4879 | 0.12854

## PE
PE
Time | Total ammonia (NHx) (Pipe2) | Total suspended solids (TSS) (Pipe2) | Total chemical oxygen demand (Pipe2) | Flow rate (Pipe2)
d | g N/m3 | g TSS/m3 | g COD/m3 | m3/d
0 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.0069444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.013889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.020833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.027778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.034722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.041667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.048611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.055556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.069444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.076389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.083333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.090278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.097222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.10417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.11111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.11806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.13194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.13889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.14583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.15278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.15972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.16667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.17361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.18056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.19444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.20139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.20833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.21528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.22222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.22917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.23611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.24306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.25694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.26389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.27083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.27778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.28472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.29167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.29861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.30556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.31944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.32639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.33333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.34028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.34722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.35417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.36111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.36806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.38194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.38889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.39583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.40278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.40972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.41667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.42361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.43056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.44444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.45139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.45833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.46528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.47222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.47917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.48611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.49306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.50694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.51389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.52083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.52778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.53472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.54167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.54861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.55556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.56944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.57639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.58333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.59028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.59722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.60417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.61111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.61806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.63194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.63889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.64583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.65278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.65972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.66667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.67361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.68056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.69444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.70139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.70833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.71528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.72222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.72917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.73611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.74306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.75694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.76389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.77083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.77778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.78472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.79167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.79861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.80556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.81944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.82639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.83333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.84028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.84722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.85417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.86111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.86806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.88194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.88889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.89583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.90278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.90972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.91667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.92361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.93056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.94444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.95139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.95833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.96528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.97222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.97917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.98611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
0.99306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.0972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.1944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.2986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.3958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.4931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.5972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.6944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.7986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.8958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
1.9931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.0972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.1944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.2986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.3958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.4931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.5972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.6944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.7986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.8958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
2.9931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.0972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.1944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.2986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.3958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.4931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.5972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.6944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.7986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.8958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
3.9931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.0972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.1944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.2986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.3958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.4931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.5972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.6944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.7986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.8958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
4.9931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.0972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.1944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.2986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.3958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.4931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.5972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.6944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.7986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.8958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
5.9931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.0972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.1944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.25 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.2986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.3958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.4931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5069 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5139 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5208 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5278 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5347 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5417 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5486 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5556 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5694 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5764 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5833 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5903 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.5972 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6042 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6111 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6181 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.625 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6319 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6389 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6458 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6528 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6597 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6667 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6736 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6806 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.6944 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7014 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7083 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7153 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7222 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7292 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7361 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7431 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.75 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7569 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7639 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7708 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7778 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7847 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7917 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.7986 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8056 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8125 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8194 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8264 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8333 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8403 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8472 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8542 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8611 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8681 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.875 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8819 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8889 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.8958 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9028 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9097 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9167 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9236 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9306 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9375 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9444 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9514 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9583 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9653 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9722 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9792 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9861 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
6.9931 | 39.4186 | 74.8293 | 272.2449 | 23473.0581
7 | 39.4186 | 74.8293 | 272.2449 | 23473.0581

## Biomass
Biomass
Time | Ordinary heterotrophic organisms (OHO) (CSTR4) | Aerobic nitrifying organisms (NITO) (CSTR4) | Ordinary heterotrophic organisms (OHO) (CSTR3) | Aerobic nitrifying organisms (NITO) (CSTR3) | Ordinary heterotrophic organisms (OHO) (CSTR2) | Aerobic nitrifying organisms (NITO) (CSTR2)
d | g COD/m3 | g COD/m3 | g COD/m3 | g COD/m3 | g COD/m3 | g COD/m3
0 | 995.3789 | 96.3507 | 996.268 | 96.5284 | 994.9943 | 95.8728
0.0069444 | 995.3847 | 96.3516 | 996.1793 | 96.4642 | 994.9774 | 95.8459
0.013889 | 995.3896 | 96.3553 | 996.0731 | 96.4131 | 994.8394 | 95.6951
0.020833 | 995.3968 | 96.3592 | 995.9661 | 96.3566 | 994.7172 | 95.5841
0.027778 | 995.4001 | 96.364 | 995.8695 | 96.3007 | 994.6321 | 95.5024
0.034722 | 995.3979 | 96.3698 | 995.7871 | 96.2487 | 994.5735 | 95.4425
0.041667 | 995.3913 | 96.3761 | 995.7199 | 96.2022 | 994.5337 | 95.3989
0.048611 | 995.3604 | 96.3804 | 995.6669 | 96.1619 | 994.5068 | 95.3674
0.055556 | 995.3113 | 96.3863 | 995.6262 | 96.128 | 994.4871 | 95.345
0.0625 | 995.2719 | 96.3978 | 995.6053 | 96.1087 | 994.5016 | 95.3563
0.069444 | 995.2564 | 96.4147 | 995.653 | 96.1577 | 994.5833 | 95.4389
0.076389 | 995.263 | 96.4332 | 995.7129 | 96.1993 | 994.6668 | 95.5198
0.083333 | 995.279 | 96.4479 | 995.7505 | 96.2213 | 994.7339 | 95.5892
0.090278 | 995.3259 | 96.4657 | 995.7694 | 96.2324 | 994.7718 | 95.6259
0.097222 | 995.3837 | 96.4703 | 995.7854 | 96.2453 | 994.7823 | 95.6317
0.10417 | 995.4343 | 96.476 | 995.8609 | 96.322 | 994.7976 | 95.6421
0.11111 | 995.4705 | 96.486 | 995.9738 | 96.421 | 994.8304 | 95.6656
0.11806 | 995.4886 | 96.4971 | 996.0666 | 96.4816 | 994.8194 | 95.6344
0.125 | 995.5039 | 96.5076 | 996.1208 | 96.5043 | 994.7593 | 95.5683
0.13194 | 995.5222 | 96.5131 | 996.1357 | 96.4939 | 994.7139 | 95.5219
0.13889 | 995.538 | 96.5126 | 996.0708 | 96.4084 | 994.7659 | 95.5613
0.14583 | 995.5674 | 96.5158 | 996.0275 | 96.3654 | 994.8778 | 95.6573
0.15278 | 995.5939 | 96.5191 | 996.0287 | 96.3607 | 994.9921 | 95.7549
0.15972 | 995.6213 | 96.5294 | 996.0578 | 96.3784 | 995.0841 | 95.8281
0.16667 | 995.6631 | 96.541 | 996.1004 | 96.4061 | 995.1575 | 95.8833
0.17361 | 995.7085 | 96.549 | 996.1488 | 96.4367 | 995.2189 | 95.9254
0.18056 | 995.7448 | 96.5563 | 996.1961 | 96.4634 | 995.257 | 95.9346
0.1875 | 995.7638 | 96.5635 | 996.2192 | 96.4659 | 995.1622 | 95.8075
0.19444 | 995.7795 | 96.5718 | 996.2114 | 96.4432 | 995.0782 | 95.7156
0.20139 | 995.8194 | 96.5788 | 996.1931 | 96.4105 | 995.0275 | 95.6496
0.20833 | 995.87 | 96.5794 | 996.1744 | 96.3759 | 995.0018 | 95.6025
0.21528 | 995.9142 | 96.5806 | 996.1771 | 96.3572 | 995.0991 | 95.673
0.22222 | 995.9602 | 96.5889 | 996.2601 | 96.4131 | 995.2295 | 95.7649
0.22917 | 996.0137 | 96.5996 | 996.3773 | 96.4875 | 995.3459 | 95.8443
0.23611 | 996.068 | 96.6087 | 996.4978 | 96.561 | 995.4454 | 95.9096
0.24306 | 996.1119 | 96.617 | 996.6238 | 96.6374 | 995.5292 | 95.9593
0.25 | 996.1392 | 96.6257 | 996.7362 | 96.6894 | 995.593 | 95.9861
0.25694 | 996.1565 | 96.6339 | 996.8169 | 96.7076 | 995.6304 | 95.984
0.26389 | 996.1822 | 96.6394 | 996.8792 | 96.7161 | 995.6588 | 95.9791
0.27083 | 996.2167 | 96.6421 | 996.9418 | 96.7308 | 995.7095 | 96.0086
0.27778 | 996.2445 | 96.6473 | 997.0091 | 96.7499 | 995.7674 | 96.045
0.28472 | 996.268 | 96.6537 | 997.0752 | 96.7667 | 995.8181 | 96.0729
0.29167 | 996.2946 | 96.658 | 997.1336 | 96.7771 | 995.8617 | 96.0948
0.29861 | 996.3233 | 96.6608 | 997.1831 | 96.7827 | 995.8905 | 96.0972
0.30556 | 996.3587 | 96.6597 | 997.1996 | 96.766 | 995.8387 | 96.0059
0.3125 | 996.4109 | 96.6532 | 997.1839 | 96.7375 | 995.8182 | 95.9638
0.31944 | 996.4704 | 96.6482 | 997.1727 | 96.7224 | 995.8535 | 95.9755
0.32639 | 996.519 | 96.6487 | 997.1954 | 96.7366 | 995.8958 | 95.9831
0.33333 | 996.551 | 96.6537 | 997.2352 | 96.7545 | 995.884 | 95.9279
0.34028 | 996.5629 | 96.6625 | 997.254 | 96.748 | 995.8139 | 95.8329
0.34722 | 996.569 | 96.6725 | 997.2511 | 96.73 | 995.7589 | 95.7634
0.35417 | 996.5806 | 96.6792 | 997.2197 | 96.6888 | 995.7262 | 95.713
0.36111 | 996.5929 | 96.6842 | 997.1703 | 96.6388 | 995.709 | 95.6769
0.36806 | 996.6033 | 96.6895 | 997.1224 | 96.5944 | 995.7024 | 95.6514
0.375 | 996.6119 | 96.6957 | 997.0866 | 96.5602 | 995.7033 | 95.6337
0.38194 | 996.6148 | 96.699 | 997.0194 | 96.4882 | 995.7092 | 95.622
0.38889 | 996.6443 | 96.709 | 996.9652 | 96.4373 | 995.7187 | 95.6147
0.39583 | 996.6901 | 96.7118 | 996.933 | 96.4011 | 995.7328 | 95.6108
0.40278 | 996.7309 | 96.7143 | 996.9351 | 96.392 | 995.7951 | 95.6469
0.40972 | 996.7787 | 96.7276 | 997.0549 | 96.5112 | 995.8928 | 95.7103
0.41667 | 996.8353 | 96.7406 | 997.1841 | 96.601 | 995.9681 | 95.7465
0.42361 | 996.8863 | 96.7488 | 997.2945 | 96.6685 | 996.0549 | 95.8021
0.43056 | 996.9293 | 96.7553 | 997.3912 | 96.7187 | 996.1233 | 95.8338
0.4375 | 996.9659 | 96.759 | 997.4403 | 96.72 | 996.1014 | 95.784
0.44444 | 996.9937 | 96.7598 | 997.4174 | 96.6631 | 996.0807 | 95.7487
0.45139 | 996.9879 | 96.7586 | 997.3584 | 96.5892 | 996.0758 | 95.7237
0.45833 | 996.9713 | 96.7648 | 997.316 | 96.5379 | 996.106 | 95.7287
0.46528 | 996.9646 | 96.7736 | 997.3137 | 96.5191 | 996.2369 | 95.8443
0.47222 | 996.9804 | 96.7923 | 997.4146 | 96.6051 | 996.3738 | 95.9614
0.47917 | 997.0491 | 96.8205 | 997.5499 | 96.7071 | 996.4797 | 96.0497
0.48611 | 997.1339 | 96.8281 | 997.6771 | 96.7947 | 996.5641 | 96.1177
0.49306 | 997.2054 | 96.8257 | 997.7632 | 96.8333 | 996.6199 | 96.1451
0.5 | 997.2614 | 96.8202 | 997.7598 | 96.7947 | 996.6222 | 96.1066
0.50694 | 997.306 | 96.818 | 997.7303 | 96.7553 | 996.5482 | 96.0049
0.51389 | 997.3428 | 96.8232 | 997.7739 | 96.7945 | 996.4922 | 95.9305
0.52083 | 997.3486 | 96.8322 | 997.8436 | 96.8293 | 996.5468 | 95.9544
0.52778 | 997.3517 | 96.8476 | 997.9156 | 96.8542 | 996.6428 | 96.0121
0.53472 | 997.3678 | 96.8585 | 997.9694 | 96.8592 | 996.7245 | 96.0575
0.54167 | 997.3881 | 96.864 | 997.9672 | 96.8206 | 996.8124 | 96.1258
0.54861 | 997.4085 | 96.8699 | 997.9622 | 96.8021 | 996.8931 | 96.1893
0.55556 | 997.4303 | 96.8783 | 997.9759 | 96.8046 | 996.9584 | 96.2374
0.5625 | 997.456 | 96.889 | 998.0196 | 96.8332 | 997.0116 | 96.2744
0.56944 | 997.4835 | 96.8984 | 998.0504 | 96.8431 | 997.0567 | 96.3035
0.57639 | 997.5401 | 96.9057 | 998.0839 | 96.8597 | 997.0843 | 96.3078
0.58333 | 997.6084 | 96.9044 | 998.1549 | 96.9066 | 997.0864 | 96.2779
0.59028 | 997.6667 | 96.9018 | 998.2106 | 96.9224 | 997.0913 | 96.2521
0.59722 | 997.7156 | 96.9009 | 998.2624 | 96.938 | 997.1364 | 96.2734
0.60417 | 997.7558 | 96.9033 | 998.3459 | 96.9822 | 997.2008 | 96.3108
0.61111 | 997.7894 | 96.9045 | 998.4367 | 97.0186 | 997.2607 | 96.3386
0.61806 | 997.8207 | 96.9029 | 998.5057 | 97.0298 | 997.3132 | 96.3583
0.625 | 997.8558 | 96.8997 | 998.4862 | 96.9784 | 997.3498 | 96.3574
0.63194 | 997.891 | 96.9006 | 998.462 | 96.9505 | 997.3734 | 96.3436
0.63889 | 997.9233 | 96.9043 | 998.4529 | 96.933 | 997.3966 | 96.3335
0.64583 | 997.9543 | 96.9103 | 998.482 | 96.9464 | 997.4229 | 96.3288
0.65278 | 997.9848 | 96.9169 | 998.552 | 96.9864 | 997.4349 | 96.3056
0.65972 | 998.0133 | 96.9206 | 998.6206 | 97.0104 | 997.4422 | 96.2812
0.66667 | 998.0415 | 96.9217 | 998.6665 | 97.0122 | 997.464 | 96.2768
0.67361 | 998.0709 | 96.9221 | 998.6922 | 97.0027 | 997.487 | 96.2715
0.68056 | 998.0947 | 96.9261 | 998.7395 | 97.0218 | 997.4986 | 96.2532
0.6875 | 998.0986 | 96.9353 | 998.7799 | 97.0269 | 997.4492 | 96.1741
0.69444 | 998.0963 | 96.9452 | 998.7865 | 97.0077 | 997.369 | 96.0849
0.70139 | 998.1034 | 96.9525 | 998.7857 | 96.9934 | 997.3767 | 96.0837
0.70833 | 998.1386 | 96.9544 | 998.8101 | 97.0038 | 997.4604 | 96.1589
0.71528 | 998.1855 | 96.9498 | 998.8547 | 97.0266 | 997.5544 | 96.2398
0.72222 | 998.2209 | 96.9468 | 998.9065 | 97.0504 | 997.6315 | 96.2995
0.72917 | 998.247 | 96.9445 | 998.9573 | 97.0685 | 997.6869 | 96.3324
0.73611 | 998.2663 | 96.9443 | 998.9979 | 97.0749 | 997.7133 | 96.3297
0.74306 | 998.2792 | 96.9473 | 999.0286 | 97.0756 | 997.7456 | 96.3435
0.75 | 998.2937 | 96.9486 | 999.0537 | 97.0763 | 997.7902 | 96.3758
0.75694 | 998.3165 | 96.9468 | 999.0754 | 97.0783 | 997.8295 | 96.3994
0.76389 | 998.3397 | 96.9453 | 999.0989 | 97.084 | 997.858 | 96.4099
0.77083 | 998.3597 | 96.9447 | 999.1117 | 97.0795 | 997.8643 | 96.3913
0.77778 | 998.3643 | 96.9534 | 999.1185 | 97.0737 | 997.8485 | 96.3498
0.78472 | 998.3559 | 96.9658 | 999.1327 | 97.0759 | 997.8228 | 96.3045
0.79167 | 998.3565 | 96.9749 | 999.1528 | 97.0805 | 997.8316 | 96.3075
0.79861 | 998.3625 | 96.9814 | 999.1757 | 97.086 | 997.8622 | 96.3352
0.80556 | 998.381 | 96.9802 | 999.1979 | 97.0919 | 997.8983 | 96.3699
0.8125 | 998.4109 | 96.9739 | 999.2157 | 97.0956 | 997.9329 | 96.401
0.81944 | 998.4287 | 96.9751 | 999.2166 | 97.0882 | 997.9628 | 96.424
0.82639 | 998.4296 | 96.9819 | 999.2068 | 97.0794 | 997.9785 | 96.427
0.83333 | 998.4299 | 96.9899 | 999.2028 | 97.0802 | 997.8572 | 96.2848
0.84028 | 998.4335 | 96.9955 | 999.1841 | 97.0668 | 997.7469 | 96.181
0.84722 | 998.4555 | 96.9944 | 999.1379 | 97.0292 | 997.6718 | 96.1053
0.85417 | 998.4894 | 96.9872 | 999.0207 | 96.9313 | 997.6232 | 96.05
0.86111 | 998.5103 | 96.985 | 998.9146 | 96.8597 | 997.5943 | 96.0091
0.86806 | 998.5228 | 96.9881 | 998.8576 | 96.8219 | 997.7022 | 96.1096
0.875 | 998.5371 | 96.9954 | 998.8542 | 96.8218 | 997.8307 | 96.2165
0.88194 | 998.5544 | 97.0045 | 998.8812 | 96.8437 | 997.9295 | 96.2938
0.88889 | 998.5564 | 97.013 | 998.9152 | 96.8667 | 997.9602 | 96.2898
0.89583 | 998.5371 | 97.0218 | 998.9306 | 96.8705 | 997.8912 | 96.2003
0.90278 | 998.5206 | 97.0348 | 998.9363 | 96.8662 | 997.907 | 96.2166
0.90972 | 998.5174 | 97.0469 | 998.9561 | 96.8728 | 997.9679 | 96.2717
0.91667 | 998.5625 | 97.0636 | 998.9883 | 96.8916 | 998.0316 | 96.3321
0.92361 | 998.6214 | 97.065 | 999.0265 | 96.9167 | 998.0816 | 96.3737
0.93056 | 998.6664 | 97.0659 | 999.0604 | 96.9362 | 998.0885 | 96.3574
0.9375 | 998.6945 | 97.073 | 999.1441 | 97.0099 | 998.034 | 96.2821
0.94444 | 998.7257 | 97.0827 | 999.2469 | 97.0837 | 998.0484 | 96.2875
0.95139 | 998.7605 | 97.0854 | 999.3401 | 97.1307 | 998.1216 | 96.3495
0.95833 | 998.7929 | 97.0843 | 999.4217 | 97.1627 | 998.2018 | 96.4132
0.96528 | 998.8223 | 97.082 | 999.4659 | 97.1608 | 998.2695 | 96.4607
0.97222 | 998.8441 | 97.0817 | 999.4432 | 97.1177 | 998.3254 | 96.496
0.97917 | 998.8565 | 97.0867 | 999.4196 | 97.0943 | 998.3329 | 96.4675
0.98611 | 998.8763 | 97.0944 | 999.4345 | 97.105 | 998.2312 | 96.3421
0.99306 | 998.905 | 97.0993 | 999.4613 | 97.1188 | 998.1439 | 96.2504
1 | 998.9366 | 97.1014 | 999.4848 | 97.1243 | 998.0888 | 96.1836
1.0069 | 998.9697 | 97.1019 | 999.5043 | 97.1258 | 998.0573 | 96.135
1.0139 | 999.0024 | 97.1012 | 999.5112 | 97.113 | 998.0427 | 96.0996
1.0208 | 999.0325 | 97.1007 | 999.4981 | 97.0817 | 998.0403 | 96.0738
1.0278 | 999.0563 | 97.1009 | 999.4585 | 97.0258 | 998.0719 | 96.0766
1.0347 | 999.0439 | 97.1013 | 999.386 | 96.9442 | 998.0807 | 96.0573
1.0417 | 999.0085 | 97.1067 | 999.3265 | 96.8857 | 998.0852 | 96.0432
1.0486 | 998.9793 | 97.1154 | 999.288 | 96.8429 | 998.0895 | 96.0333
1.0556 | 998.9734 | 97.1287 | 999.2743 | 96.8194 | 998.1573 | 96.0863
1.0625 | 999.0069 | 97.1457 | 999.2919 | 96.8211 | 998.2636 | 96.1779
1.0694 | 999.06 | 97.1547 | 999.3297 | 96.8406 | 998.3435 | 96.2373
1.0764 | 999.11 | 97.1593 | 999.3587 | 96.854 | 998.3059 | 96.1846
1.0833 | 999.1501 | 97.1628 | 999.3678 | 96.8532 | 998.2679 | 96.1475
1.0903 | 999.1834 | 97.1673 | 999.3891 | 96.8625 | 998.3711 | 96.2481
1.0972 | 999.204 | 97.173 | 999.4406 | 96.8956 | 998.5037 | 96.3614
1.1042 | 999.2012 | 97.1827 | 999.5655 | 97.0062 | 998.6102 | 96.4458
1.1111 | 999.2386 | 97.2133 | 999.723 | 97.1358 | 998.6916 | 96.5096
1.1181 | 999.3043 | 97.2229 | 999.8583 | 97.2262 | 998.7504 | 96.5484
1.125 | 999.3599 | 97.2185 | 999.9548 | 97.2705 | 998.793 | 96.567
1.1319 | 999.4028 | 97.2132 | 1000.0269 | 97.2933 | 998.8306 | 96.5787
1.1389 | 999.4376 | 97.2095 | 1000.0904 | 97.3099 | 998.8425 | 96.555
1.1458 | 999.4683 | 97.2065 | 1000.1297 | 97.3075 | 998.7551 | 96.4385
1.1528 | 999.4993 | 97.2043 | 1000.1368 | 97.2878 | 998.6819 | 96.3528
1.1597 | 999.5279 | 97.2044 | 1000.1201 | 97.2554 | 998.6383 | 96.2893
1.1667 | 999.5506 | 97.2053 | 1000.0555 | 97.1831 | 998.6149 | 96.2423
1.1736 | 999.5673 | 97.2078 | 999.9771 | 97.1089 | 998.7047 | 96.3068
1.1806 | 999.5885 | 97.2166 | 999.9892 | 97.1251 | 998.8319 | 96.4056
1.1875 | 999.6192 | 97.2265 | 1000.0448 | 97.1623 | 998.9417 | 96.4891
1.1944 | 999.6461 | 97.2321 | 1000.0601 | 97.1541 | 999.0233 | 96.5454
1.2014 | 999.6427 | 97.2387 | 1000.0759 | 97.1602 | 999.0836 | 96.583
1.2083 | 999.6294 | 97.2519 | 1000.1009 | 97.1726 | 999.1315 | 96.6138
1.2153 | 999.6289 | 97.2676 | 1000.1576 | 97.2143 | 999.1691 | 96.6385
1.2222 | 999.6666 | 97.283 | 1000.2785 | 97.3138 | 999.1967 | 96.655
1.2292 | 999.7091 | 97.2805 | 1000.3831 | 97.3641 | 999.1992 | 96.6374
1.2361 | 999.7441 | 97.2725 | 1000.4381 | 97.3684 | 999.0935 | 96.5137
1.2431 | 999.7797 | 97.2642 | 1000.4507 | 97.3508 | 999.0044 | 96.4233
1.25 | 999.8159 | 97.2584 | 1000.4406 | 97.325 | 998.9495 | 96.3566
1.2569 | 999.8487 | 97.2561 | 1000.4289 | 97.3042 | 998.9615 | 96.3443
1.2639 | 999.8784 | 97.2568 | 1000.4369 | 97.3006 | 999.0219 | 96.3716
1.2708 | 999.9055 | 97.2589 | 1000.4498 | 97.2986 | 999.0005 | 96.3175
1.2778 | 999.93 | 97.2612 | 1000.4542 | 97.2918 | 998.9761 | 96.2774
1.2847 | 999.9526 | 97.2637 | 1000.4549 | 97.2819 | 998.9654 | 96.2478
1.2917 | 999.9693 | 97.2676 | 1000.4552 | 97.2722 | 998.9644 | 96.2264
1.2986 | 999.9576 | 97.2748 | 1000.4595 | 97.2598 | 999.0761 | 96.3205
1.3056 | 999.9357 | 97.2841 | 1000.412 | 97.1909 | 999.2107 | 96.4348
1.3125 | 999.9211 | 97.2938 | 1000.3882 | 97.1694 | 999.3107 | 96.5169
1.3194 | 999.9164 | 97.3051 | 1000.3902 | 97.169 | 999.3625 | 96.5513
1.3264 | 999.9442 | 97.3188 | 1000.3955 | 97.1692 | 999.3516 | 96.5234
1.3333 | 999.9909 | 97.3252 | 1000.4499 | 97.2229 | 999.3113 | 96.4768
1.3403 | 1000.0384 | 97.3256 | 1000.4758 | 97.226 | 999.3674 | 96.5425
1.3472 | 1000.0779 | 97.3247 | 1000.4819 | 97.2201 | 999.4497 | 96.6186
1.3542 | 1000.1047 | 97.327 | 1000.5 | 97.2323 | 999.5199 | 96.6753
1.3611 | 1000.1004 | 97.3369 | 1000.5938 | 97.3182 | 999.5713 | 96.7086
1.3681 | 1000.098 | 97.3559 | 1000.7016 | 97.3928 | 999.5113 | 96.6151
1.375 | 1000.1096 | 97.3642 | 1000.7608 | 97.4107 | 999.4156 | 96.5159
1.3819 | 1000.1329 | 97.3639 | 1000.8017 | 97.4179 | 999.4689 | 96.5766
1.3889 | 1000.1507 | 97.3657 | 1000.8538 | 97.4352 | 999.5584 | 96.6536
1.3958 | 1000.1632 | 97.3704 | 1000.9013 | 97.4475 | 999.6303 | 96.711
1.4028 | 1000.1766 | 97.3708 | 1000.8622 | 97.3926 | 999.6855 | 96.7542
1.4097 | 1000.1887 | 97.3742 | 1000.8271 | 97.3719 | 999.7287 | 96.7865
1.4167 | 1000.2003 | 97.3806 | 1000.8133 | 97.3662 | 999.7565 | 96.8005
1.4236 | 1000.2121 | 97.3881 | 1000.8089 | 97.3639 | 999.7625 | 96.7881
1.4306 | 1000.2303 | 97.4004 | 1000.8881 | 97.4381 | 999.748 | 96.7545
1.4375 | 1000.267 | 97.4045 | 1000.9784 | 97.486 | 999.7672 | 96.7691
1.4444 | 1000.3085 | 97.3964 | 1001.052 | 97.5094 | 999.8093 | 96.8046
1.4514 | 1000.3444 | 97.3882 | 1001.1125 | 97.5222 | 999.8504 | 96.831
1.4583 | 1000.3722 | 97.3839 | 1001.1633 | 97.5293 | 999.8874 | 96.8502
1.4653 | 1000.3864 | 97.3878 | 1001.2068 | 97.5336 | 999.9204 | 96.8639
1.4722 | 1000.3911 | 97.3938 | 1001.2395 | 97.532 | 999.9254 | 96.8402
1.4792 | 1000.4023 | 97.3948 | 1001.1638 | 97.4563 | 999.8073 | 96.6974
1.4861 | 1000.4122 | 97.3966 | 1001.0526 | 97.3852 | 999.7025 | 96.5924
1.4931 | 1000.4182 | 97.4031 | 1000.9943 | 97.3617 | 999.6315 | 96.5152
1.5 | 1000.4272 | 97.414 | 1000.9994 | 97.3861 | 999.5846 | 96.4587
1.5069 | 1000.4399 | 97.4246 | 1001.0325 | 97.4139 | 999.6684 | 96.5353
1.5139 | 1000.4563 | 97.4341 | 1001.0882 | 97.4495 | 999.7747 | 96.6207
1.5208 | 1000.4747 | 97.4413 | 1001.1476 | 97.4797 | 999.8435 | 96.6645
1.5278 | 1000.4934 | 97.4453 | 1001.1803 | 97.4841 | 999.7762 | 96.5756
1.5347 | 1000.5119 | 97.4472 | 1001.1867 | 97.476 | 999.71 | 96.5114
1.5417 | 1000.5347 | 97.4483 | 1001.1816 | 97.4627 | 999.6687 | 96.4651
1.5486 | 1000.5793 | 97.444 | 1001.1628 | 97.4382 | 999.6459 | 96.4319
1.5556 | 1000.6308 | 97.436 | 1001.1224 | 97.39 | 999.7487 | 96.5209
1.5625 | 1000.6691 | 97.4326 | 1001.0746 | 97.3397 | 999.8831 | 96.629
1.5694 | 1000.6919 | 97.4358 | 1001.0624 | 97.3306 | 999.9977 | 96.7166
1.5764 | 1000.6768 | 97.4424 | 1001.0802 | 97.3429 | 1000.0865 | 96.7805
1.5833 | 1000.6662 | 97.4642 | 1001.1698 | 97.4234 | 1000.1531 | 96.8276
1.5903 | 1000.6782 | 97.4857 | 1001.3014 | 97.5248 | 1000.2032 | 96.8635
1.5972 | 1000.6945 | 97.4971 | 1001.4102 | 97.5781 | 1000.2424 | 96.8921
1.6042 | 1000.71 | 97.5003 | 1001.4917 | 97.602 | 1000.2748 | 96.9155
1.6111 | 1000.7275 | 97.4996 | 1001.5474 | 97.6065 | 1000.2923 | 96.9192
1.6181 | 1000.7489 | 97.4971 | 1001.5536 | 97.582 | 1000.2965 | 96.9074
1.625 | 1000.773 | 97.4945 | 1001.4983 | 97.5301 | 1000.2971 | 96.8927
1.6319 | 1000.8141 | 97.4929 | 1001.501 | 97.5458 | 1000.2555 | 96.8266
1.6389 | 1000.8601 | 97.4886 | 1001.5288 | 97.5644 | 1000.1533 | 96.7131
1.6458 | 1000.8919 | 97.4868 | 1001.5387 | 97.5605 | 1000.0744 | 96.6292
1.6528 | 1000.9132 | 97.4881 | 1001.543 | 97.5517 | 1000.083 | 96.6181
1.6597 | 1000.9349 | 97.4903 | 1001.56 | 97.5515 | 1000.1555 | 96.664
1.6667 | 1000.9592 | 97.4921 | 1001.5784 | 97.548 | 1000.2576 | 96.747
1.6736 | 1000.9852 | 97.494 | 1001.6018 | 97.5532 | 1000.3476 | 96.8159
1.6806 | 1001.0076 | 97.4971 | 1001.6318 | 97.5654 | 1000.4082 | 96.8512
1.6875 | 1001.0087 | 97.5033 | 1001.6302 | 97.5474 | 1000.4516 | 96.8732
1.6944 | 1001.0036 | 97.5161 | 1001.6626 | 97.5728 | 1000.4851 | 96.8897
1.7014 | 1001.0071 | 97.5271 | 1001.7193 | 97.6058 | 1000.4813 | 96.8623
1.7083 | 1001.0147 | 97.5327 | 1001.7493 | 97.6063 | 1000.3901 | 96.7563
1.7153 | 1001.0263 | 97.5353 | 1001.7631 | 97.6018 | 1000.3656 | 96.7315
1.7222 | 1001.041 | 97.5376 | 1001.7793 | 97.6003 | 1000.3866 | 96.7414
1.7292 | 1001.0746 | 97.5335 | 1001.797 | 97.6012 | 1000.4306 | 96.7755
1.7361 | 1001.1204 | 97.5246 | 1001.8185 | 97.6072 | 1000.4939 | 96.8324
1.7431 | 1001.1561 | 97.5192 | 1001.848 | 97.6205 | 1000.5516 | 96.8762
1.75 | 1001.1833 | 97.5157 | 1001.8639 | 97.6187 | 1000.5974 | 96.904
1.7569 | 1001.2068 | 97.5138 | 1001.8547 | 97.6014 | 1000.6453 | 96.9384
1.7639 | 1001.2261 | 97.5148 | 1001.8393 | 97.5886 | 1000.6878 | 96.9644
1.7708 | 1001.2407 | 97.5173 | 1001.8096 | 97.5662 | 1000.7231 | 96.9829
1.7778 | 1001.2511 | 97.5219 | 1001.7908 | 97.5578 | 1000.7524 | 96.9962
1.7847 | 1001.2548 | 97.5285 | 1001.7845 | 97.5552 | 1000.7724 | 96.9989
1.7917 | 1001.2559 | 97.5357 | 1001.7813 | 97.5506 | 1000.7654 | 96.9681
1.7986 | 1001.2626 | 97.541 | 1001.7766 | 97.5416 | 1000.7535 | 96.9396
1.8056 | 1001.2766 | 97.5443 | 1001.775 | 97.5349 | 1000.7676 | 96.9487
1.8125 | 1001.2951 | 97.5488 | 1001.8292 | 97.5807 | 1000.7975 | 96.9753
1.8194 | 1001.313 | 97.5504 | 1001.8723 | 97.5977 | 1000.8251 | 96.9955
1.8264 | 1001.3279 | 97.55 | 1001.8712 | 97.5825 | 1000.849 | 97.011
1.8333 | 1001.3366 | 97.5521 | 1001.8677 | 97.5774 | 1000.87 | 97.0229
1.8403 | 1001.3387 | 97.5578 | 1001.889 | 97.5928 | 1000.8883 | 97.0321
1.8472 | 1001.343 | 97.5655 | 1001.9841 | 97.6695 | 1000.8959 | 97.0271
1.8542 | 1001.3478 | 97.5638 | 1002.0681 | 97.6984 | 1000.8827 | 96.9961
1.8611 | 1001.3584 | 97.557 | 1002.1176 | 97.6969 | 1000.8416 | 96.9357
1.8681 | 1001.3757 | 97.5505 | 1002.1369 | 97.6819 | 1000.7723 | 96.8523
1.875 | 1001.3992 | 97.5452 | 1002.1009 | 97.6349 | 1000.6717 | 96.7491
1.8819 | 1001.4166 | 97.5431 | 1001.9829 | 97.5371 | 1000.5934 | 96.6723
1.8889 | 1001.3986 | 97.5467 | 1001.8756 | 97.4674 | 1000.5744 | 96.6444
1.8958 | 1001.378 | 97.5588 | 1001.815 | 97.4303 | 1000.6553 | 96.7233
1.9028 | 1001.3808 | 97.5758 | 1001.871 | 97.5055 | 1000.7526 | 96.8166
1.9097 | 1001.3994 | 97.5908 | 1001.9629 | 97.5852 | 1000.8264 | 96.8863
1.9167 | 1001.4267 | 97.5964 | 1002.0521 | 97.6502 | 1000.8701 | 96.9224
1.9236 | 1001.4512 | 97.5919 | 1002.1157 | 97.6786 | 1000.8481 | 96.8788
1.9306 | 1001.4702 | 97.5862 | 1002.1401 | 97.6745 | 1000.7497 | 96.7748
1.9375 | 1001.4818 | 97.5848 | 1002.1502 | 97.668 | 1000.7707 | 96.8012
1.9444 | 1001.4885 | 97.5867 | 1002.1763 | 97.6769 | 1000.8528 | 96.8813
1.9514 | 1001.4994 | 97.5866 | 1002.2136 | 97.6935 | 1000.9221 | 96.9399
1.9583 | 1001.5148 | 97.5826 | 1002.2528 | 97.7089 | 1000.9742 | 96.9828
1.9653 | 1001.5296 | 97.5781 | 1002.289 | 97.7193 | 1001.0082 | 97.0044
1.9722 | 1001.5418 | 97.5739 | 1002.3135 | 97.719 | 1000.99 | 96.9596
1.9792 | 1001.5552 | 97.5704 | 1002.3223 | 97.7099 | 1000.9539 | 96.9062
1.9861 | 1001.5705 | 97.568 | 1002.3235 | 97.7009 | 1000.9727 | 96.9231
1.9931 | 1001.5877 | 97.5662 | 1002.2837 | 97.6623 | 1001.0197 | 96.9685
2 | 1001.6029 | 97.5669 | 1002.2182 | 97.6218 | 1001.0595 | 97.0009
2.0069 | 1001.6116 | 97.5712 | 1002.1719 | 97.6058 | 1001.0898 | 97.0239
2.0139 | 1001.6114 | 97.5815 | 1002.2233 | 97.6745 | 1001.113 | 97.0406
2.0208 | 1001.5954 | 97.593 | 1002.2959 | 97.721 | 1001.1308 | 97.0532
2.0278 | 1001.5738 | 97.601 | 1002.3519 | 97.7389 | 1001.1423 | 97.0619
2.0347 | 1001.5585 | 97.6053 | 1002.3894 | 97.7409 | 1001.1383 | 97.0525
2.0417 | 1001.55 | 97.607 | 1002.3871 | 97.7179 | 1001.0814 | 96.9816
2.0486 | 1001.5494 | 97.6055 | 1002.2994 | 97.6459 | 1000.9504 | 96.8547
2.0556 | 1001.5463 | 97.6051 | 1002.1786 | 97.5719 | 1000.8403 | 96.7618
2.0625 | 1001.5358 | 97.607 | 1002.0703 | 97.5097 | 1000.7616 | 96.6936
2.0694 | 1001.5538 | 97.6119 | 1001.9811 | 97.4566 | 1000.7059 | 96.6437
2.0764 | 1001.5811 | 97.6096 | 1001.9255 | 97.4247 | 1000.7666 | 96.7056
2.0833 | 1001.6007 | 97.6115 | 1001.9146 | 97.4241 | 1000.8761 | 96.8113
2.0903 | 1001.6176 | 97.6171 | 1001.9344 | 97.4466 | 1000.9699 | 96.8955
2.0972 | 1001.6314 | 97.6242 | 1001.9691 | 97.4794 | 1001.0412 | 96.9577
2.1042 | 1001.6414 | 97.6321 | 1002.0094 | 97.5145 | 1001.0958 | 97.0039
2.1111 | 1001.6525 | 97.6399 | 1002.047 | 97.5438 | 1001.1191 | 97.0094
2.1181 | 1001.6739 | 97.6492 | 1002.1413 | 97.6361 | 1001.0121 | 96.8831
2.125 | 1001.6967 | 97.6504 | 1002.2024 | 97.6686 | 1000.9163 | 96.7915
2.1319 | 1001.7168 | 97.6467 | 1002.1994 | 97.6391 | 1000.8541 | 96.7248
2.1389 | 1001.734 | 97.6426 | 1002.139 | 97.5684 | 1000.8156 | 96.6762
2.1458 | 1001.7496 | 97.6451 | 1002.1436 | 97.5787 | 1000.873 | 96.7166
2.1528 | 1001.7658 | 97.6518 | 1002.2111 | 97.6313 | 1000.996 | 96.8286
2.1597 | 1001.7736 | 97.6606 | 1002.3019 | 97.6928 | 1001.1032 | 96.918
2.1667 | 1001.765 | 97.671 | 1002.3868 | 97.738 | 1001.1782 | 96.9772
2.1736 | 1001.756 | 97.6811 | 1002.4468 | 97.7561 | 1001.1538 | 96.9229
2.1806 | 1001.7564 | 97.6852 | 1002.4645 | 97.744 | 1001.0611 | 96.8286
2.1875 | 1001.7629 | 97.6865 | 1002.4428 | 97.7117 | 1000.984 | 96.7604
2.1944 | 1001.7712 | 97.6876 | 1002.4026 | 97.6755 | 1000.9312 | 96.7111
2.2014 | 1001.7798 | 97.6917 | 1002.39 | 97.6731 | 1000.9579 | 96.7323
2.2083 | 1001.7906 | 97.6985 | 1002.4116 | 97.6932 | 1001.0202 | 96.7803
2.2153 | 1001.8205 | 97.7026 | 1002.4413 | 97.7091 | 1001.0793 | 96.8245
2.2222 | 1001.8648 | 97.697 | 1002.4439 | 97.6936 | 1001.1469 | 96.8832
2.2292 | 1001.9054 | 97.6904 | 1002.3976 | 97.6429 | 1001.2135 | 96.9382
2.2361 | 1001.9363 | 97.6908 | 1002.3963 | 97.6511 | 1001.2264 | 96.9242
2.2431 | 1001.9625 | 97.6952 | 1002.4376 | 97.6917 | 1001.1541 | 96.8375
2.25 | 1001.9837 | 97.6976 | 1002.4597 | 97.7001 | 1001.0934 | 96.7736
2.2569 | 1001.9981 | 97.6954 | 1002.3893 | 97.6152 | 1001.057 | 96.7265
2.2639 | 1002.0012 | 97.6957 | 1002.3116 | 97.5472 | 1001.0369 | 96.6918
2.2708 | 1002.0016 | 97.6998 | 1002.2674 | 97.5051 | 1001.1076 | 96.7432
2.2778 | 1002.0084 | 97.7061 | 1002.262 | 97.4908 | 1001.2005 | 96.809
2.2847 | 1002.0191 | 97.7132 | 1002.2815 | 97.4963 | 1001.2822 | 96.8687
2.2917 | 1002.0341 | 97.7214 | 1002.3149 | 97.5143 | 1001.3535 | 96.9253
2.2986 | 1002.0543 | 97.7292 | 1002.3502 | 97.5337 | 1001.3808 | 96.9312
2.3056 | 1002.07 | 97.7349 | 1002.3761 | 97.5449 | 1001.3735 | 96.908
2.3125 | 1002.0765 | 97.7409 | 1002.3989 | 97.5543 | 1001.4064 | 96.9372
2.3194 | 1002.0862 | 97.7493 | 1002.4242 | 97.5655 | 1001.4314 | 96.9475
2.3264 | 1002.0745 | 97.7534 | 1002.4554 | 97.5865 | 1001.3576 | 96.8648
2.3333 | 1002.0674 | 97.7686 | 1002.5112 | 97.6361 | 1001.3242 | 96.836
2.3403 | 1002.0981 | 97.7841 | 1002.5705 | 97.6743 | 1001.3814 | 96.8943
2.3472 | 1002.147 | 97.7857 | 1002.6137 | 97.6924 | 1001.468 | 96.9772
2.3542 | 1002.1918 | 97.782 | 1002.6168 | 97.6783 | 1001.5535 | 97.0582
2.3611 | 1002.2281 | 97.781 | 1002.6279 | 97.6862 | 1001.6242 | 97.1186
2.3681 | 1002.2579 | 97.7826 | 1002.6527 | 97.7042 | 1001.6823 | 97.1635
2.375 | 1002.2829 | 97.7856 | 1002.6843 | 97.7255 | 1001.7313 | 97.1969
2.3819 | 1002.2998 | 97.7898 | 1002.7185 | 97.7464 | 1001.7733 | 97.2219
2.3889 | 1002.2858 | 97.7968 | 1002.7527 | 97.7653 | 1001.8089 | 97.2409
2.3958 | 1002.2735 | 97.814 | 1002.8352 | 97.8281 | 1001.8169 | 97.2255
2.4028 | 1002.2888 | 97.8257 | 1002.9398 | 97.8918 | 1001.8215 | 97.2166
2.4097 | 1002.3186 | 97.8203 | 1003.0279 | 97.925 | 1001.8422 | 97.2317
2.4167 | 1002.3513 | 97.8098 | 1003.0929 | 97.9368 | 1001.8667 | 97.2462
2.4236 | 1002.3793 | 97.8011 | 1003.1368 | 97.937 | 1001.8838 | 97.2473
2.4306 | 1002.3927 | 97.8041 | 1003.1616 | 97.9303 | 1001.8951 | 97.2409
2.4375 | 1002.3906 | 97.8116 | 1003.1775 | 97.925 | 1001.895 | 97.2219
2.4444 | 1002.3955 | 97.8176 | 1003.2003 | 97.9297 | 1001.8787 | 97.1873
2.4514 | 1002.4047 | 97.8215 | 1003.2198 | 97.9293 | 1001.8534 | 97.1474
2.4583 | 1002.4276 | 97.8169 | 1003.2203 | 97.9166 | 1001.7739 | 97.0558
2.4653 | 1002.4666 | 97.8078 | 1003.2045 | 97.8997 | 1001.7199 | 96.9982
2.4722 | 1002.4971 | 97.8044 | 1003.197 | 97.8938 | 1001.7623 | 97.0362
2.4792 | 1002.5024 | 97.8097 | 1003.2001 | 97.893 | 1001.8397 | 97.1035
2.4861 | 1002.4961 | 97.8189 | 1003.1986 | 97.8877 | 1001.9097 | 97.1633
2.4931 | 1002.5113 | 97.8203 | 1003.1616 | 97.8566 | 1001.9626 | 97.2073
2.5 | 1002.5424 | 97.8176 | 1003.1532 | 97.8641 | 1001.9987 | 97.2321
2.5069 | 1002.5674 | 97.8162 | 1003.1589 | 97.8717 | 1002.0099 | 97.2238
2.5139 | 1002.5851 | 97.8148 | 1003.1259 | 97.8402 | 1002.0033 | 97.1963
2.5208 | 1002.5969 | 97.8185 | 1003.1505 | 97.8717 | 1002.0172 | 97.1991
2.5278 | 1002.6041 | 97.8228 | 1003.2056 | 97.9078 | 1002.0564 | 97.2344
2.5347 | 1002.6095 | 97.8239 | 1003.228 | 97.9054 | 1002.0919 | 97.2603
2.5417 | 1002.6127 | 97.8257 | 1003.2253 | 97.8935 | 1002.1198 | 97.2794
2.5486 | 1002.5998 | 97.8347 | 1003.2552 | 97.9177 | 1002.1412 | 97.2937
2.5556 | 1002.5829 | 97.8468 | 1003.3089 | 97.9498 | 1002.1545 | 97.3019
2.5625 | 1002.574 | 97.8532 | 1003.3513 | 97.9602 | 1002.1134 | 97.2415
2.5694 | 1002.5727 | 97.8546 | 1003.355 | 97.9427 | 1001.9828 | 97.1092
2.5764 | 1002.5774 | 97.8544 | 1003.3274 | 97.9156 | 1001.8715 | 97.0128
2.5833 | 1002.5841 | 97.8552 | 1003.2965 | 97.8969 | 1001.7931 | 96.9423
2.5903 | 1002.5997 | 97.855 | 1003.2674 | 97.8817 | 1001.7389 | 96.8907
2.5972 | 1002.6303 | 97.8497 | 1003.2346 | 97.8614 | 1001.7031 | 96.853
2.6042 | 1002.6612 | 97.8428 | 1003.1711 | 97.807 | 1001.6822 | 96.8251
2.6111 | 1002.6768 | 97.8389 | 1003.0791 | 97.7289 | 1001.7892 | 96.9272
2.6181 | 1002.6803 | 97.842 | 1003.0358 | 97.7034 | 1001.9157 | 97.0352
2.625 | 1002.6725 | 97.8495 | 1003.0353 | 97.7098 | 1002.0178 | 97.1229
2.6319 | 1002.6696 | 97.8675 | 1003.1398 | 97.8243 | 1002.0789 | 97.1662
2.6389 | 1002.6854 | 97.8821 | 1003.2409 | 97.895 | 1002.0843 | 97.1499
2.6458 | 1002.7024 | 97.8848 | 1003.2948 | 97.914 | 1002.1018 | 97.1623
2.6528 | 1002.7173 | 97.8847 | 1003.3146 | 97.9091 | 1002.1405 | 97.1998
2.6597 | 1002.733 | 97.8837 | 1003.2965 | 97.8807 | 1002.1717 | 97.223
2.6667 | 1002.7493 | 97.8843 | 1003.2857 | 97.8715 | 1002.1558 | 97.1875
2.6736 | 1002.7678 | 97.886 | 1003.2871 | 97.8727 | 1002.0552 | 97.0799
2.6806 | 1002.7874 | 97.8837 | 1003.227 | 97.8117 | 1001.9709 | 97.001
2.6875 | 1002.8028 | 97.8823 | 1003.1635 | 97.7605 | 1001.9435 | 96.9663
2.6944 | 1002.8135 | 97.8834 | 1003.1191 | 97.7209 | 1001.9411 | 96.947
2.7014 | 1002.826 | 97.8883 | 1003.1203 | 97.7246 | 1001.9106 | 96.9031
2.7083 | 1002.8427 | 97.8946 | 1003.1474 | 97.7461 | 1001.8858 | 96.8711
2.7153 | 1002.8625 | 97.9013 | 1003.1962 | 97.7874 | 1001.8883 | 96.8609
2.7222 | 1002.882 | 97.906 | 1003.2359 | 97.8093 | 1001.8826 | 96.8414
2.7292 | 1002.8854 | 97.906 | 1003.2073 | 97.7554 | 1001.8802 | 96.8279
2.7361 | 1002.8503 | 97.9033 | 1003.147 | 97.6879 | 1001.8873 | 96.823
2.7431 | 1002.8099 | 97.9097 | 1003.1128 | 97.6507 | 1001.9689 | 96.8927
2.75 | 1002.7866 | 97.9194 | 1003.12 | 97.6485 | 1002.0912 | 97.0109
2.7569 | 1002.7804 | 97.9322 | 1003.1563 | 97.6744 | 1002.1982 | 97.1186
2.7639 | 1002.7881 | 97.9467 | 1003.2042 | 97.7137 | 1002.2687 | 97.1891
2.7708 | 1002.8048 | 97.9606 | 1003.2538 | 97.7568 | 1002.3231 | 97.2509
2.7778 | 1002.8487 | 97.9772 | 1003.3018 | 97.8002 | 1002.3682 | 97.3036
2.7847 | 1002.9097 | 97.9819 | 1003.3469 | 97.8409 | 1002.4066 | 97.3449
2.7917 | 1002.9701 | 97.9833 | 1003.448 | 97.9376 | 1002.4352 | 97.3662
2.7986 | 1003.0177 | 97.9814 | 1003.5435 | 98.0014 | 1002.4524 | 97.3659
2.8056 | 1003.0512 | 97.9774 | 1003.607 | 98.0284 | 1002.4686 | 97.3611
2.8125 | 1003.0763 | 97.9744 | 1003.6657 | 98.0529 | 1002.4988 | 97.3724
2.8194 | 1003.0941 | 97.9732 | 1003.734 | 98.0818 | 1002.5297 | 97.3798
2.8264 | 1003.108 | 97.971 | 1003.7942 | 98.0953 | 1002.4969 | 97.3093
2.8333 | 1003.1273 | 97.9657 | 1003.8186 | 98.0817 | 1002.3989 | 97.1943
2.8403 | 1003.1533 | 97.9609 | 1003.8138 | 98.0586 | 1002.3207 | 97.1091
2.8472 | 1003.1814 | 97.957 | 1003.7625 | 98.0012 | 1002.2703 | 97.0454
2.8542 | 1003.2045 | 97.9541 | 1003.6493 | 97.9007 | 1002.2395 | 96.9974
2.8611 | 1003.2173 | 97.9562 | 1003.5706 | 97.846 | 1002.3503 | 97.0997
2.8681 | 1003.2216 | 97.9631 | 1003.551 | 97.8342 | 1002.4759 | 97.2012
2.875 | 1003.2284 | 97.9754 | 1003.604 | 97.8881 | 1002.5709 | 97.2755
2.8819 | 1003.2454 | 97.9875 | 1003.6927 | 97.9617 | 1002.6409 | 97.3306
2.8889 | 1003.2633 | 97.9941 | 1003.7757 | 98.0178 | 1002.6884 | 97.363
2.8958 | 1003.2668 | 98.0001 | 1003.8595 | 98.071 | 1002.7265 | 97.3904
2.9028 | 1003.2549 | 98.0082 | 1003.9391 | 98.1093 | 1002.761 | 97.4183
2.9097 | 1003.242 | 98.0143 | 1004.0053 | 98.1288 | 1002.7859 | 97.4375
2.9167 | 1003.2375 | 98.0155 | 1004.0499 | 98.1302 | 1002.7673 | 97.4012
2.9236 | 1003.2437 | 98.0123 | 1004.0591 | 98.1131 | 1002.6425 | 97.2696
2.9306 | 1003.2679 | 98.0023 | 1004.0363 | 98.0881 | 1002.5341 | 97.1732
2.9375 | 1003.3018 | 97.9935 | 1004.0019 | 98.0645 | 1002.4603 | 97.1018
2.9444 | 1003.3228 | 97.9907 | 1003.9633 | 98.0412 | 1002.412 | 97.0484
2.9514 | 1003.3194 | 97.994 | 1003.9182 | 98.011 | 1002.3809 | 97.0081
2.9583 | 1003.3059 | 98.0018 | 1003.874 | 97.9826 | 1002.3604 | 96.9781
2.9653 | 1003.296 | 98.0086 | 1003.829 | 97.9505 | 1002.3463 | 96.956
2.9722 | 1003.2904 | 98.0168 | 1003.8174 | 97.9528 | 1002.3884 | 96.9869
2.9792 | 1003.2921 | 98.0274 | 1003.8517 | 97.9895 | 1002.5041 | 97.1007
2.9861 | 1003.3003 | 98.0376 | 1003.9071 | 98.0315 | 1002.6111 | 97.2003
2.9931 | 1003.3308 | 98.0415 | 1003.9598 | 98.0634 | 1002.6737 | 97.2507
3 | 1003.3709 | 98.0343 | 1004.0077 | 98.0893 | 1002.7021 | 97.2665
3.0069 | 1003.4037 | 98.0268 | 1004.0461 | 98.1031 | 1002.7288 | 97.2836
3.0139 | 1003.4279 | 98.0214 | 1004.0822 | 98.1155 | 1002.7759 | 97.3251
3.0208 | 1003.4451 | 98.0178 | 1004.1242 | 98.1329 | 1002.8322 | 97.3749
3.0278 | 1003.4544 | 98.0167 | 1004.1658 | 98.1466 | 1002.8783 | 97.4091
3.0347 | 1003.4552 | 98.0187 | 1004.2016 | 98.154 | 1002.9034 | 97.4178
3.0417 | 1003.4582 | 98.017 | 1004.2181 | 98.1465 | 1002.8962 | 97.3901
3.0486 | 1003.4759 | 98.0119 | 1004.1895 | 98.1101 | 1002.8378 | 97.313
3.0556 | 1003.497 | 98.0077 | 1004.0858 | 98.0276 | 1002.7369 | 97.2092
3.0625 | 1003.5095 | 98.0091 | 1004.0038 | 97.9853 | 1002.657 | 97.1319
3.0694 | 1003.5187 | 98.0154 | 1003.9914 | 98.0025 | 1002.6028 | 97.0742
3.0764 | 1003.5285 | 98.0201 | 1003.9975 | 98.0162 | 1002.5671 | 97.0315
3.0833 | 1003.5374 | 98.0223 | 1004.0031 | 98.0168 | 1002.6258 | 97.0787
3.0903 | 1003.5461 | 98.0241 | 1004.0141 | 98.0158 | 1002.7503 | 97.2007
3.0972 | 1003.5527 | 98.0268 | 1004.0313 | 98.0222 | 1002.8529 | 97.2905
3.1042 | 1003.5553 | 98.0307 | 1004.0477 | 98.0306 | 1002.9274 | 97.3565
3.1111 | 1003.5605 | 98.0351 | 1004.0842 | 98.0616 | 1002.9798 | 97.4021
3.1181 | 1003.5678 | 98.0358 | 1004.0972 | 98.0639 | 1002.8771 | 97.2772
3.125 | 1003.5736 | 98.0327 | 1004.0287 | 97.9976 | 1002.7781 | 97.1855
3.1319 | 1003.5736 | 98.0318 | 1003.9503 | 97.9384 | 1002.71 | 97.1179
3.1389 | 1003.5575 | 98.0347 | 1003.9051 | 97.9061 | 1002.7921 | 97.2095
3.1458 | 1003.5494 | 98.0497 | 1003.9879 | 98.0031 | 1002.8914 | 97.3003
3.1528 | 1003.558 | 98.0615 | 1004.0983 | 98.0895 | 1002.9643 | 97.3677
3.1597 | 1003.5625 | 98.0652 | 1004.1892 | 98.1432 | 1003.0165 | 97.4184
3.1667 | 1003.5632 | 98.0643 | 1004.2475 | 98.1614 | 1003.0545 | 97.4566
3.1736 | 1003.5696 | 98.0587 | 1004.214 | 98.1118 | 1003.0826 | 97.4853
3.1806 | 1003.5639 | 98.0598 | 1004.1675 | 98.0805 | 1003.0542 | 97.4382
3.1875 | 1003.5487 | 98.0698 | 1004.1798 | 98.1065 | 1002.9302 | 97.3113
3.1944 | 1003.54 | 98.0789 | 1004.1997 | 98.1225 | 1002.822 | 97.2185
3.2014 | 1003.5366 | 98.0835 | 1004.2013 | 98.1177 | 1002.7447 | 97.1511
3.2083 | 1003.5445 | 98.0845 | 1004.1887 | 98.1042 | 1002.6899 | 97.1024
3.2153 | 1003.5733 | 98.0788 | 1004.1713 | 98.0904 | 1002.6595 | 97.0731
3.2222 | 1003.6062 | 98.072 | 1004.1639 | 98.0842 | 1002.7147 | 97.1213
3.2292 | 1003.6265 | 98.0708 | 1004.1843 | 98.0997 | 1002.8096 | 97.2028
3.2361 | 1003.6378 | 98.073 | 1004.2224 | 98.1236 | 1002.9096 | 97.2942
3.2431 | 1003.6462 | 98.075 | 1004.2559 | 98.1371 | 1002.9863 | 97.3591
3.25 | 1003.6584 | 98.0735 | 1004.2358 | 98.1027 | 1003.0235 | 97.3783
3.2569 | 1003.6754 | 98.0716 | 1004.1888 | 98.0635 | 1003.0465 | 97.389
3.2639 | 1003.6899 | 98.0724 | 1004.1553 | 98.0426 | 1003.0665 | 97.3981
3.2708 | 1003.6956 | 98.0762 | 1004.1375 | 98.0318 | 1003.0829 | 97.4035
3.2778 | 1003.6998 | 98.0867 | 1004.215 | 98.1163 | 1003.1084 | 97.4239
3.2847 | 1003.7065 | 98.0922 | 1004.3058 | 98.1748 | 1003.1349 | 97.445
3.2917 | 1003.7122 | 98.0898 | 1004.3738 | 98.2015 | 1003.1404 | 97.4379
3.2986 | 1003.7184 | 98.0845 | 1004.4213 | 98.21 | 1003.1528 | 97.4458
3.3056 | 1003.7245 | 98.0797 | 1004.4588 | 98.2148 | 1003.1805 | 97.4737
3.3125 | 1003.7275 | 98.0778 | 1004.4856 | 98.2147 | 1003.195 | 97.4796
3.3194 | 1003.7195 | 98.0832 | 1004.5038 | 98.2127 | 1003.1752 | 97.4453
3.3264 | 1003.7051 | 98.0898 | 1004.5086 | 98.204 | 1003.1352 | 97.3977
3.3333 | 1003.6993 | 98.0938 | 1004.5004 | 98.1915 | 1003.0836 | 97.3437
3.3403 | 1003.6985 | 98.0968 | 1004.4895 | 98.1836 | 1003.0784 | 97.3461
3.3472 | 1003.6996 | 98.0998 | 1004.4873 | 98.1856 | 1003.1213 | 97.4041
3.3542 | 1003.7038 | 98.101 | 1004.476 | 98.1788 | 1003.1661 | 97.4581
3.3611 | 1003.7155 | 98.099 | 1004.4705 | 98.1843 | 1003.1996 | 97.4979
3.3681 | 1003.7267 | 98.0969 | 1004.4741 | 98.1945 | 1003.2089 | 97.5029
3.375 | 1003.7231 | 98.0997 | 1004.4738 | 98.1959 | 1003.1328 | 97.4102
3.3819 | 1003.712 | 98.1043 | 1004.4568 | 98.1848 | 1003.0171 | 97.3013
3.3889 | 1003.7054 | 98.1072 | 1004.4264 | 98.1673 | 1002.9253 | 97.2213
3.3958 | 1003.7011 | 98.1095 | 1004.3897 | 98.1474 | 1002.8601 | 97.1626
3.4028 | 1003.7133 | 98.109 | 1004.3642 | 98.1367 | 1002.9048 | 97.2095
3.4097 | 1003.7417 | 98.1034 | 1004.3672 | 98.1459 | 1003.0027 | 97.3067
3.4167 | 1003.7662 | 98.0987 | 1004.3887 | 98.1647 | 1003.0771 | 97.3678
3.4236 | 1003.7813 | 98.0959 | 1004.4138 | 98.1803 | 1003.1027 | 97.3725
3.4306 | 1003.7908 | 98.0938 | 1004.4317 | 98.1853 | 1003.1035 | 97.3571
3.4375 | 1003.7988 | 98.0923 | 1004.4378 | 98.1796 | 1003.1364 | 97.3869
3.4444 | 1003.8079 | 98.0907 | 1004.4033 | 98.1422 | 1003.1945 | 97.4474
3.4514 | 1003.8138 | 98.0918 | 1004.3557 | 98.1116 | 1003.2423 | 97.4909
3.4583 | 1003.811 | 98.0969 | 1004.3266 | 98.1026 | 1003.2772 | 97.5222
3.4653 | 1003.796 | 98.1077 | 1004.3558 | 98.143 | 1003.3022 | 97.545
3.4722 | 1003.7702 | 98.1174 | 1004.3408 | 98.1225 | 1003.2102 | 97.4306
3.4792 | 1003.7646 | 98.1229 | 1004.2827 | 98.0779 | 1003.0879 | 97.3182
3.4861 | 1003.7785 | 98.1203 | 1004.2141 | 98.0284 | 1002.9938 | 97.2363
3.4931 | 1003.7935 | 98.1213 | 1004.211 | 98.047 | 1002.9284 | 97.1764
3.5 | 1003.8086 | 98.1245 | 1004.248 | 98.0901 | 1002.8842 | 97.1326
3.5069 | 1003.8229 | 98.1253 | 1004.2872 | 98.1166 | 1002.9416 | 97.1847
3.5139 | 1003.8357 | 98.1251 | 1004.3371 | 98.1455 | 1003.0364 | 97.2663
3.5208 | 1003.8463 | 98.1248 | 1004.3935 | 98.1757 | 1003.1199 | 97.3369
3.5278 | 1003.8551 | 98.1233 | 1004.4323 | 98.1843 | 1003.1707 | 97.3715
3.5347 | 1003.8569 | 98.1246 | 1004.452 | 98.1816 | 1003.1903 | 97.376
3.5417 | 1003.842 | 98.1317 | 1004.4718 | 98.1872 | 1003.1811 | 97.3549
3.5486 | 1003.8407 | 98.1372 | 1004.4793 | 98.1848 | 1003.0944 | 97.2678
3.5556 | 1003.8584 | 98.1339 | 1004.4662 | 98.1708 | 1003.0182 | 97.204
3.5625 | 1003.8758 | 98.1304 | 1004.4344 | 98.1431 | 1002.966 | 97.1571
3.5694 | 1003.8902 | 98.1285 | 1004.3955 | 98.114 | 1002.9315 | 97.1223
3.5764 | 1003.8983 | 98.1294 | 1004.3719 | 98.0999 | 1002.9627 | 97.1446
3.5833 | 1003.8842 | 98.1335 | 1004.3544 | 98.0805 | 1003.0357 | 97.2031
3.5903 | 1003.8535 | 98.1389 | 1004.2968 | 98.0198 | 1003.0795 | 97.2287
3.5972 | 1003.8244 | 98.1467 | 1004.2545 | 97.9895 | 1003.1302 | 97.2775
3.6042 | 1003.8067 | 98.157 | 1004.252 | 97.995 | 1003.2029 | 97.3624
3.6111 | 1003.8003 | 98.1687 | 1004.2719 | 98.0185 | 1003.2687 | 97.4414
3.6181 | 1003.8026 | 98.1808 | 1004.3063 | 98.0567 | 1003.3158 | 97.5008
3.625 | 1003.8108 | 98.1918 | 1004.3466 | 98.0985 | 1003.3491 | 97.5461
3.6319 | 1003.8528 | 98.1995 | 1004.3791 | 98.1304 | 1003.3744 | 97.5813
3.6389 | 1003.9004 | 98.1951 | 1004.4375 | 98.1876 | 1003.3975 | 97.609
3.6458 | 1003.9326 | 98.1911 | 1004.518 | 98.2507 | 1003.393 | 97.5899
3.6528 | 1003.9518 | 98.1849 | 1004.5583 | 98.261 | 1003.2751 | 97.456
3.6597 | 1003.9682 | 98.1769 | 1004.4836 | 98.1786 | 1003.1745 | 97.3574
3.6667 | 1003.9572 | 98.1762 | 1004.3956 | 98.1112 | 1003.1078 | 97.2841
3.6736 | 1003.9239 | 98.1813 | 1004.3233 | 98.0539 | 1003.0624 | 97.2294
3.6806 | 1003.8943 | 98.1895 | 1004.2816 | 98.0189 | 1003.1314 | 97.292
3.6875 | 1003.9132 | 98.2094 | 1004.3545 | 98.0983 | 1003.234 | 97.3863
3.6944 | 1003.9584 | 98.2183 | 1004.4731 | 98.1979 | 1003.3239 | 97.4718
3.7014 | 1003.992 | 98.2198 | 1004.578 | 98.2664 | 1003.3934 | 97.536
3.7083 | 1003.9968 | 98.223 | 1004.6538 | 98.2995 | 1003.4473 | 97.5841
3.7153 | 1003.9892 | 98.2252 | 1004.6285 | 98.2502 | 1003.4888 | 97.6203
3.7222 | 1004.0073 | 98.2243 | 1004.5992 | 98.2308 | 1003.5206 | 97.6477
3.7292 | 1004.042 | 98.2189 | 1004.5842 | 98.222 | 1003.527 | 97.6382
3.7361 | 1004.0705 | 98.215 | 1004.5564 | 98.199 | 1003.4086 | 97.5005
3.7431 | 1004.0927 | 98.2156 | 1004.5719 | 98.2228 | 1003.3051 | 97.3988
3.75 | 1004.1118 | 98.2151 | 1004.5712 | 98.2078 | 1003.2372 | 97.3236
3.7569 | 1004.128 | 98.2137 | 1004.5403 | 98.1653 | 1003.282 | 97.3535
3.7639 | 1004.1362 | 98.2148 | 1004.5091 | 98.1278 | 1003.3816 | 97.4355
3.7708 | 1004.1432 | 98.2221 | 1004.5429 | 98.1584 | 1003.4472 | 97.4714
3.7778 | 1004.1608 | 98.231 | 1004.6247 | 98.2301 | 1003.3778 | 97.3777
3.7847 | 1004.18 | 98.2324 | 1004.6766 | 98.2564 | 1003.3092 | 97.3092
3.7917 | 1004.1957 | 98.2308 | 1004.6999 | 98.2574 | 1003.2651 | 97.2591
3.7986 | 1004.2063 | 98.23 | 1004.7101 | 98.247 | 1003.2951 | 97.2743
3.8056 | 1004.2128 | 98.2298 | 1004.6946 | 98.209 | 1003.4036 | 97.374
3.8125 | 1004.22 | 98.2305 | 1004.654 | 98.1602 | 1003.4968 | 97.4471
3.8194 | 1004.2305 | 98.2331 | 1004.6296 | 98.1397 | 1003.5404 | 97.4674
3.8264 | 1004.2435 | 98.2364 | 1004.6209 | 98.1306 | 1003.5669 | 97.4801
3.8333 | 1004.2568 | 98.2402 | 1004.6228 | 98.1293 | 1003.5978 | 97.5023
3.8403 | 1004.2702 | 98.2443 | 1004.6319 | 98.133 | 1003.6229 | 97.5169
3.8472 | 1004.2811 | 98.248 | 1004.6382 | 98.1326 | 1003.6048 | 97.4816
3.8542 | 1004.28 | 98.2515 | 1004.6264 | 98.117 | 1003.5175 | 97.3909
3.8611 | 1004.2544 | 98.2578 | 1004.6501 | 98.1458 | 1003.4433 | 97.3245
3.8681 | 1004.2375 | 98.2748 | 1004.7208 | 98.2109 | 1003.501 | 97.3904
3.875 | 1004.242 | 98.289 | 1004.8023 | 98.2667 | 1003.5872 | 97.4731
3.8819 | 1004.2718 | 98.2925 | 1004.8693 | 98.3034 | 1003.6189 | 97.4885
3.8889 | 1004.3096 | 98.2842 | 1004.9025 | 98.3116 | 1003.5401 | 97.4038
3.8958 | 1004.3433 | 98.2749 | 1004.8898 | 98.2859 | 1003.4697 | 97.342
3.9028 | 1004.3695 | 98.2674 | 1004.8235 | 98.218 | 1003.4256 | 97.2962
3.9097 | 1004.3822 | 98.2637 | 1004.7395 | 98.1451 | 1003.4535 | 97.3103
3.9167 | 1004.3857 | 98.2656 | 1004.6946 | 98.1098 | 1003.5503 | 97.3922
3.9236 | 1004.3862 | 98.2713 | 1004.6886 | 98.1029 | 1003.6335 | 97.4516
3.9306 | 1004.3888 | 98.2795 | 1004.7059 | 98.115 | 1003.7165 | 97.527
3.9375 | 1004.4015 | 98.2884 | 1004.7385 | 98.1406 | 1003.7905 | 97.5967
3.9444 | 1004.4183 | 98.2951 | 1004.777 | 98.1714 | 1003.8431 | 97.6418
3.9514 | 1004.437 | 98.3018 | 1004.8364 | 98.2216 | 1003.8449 | 97.6226
3.9583 | 1004.4586 | 98.3081 | 1004.9285 | 98.2988 | 1003.8264 | 97.5897
3.9653 | 1004.4764 | 98.3099 | 1005.0066 | 98.3431 | 1003.8401 | 97.5984
3.9722 | 1004.4876 | 98.3097 | 1005.0627 | 98.3648 | 1003.8904 | 97.6507
3.9792 | 1004.4895 | 98.3117 | 1005.1133 | 98.386 | 1003.9386 | 97.6938
3.9861 | 1004.4834 | 98.3161 | 1005.1593 | 98.4037 | 1003.9757 | 97.7259
3.9931 | 1004.4845 | 98.3166 | 1005.2067 | 98.423 | 1003.9986 | 97.7425
4 | 1004.4966 | 98.3092 | 1005.2545 | 98.4385 | 1003.9932 | 97.7225
4.0069 | 1004.5129 | 98.2997 | 1005.2868 | 98.4379 | 1003.9722 | 97.6882
4.0139 | 1004.5305 | 98.2918 | 1005.2995 | 98.4274 | 1003.9599 | 97.6665
4.0208 | 1004.5501 | 98.2858 | 1005.2797 | 98.3999 | 1003.9717 | 97.6736
4.0278 | 1004.5616 | 98.2855 | 1005.2066 | 98.3445 | 1003.9937 | 97.6898
4.0347 | 1004.5454 | 98.2934 | 1005.1458 | 98.3167 | 1004.0058 | 97.6924
4.0417 | 1004.5214 | 98.3057 | 1005.1046 | 98.2997 | 1004.0009 | 97.6788
4.0486 | 1004.5043 | 98.3162 | 1005.0741 | 98.2871 | 1003.9916 | 97.6669
4.0556 | 1004.4985 | 98.3303 | 1005.1342 | 98.3617 | 1003.9889 | 97.6678
4.0625 | 1004.499 | 98.3403 | 1005.2106 | 98.414 | 1004.004 | 97.6943
4.0694 | 1004.4984 | 98.3432 | 1005.2677 | 98.4373 | 1004.0184 | 97.7161
4.0764 | 1004.4988 | 98.3422 | 1005.3061 | 98.4446 | 1004.0156 | 97.7137
4.0833 | 1004.5055 | 98.337 | 1005.3275 | 98.4422 | 1003.9906 | 97.6849
4.0903 | 1004.5281 | 98.3248 | 1005.3035 | 98.4098 | 1003.9316 | 97.6199
4.0972 | 1004.5591 | 98.3156 | 1005.2598 | 98.3797 | 1003.9159 | 97.6066
4.1042 | 1004.5642 | 98.3194 | 1005.2681 | 98.404 | 1003.9546 | 97.6508
4.1111 | 1004.5539 | 98.3287 | 1005.3007 | 98.4294 | 1003.9982 | 97.6931
4.1181 | 1004.5467 | 98.3341 | 1005.3298 | 98.4416 | 1004.0112 | 97.6955
4.125 | 1004.5433 | 98.336 | 1005.332 | 98.432 | 1003.8971 | 97.5717
4.1319 | 1004.544 | 98.336 | 1005.3044 | 98.4099 | 1003.7922 | 97.4807
4.1389 | 1004.5591 | 98.3314 | 1005.2554 | 98.3764 | 1003.7185 | 97.4138
4.1458 | 1004.5871 | 98.3242 | 1005.2002 | 98.3444 | 1003.6684 | 97.3642
4.1528 | 1004.6068 | 98.3207 | 1005.1488 | 98.3162 | 1003.6361 | 97.3269
4.1597 | 1004.6038 | 98.3195 | 1005.0602 | 98.2435 | 1003.6162 | 97.2987
4.1667 | 1004.5711 | 98.32 | 1004.9557 | 98.1637 | 1003.6034 | 97.2773
4.1736 | 1004.532 | 98.326 | 1004.8862 | 98.116 | 1003.6703 | 97.3346
4.1806 | 1004.5032 | 98.3343 | 1004.8575 | 98.0955 | 1003.7311 | 97.3775
4.1875 | 1004.4842 | 98.343 | 1004.8381 | 98.0807 | 1003.6939 | 97.3363
4.1944 | 1004.5086 | 98.3608 | 1004.8325 | 98.0837 | 1003.6497 | 97.307
4.2014 | 1004.5498 | 98.3626 | 1004.8114 | 98.0625 | 1003.6517 | 97.3145
4.2083 | 1004.5812 | 98.3616 | 1004.8119 | 98.0657 | 1003.7651 | 97.4401
4.2153 | 1004.6131 | 98.3684 | 1004.8925 | 98.1487 | 1003.8834 | 97.5535
4.2222 | 1004.6518 | 98.3786 | 1005.0212 | 98.2696 | 1003.9715 | 97.6315
4.2292 | 1004.6878 | 98.3844 | 1005.1489 | 98.3739 | 1004.0253 | 97.6683
4.2361 | 1004.7096 | 98.3849 | 1005.2548 | 98.4417 | 1004.0742 | 97.7057
4.2431 | 1004.7187 | 98.383 | 1005.3399 | 98.4802 | 1004.1292 | 97.7533
4.25 | 1004.7202 | 98.3812 | 1005.4093 | 98.5012 | 1004.1757 | 97.7886
4.2569 | 1004.7204 | 98.3788 | 1005.4651 | 98.5113 | 1004.2082 | 97.8084
4.2639 | 1004.7301 | 98.3719 | 1005.4794 | 98.4931 | 1004.2237 | 97.8091
4.2708 | 1004.7532 | 98.3642 | 1005.4183 | 98.4342 | 1004.2082 | 97.7724
4.2778 | 1004.7736 | 98.3617 | 1005.3408 | 98.3845 | 1004.0945 | 97.6433
4.2847 | 1004.7853 | 98.3623 | 1005.2589 | 98.3306 | 1003.9923 | 97.5442
4.2917 | 1004.794 | 98.3677 | 1005.244 | 98.3412 | 1003.9215 | 97.4704
4.2986 | 1004.8043 | 98.3727 | 1005.2516 | 98.3511 | 1003.8738 | 97.4157
4.3056 | 1004.8138 | 98.3757 | 1005.2566 | 98.353 | 1003.8427 | 97.3754
4.3125 | 1004.8162 | 98.3784 | 1005.2529 | 98.3436 | 1003.8232 | 97.3459
4.3194 | 1004.7953 | 98.3821 | 1005.2366 | 98.3187 | 1003.8485 | 97.357
4.3264 | 1004.763 | 98.3866 | 1005.176 | 98.2475 | 1003.9449 | 97.4451
4.3333 | 1004.7651 | 98.3963 | 1005.1435 | 98.2205 | 1004.0362 | 97.525
4.3403 | 1004.792 | 98.3987 | 1005.1403 | 98.2183 | 1004.0993 | 97.5801
4.3472 | 1004.8193 | 98.4008 | 1005.168 | 98.2454 | 1004.1564 | 97.6371
4.3542 | 1004.842 | 98.4082 | 1005.2656 | 98.3442 | 1004.2116 | 97.6932
4.3611 | 1004.8517 | 98.4165 | 1005.3706 | 98.426 | 1004.2596 | 97.7402
4.3681 | 1004.843 | 98.425 | 1005.4582 | 98.4811 | 1004.2966 | 97.7745
4.375 | 1004.8349 | 98.4309 | 1005.5118 | 98.4984 | 1004.3203 | 97.7948
4.3819 | 1004.8392 | 98.4297 | 1005.5282 | 98.4906 | 1004.3387 | 97.8123
4.3889 | 1004.84 | 98.4277 | 1005.4905 | 98.4517 | 1004.3629 | 97.8408
4.3958 | 1004.8337 | 98.4312 | 1005.4585 | 98.4367 | 1004.3838 | 97.8642
4.4028 | 1004.8297 | 98.4364 | 1005.4421 | 98.4335 | 1004.399 | 97.8819
4.4097 | 1004.8277 | 98.442 | 1005.4327 | 98.4331 | 1004.3952 | 97.8732
4.4167 | 1004.8363 | 98.4506 | 1005.4965 | 98.4982 | 1004.353 | 97.819
4.4236 | 1004.8606 | 98.4475 | 1005.5573 | 98.5274 | 1004.2824 | 97.7416
4.4306 | 1004.8929 | 98.4355 | 1005.579 | 98.5217 | 1004.1726 | 97.6342
4.4375 | 1004.9253 | 98.4249 | 1005.5497 | 98.4821 | 1004.0878 | 97.5547
4.4444 | 1004.9526 | 98.4163 | 1005.4386 | 98.3822 | 1004.0328 | 97.495
4.4514 | 1004.9646 | 98.414 | 1005.3342 | 98.309 | 1003.9985 | 97.4496
4.4583 | 1004.9384 | 98.4207 | 1005.3441 | 98.3442 | 1004.0804 | 97.5197
4.4653 | 1004.9175 | 98.4416 | 1005.4222 | 98.4148 | 1004.1836 | 97.6037
4.4722 | 1004.9142 | 98.4579 | 1005.5032 | 98.4696 | 1004.2501 | 97.652
4.4792 | 1004.9167 | 98.4651 | 1005.5352 | 98.4726 | 1004.1787 | 97.5676
4.4861 | 1004.9185 | 98.4625 | 1005.4525 | 98.3818 | 1004.1054 | 97.5068
4.4931 | 1004.9423 | 98.4596 | 1005.3617 | 98.3133 | 1004.0549 | 97.4631
4.5 | 1004.9747 | 98.4557 | 1005.3263 | 98.2973 | 1004.0226 | 97.4314
4.5069 | 1004.9981 | 98.4563 | 1005.3345 | 98.3133 | 1004.0045 | 97.4081
4.5139 | 1005.0107 | 98.4598 | 1005.3575 | 98.3347 | 1003.9966 | 97.3911
4.5208 | 1005.015 | 98.4645 | 1005.3754 | 98.3443 | 1003.9953 | 97.3789
4.5278 | 1004.9969 | 98.4677 | 1005.3825 | 98.3408 | 1003.9976 | 97.3704
4.5347 | 1004.9799 | 98.478 | 1005.4033 | 98.3522 | 1004.0592 | 97.4183
4.5417 | 1005.0094 | 98.4902 | 1005.4453 | 98.3776 | 1004.176 | 97.5269
4.5486 | 1005.0548 | 98.488 | 1005.4786 | 98.3871 | 1004.2734 | 97.6079
4.5556 | 1005.0929 | 98.4848 | 1005.491 | 98.3821 | 1004.3113 | 97.6232
4.5625 | 1005.1199 | 98.4818 | 1005.4637 | 98.3457 | 1004.2886 | 97.5851
4.5694 | 1005.1366 | 98.4809 | 1005.4259 | 98.3106 | 1004.236 | 97.529
4.5764 | 1005.1346 | 98.4814 | 1005.3889 | 98.2759 | 1004.1973 | 97.4875
4.5833 | 1005.1145 | 98.4849 | 1005.3728 | 98.2568 | 1004.2709 | 97.5541
4.5903 | 1005.1132 | 98.4979 | 1005.4099 | 98.2846 | 1004.357 | 97.6193
4.5972 | 1005.1296 | 98.51 | 1005.4976 | 98.3595 | 1004.4015 | 97.6428
4.6042 | 1005.1597 | 98.5194 | 1005.5698 | 98.4076 | 1004.3793 | 97.6066
4.6111 | 1005.1903 | 98.5202 | 1005.5923 | 98.4068 | 1004.3747 | 97.5982
4.6181 | 1005.1998 | 98.5215 | 1005.6227 | 98.425 | 1004.4168 | 97.6336
4.625 | 1005.1939 | 98.529 | 1005.6749 | 98.4611 | 1004.4923 | 97.7057
4.6319 | 1005.217 | 98.5379 | 1005.7079 | 98.4718 | 1004.5636 | 97.772
4.6389 | 1005.2549 | 98.5348 | 1005.7178 | 98.4689 | 1004.6061 | 97.8019
4.6458 | 1005.2883 | 98.533 | 1005.7488 | 98.4935 | 1004.6209 | 97.8006
4.6528 | 1005.3159 | 98.5333 | 1005.8082 | 98.5386 | 1004.6378 | 97.805
4.6597 | 1005.3345 | 98.5345 | 1005.8843 | 98.5893 | 1004.6709 | 97.8272
4.6667 | 1005.3448 | 98.5343 | 1005.9576 | 98.6249 | 1004.7102 | 97.8546
4.6736 | 1005.3534 | 98.531 | 1006.015 | 98.6409 | 1004.7605 | 97.8994
4.6806 | 1005.3646 | 98.5261 | 1006.0421 | 98.6348 | 1004.8065 | 97.9374
4.6875 | 1005.3754 | 98.5234 | 1006.0559 | 98.631 | 1004.8425 | 97.9646
4.6944 | 1005.38 | 98.5239 | 1006.0971 | 98.6556 | 1004.8629 | 97.9725
4.7014 | 1005.3794 | 98.5233 | 1006.1379 | 98.6655 | 1004.8466 | 97.9349
4.7083 | 1005.3826 | 98.5187 | 1006.1619 | 98.6608 | 1004.8282 | 97.9047
4.7153 | 1005.3923 | 98.5131 | 1006.1785 | 98.6572 | 1004.8435 | 97.9208
4.7222 | 1005.4021 | 98.5104 | 1006.1617 | 98.6328 | 1004.8725 | 97.9504
4.7292 | 1005.4044 | 98.5109 | 1006.0906 | 98.5838 | 1004.8953 | 97.9711
4.7361 | 1005.4034 | 98.5156 | 1006.0626 | 98.5889 | 1004.911 | 97.9856
4.7431 | 1005.3938 | 98.5247 | 1006.1098 | 98.6437 | 1004.9176 | 97.9896
4.75 | 1005.3734 | 98.5325 | 1006.1592 | 98.6662 | 1004.9202 | 97.993
4.7569 | 1005.3552 | 98.5357 | 1006.1912 | 98.6698 | 1004.9241 | 98.0025
4.7639 | 1005.3453 | 98.5349 | 1006.1832 | 98.6494 | 1004.9253 | 98.0101
4.7708 | 1005.3522 | 98.5262 | 1006.1107 | 98.6007 | 1004.9243 | 98.0162
4.7778 | 1005.3758 | 98.5172 | 1006.0451 | 98.5782 | 1004.9208 | 98.0162
4.7847 | 1005.3919 | 98.5131 | 1006.0149 | 98.5779 | 1004.8868 | 97.9695
4.7917 | 1005.396 | 98.5134 | 1006.0522 | 98.6257 | 1004.8149 | 97.884
4.7986 | 1005.3873 | 98.515 | 1006.0904 | 98.6416 | 1004.8065 | 97.8814
4.8056 | 1005.3674 | 98.5207 | 1006.1159 | 98.6431 | 1004.8249 | 97.9001
4.8125 | 1005.3467 | 98.5263 | 1006.1222 | 98.6336 | 1004.8281 | 97.899
4.8194 | 1005.3351 | 98.5277 | 1006.0671 | 98.583 | 1004.737 | 97.7983
4.8264 | 1005.3249 | 98.5274 | 1005.9565 | 98.5078 | 1004.6214 | 97.698
4.8333 | 1005.3131 | 98.531 | 1005.8872 | 98.4844 | 1004.5305 | 97.6241
4.8403 | 1005.3013 | 98.5353 | 1005.8332 | 98.4543 | 1004.5205 | 97.6216
4.8472 | 1005.2871 | 98.5383 | 1005.7742 | 98.4137 | 1004.5932 | 97.7058
4.8542 | 1005.2733 | 98.5435 | 1005.742 | 98.4019 | 1004.6429 | 97.7492
4.8611 | 1005.2618 | 98.5495 | 1005.7117 | 98.388 | 1004.561 | 97.6646
4.8681 | 1005.2497 | 98.5538 | 1005.6675 | 98.3621 | 1004.479 | 97.6031
4.875 | 1005.2362 | 98.5569 | 1005.6215 | 98.3326 | 1004.4198 | 97.5585
4.8819 | 1005.2391 | 98.5636 | 1005.5788 | 98.3036 | 1004.3772 | 97.5263
4.8889 | 1005.2666 | 98.568 | 1005.5533 | 98.2862 | 1004.4172 | 97.5686
4.8958 | 1005.2987 | 98.5678 | 1005.5573 | 98.2903 | 1004.5068 | 97.6538
4.9028 | 1005.3207 | 98.5691 | 1005.5845 | 98.3128 | 1004.5917 | 97.7294
4.9097 | 1005.304 | 98.5682 | 1005.624 | 98.3455 | 1004.6634 | 97.7939
4.9167 | 1005.2939 | 98.5861 | 1005.7131 | 98.4303 | 1004.7178 | 97.8433
4.9236 | 1005.3056 | 98.6044 | 1005.806 | 98.5043 | 1004.7376 | 97.8531
4.9306 | 1005.3267 | 98.6182 | 1005.899 | 98.5813 | 1004.6824 | 97.7878
4.9375 | 1005.3474 | 98.6246 | 1005.9596 | 98.619 | 1004.593 | 97.7071
4.9444 | 1005.3701 | 98.6246 | 1005.9855 | 98.6249 | 1004.5339 | 97.6562
4.9514 | 1005.4106 | 98.6176 | 1006.008 | 98.6302 | 1004.5868 | 97.7084
4.9583 | 1005.4575 | 98.6071 | 1006.0364 | 98.6364 | 1004.6882 | 97.8
4.9653 | 1005.495 | 98.6002 | 1006.0761 | 98.655 | 1004.787 | 97.8857
4.9722 | 1005.5208 | 98.5966 | 1006.1344 | 98.689 | 1004.8664 | 97.9478
4.9792 | 1005.5366 | 98.5932 | 1006.1967 | 98.7166 | 1004.9286 | 97.9919
4.9861 | 1005.5463 | 98.5895 | 1006.2484 | 98.7279 | 1004.9523 | 97.9859
4.9931 | 1005.5504 | 98.5903 | 1006.2738 | 98.7185 | 1004.9178 | 97.9197
5 | 1005.5451 | 98.5943 | 1006.2446 | 98.6741 | 1004.883 | 97.8681
5.0069 | 1005.5517 | 98.5953 | 1006.1644 | 98.6069 | 1004.9051 | 97.8858
5.0139 | 1005.567 | 98.598 | 1006.1431 | 98.6097 | 1004.9597 | 97.9401
5.0208 | 1005.5644 | 98.6078 | 1006.1941 | 98.6654 | 1005.0083 | 97.985
5.0278 | 1005.5556 | 98.6198 | 1006.2653 | 98.7152 | 1005.0437 | 98.0182
5.0347 | 1005.5486 | 98.6247 | 1006.3218 | 98.7363 | 1005.0666 | 98.0395
5.0417 | 1005.5515 | 98.6182 | 1006.36 | 98.7406 | 1005.0636 | 98.0276
5.0486 | 1005.572 | 98.6045 | 1006.3723 | 98.7288 | 1005.0373 | 97.99
5.0556 | 1005.5988 | 98.5928 | 1006.3514 | 98.7026 | 1005.0381 | 97.9904
5.0625 | 1005.6227 | 98.5858 | 1006.2922 | 98.66 | 1005.0542 | 98.002
5.0694 | 1005.634 | 98.5863 | 1006.2574 | 98.6515 | 1005.0697 | 98.0091
5.0764 | 1005.6208 | 98.5962 | 1006.2808 | 98.6864 | 1005.0872 | 98.0212
5.0833 | 1005.599 | 98.6084 | 1006.3172 | 98.71 | 1005.0873 | 98.0111
5.0903 | 1005.5878 | 98.6133 | 1006.3443 | 98.7179 | 1005.0466 | 97.957
5.0972 | 1005.5931 | 98.6073 | 1006.3635 | 98.7197 | 1005.0357 | 97.9506
5.1042 | 1005.6114 | 98.5965 | 1006.3778 | 98.7193 | 1005.0596 | 97.983
5.1111 | 1005.6293 | 98.5875 | 1006.3669 | 98.7027 | 1005.0901 | 98.0174
5.1181 | 1005.642 | 98.5823 | 1006.2994 | 98.6548 | 1005.1144 | 98.0414
5.125 | 1005.6409 | 98.5843 | 1006.2425 | 98.6344 | 1005.1324 | 98.0576
5.1319 | 1005.6306 | 98.59 | 1006.207 | 98.6263 | 1005.1431 | 98.0658
5.1389 | 1005.609 | 98.5976 | 1006.1798 | 98.618 | 1005.1187 | 98.0272
5.1458 | 1005.5851 | 98.6102 | 1006.2105 | 98.6601 | 1005.0212 | 97.9186
5.1528 | 1005.5691 | 98.6197 | 1006.2498 | 98.6861 | 1004.9533 | 97.8579
5.1597 | 1005.5675 | 98.6204 | 1006.2715 | 98.6888 | 1004.9021 | 97.8096
5.1667 | 1005.5851 | 98.6111 | 1006.2754 | 98.6793 | 1004.8905 | 97.8033
5.1736 | 1005.6101 | 98.6011 | 1006.2803 | 98.6774 | 1004.9431 | 97.8698
5.1806 | 1005.6266 | 98.5948 | 1006.3044 | 98.6955 | 1005.0021 | 97.9322
5.1875 | 1005.6313 | 98.5913 | 1006.3358 | 98.7133 | 1005.0396 | 97.9647
5.1944 | 1005.6255 | 98.5911 | 1006.3644 | 98.7238 | 1005.0689 | 97.9925
5.2014 | 1005.6162 | 98.5899 | 1006.3863 | 98.7274 | 1005.0751 | 97.9901
5.2083 | 1005.6145 | 98.585 | 1006.3883 | 98.7163 | 1005.0047 | 97.9033
5.2153 | 1005.6203 | 98.5802 | 1006.3718 | 98.699 | 1004.9881 | 97.8929
5.2222 | 1005.6239 | 98.5784 | 1006.3709 | 98.7023 | 1005.0193 | 97.9311
5.2292 | 1005.6227 | 98.5771 | 1006.3807 | 98.7102 | 1005.057 | 97.9736
5.2361 | 1005.6195 | 98.5748 | 1006.3842 | 98.7103 | 1005.0859 | 98.006
5.2431 | 1005.6139 | 98.5732 | 1006.3893 | 98.715 | 1005.1052 | 98.0288
5.25 | 1005.6056 | 98.5712 | 1006.3935 | 98.7174 | 1005.1172 | 98.0446
5.2569 | 1005.5983 | 98.5672 | 1006.3903 | 98.714 | 1005.1153 | 98.0422
5.2639 | 1005.5926 | 98.5627 | 1006.3891 | 98.7139 | 1005.0951 | 98.0175
5.2708 | 1005.5876 | 98.558 | 1006.3801 | 98.7052 | 1005.0414 | 97.9546
5.2778 | 1005.5852 | 98.5533 | 1006.3592 | 98.6904 | 1005.0087 | 97.9251
5.2847 | 1005.5851 | 98.55 | 1006.3236 | 98.6683 | 1004.9996 | 97.9202
5.2917 | 1005.5819 | 98.5488 | 1006.2281 | 98.6029 | 1004.9785 | 97.8958
5.2986 | 1005.5737 | 98.5505 | 1006.1248 | 98.5497 | 1004.8614 | 97.7793
5.3056 | 1005.5665 | 98.553 | 1006.0407 | 98.5119 | 1004.7563 | 97.6927
5.3125 | 1005.5556 | 98.5567 | 1005.9854 | 98.4918 | 1004.68 | 97.6284
5.3194 | 1005.54 | 98.5636 | 1005.9752 | 98.5121 | 1004.6239 | 97.5808
5.3264 | 1005.5308 | 98.57 | 1005.9906 | 98.5397 | 1004.6607 | 97.6224
5.3333 | 1005.5281 | 98.5729 | 1006.0267 | 98.5747 | 1004.7604 | 97.7334
5.3403 | 1005.5243 | 98.5744 | 1006.08 | 98.6197 | 1004.8476 | 97.8255
5.3472 | 1005.5165 | 98.574 | 1006.132 | 98.6544 | 1004.9091 | 97.8934
5.3542 | 1005.5062 | 98.5717 | 1006.1658 | 98.668 | 1004.9514 | 97.9432
5.3611 | 1005.4945 | 98.5696 | 1006.195 | 98.6823 | 1004.9797 | 97.9796
5.3681 | 1005.4829 | 98.5654 | 1006.2316 | 98.7022 | 1004.9976 | 98.0059
5.375 | 1005.474 | 98.5582 | 1006.2595 | 98.708 | 1004.9969 | 98.0074
5.3819 | 1005.4686 | 98.5506 | 1006.2671 | 98.6994 | 1004.9307 | 97.9291
5.3889 | 1005.4682 | 98.5438 | 1006.2448 | 98.6772 | 1004.7993 | 97.8048
5.3958 | 1005.4707 | 98.5394 | 1006.1997 | 98.6503 | 1004.6894 | 97.7119
5.4028 | 1005.4708 | 98.5376 | 1006.1473 | 98.6249 | 1004.6093 | 97.642
5.4097 | 1005.4665 | 98.5381 | 1006.0954 | 98.6024 | 1004.5505 | 97.5892
5.4167 | 1005.4545 | 98.5412 | 1006.0476 | 98.583 | 1004.5066 | 97.5493
5.4236 | 1005.4387 | 98.5463 | 1006.022 | 98.5798 | 1004.578 | 97.6291
5.4306 | 1005.4317 | 98.5498 | 1006.0299 | 98.5983 | 1004.6821 | 97.7382
5.4375 | 1005.4287 | 98.5502 | 1006.0568 | 98.626 | 1004.7636 | 97.8245
5.4444 | 1005.422 | 98.549 | 1006.0884 | 98.6506 | 1004.8201 | 97.8876
5.4514 | 1005.4128 | 98.5462 | 1006.1027 | 98.6546 | 1004.8582 | 97.9335
5.4583 | 1005.4024 | 98.5436 | 1006.0401 | 98.6015 | 1004.8831 | 97.9667
5.4653 | 1005.3869 | 98.5458 | 1005.981 | 98.5775 | 1004.8891 | 97.9765
5.4722 | 1005.3748 | 98.5493 | 1005.9404 | 98.5656 | 1004.8855 | 97.9789
5.4792 | 1005.3662 | 98.5519 | 1005.9115 | 98.5596 | 1004.8801 | 97.9815
5.4861 | 1005.337 | 98.5573 | 1005.8866 | 98.5526 | 1004.8497 | 97.9499
5.4931 | 1005.3061 | 98.5711 | 1005.9177 | 98.5973 | 1004.7928 | 97.8948
5.5 | 1005.2883 | 98.5807 | 1005.9565 | 98.6265 | 1004.7375 | 97.8492
5.5069 | 1005.2765 | 98.5838 | 1005.9595 | 98.6176 | 1004.6705 | 97.7925
5.5139 | 1005.266 | 98.5814 | 1005.8847 | 98.5484 | 1004.655 | 97.7961
5.5208 | 1005.2554 | 98.5814 | 1005.8202 | 98.5126 | 1004.6748 | 97.8324
5.5278 | 1005.2706 | 98.5835 | 1005.7813 | 98.497 | 1004.6869 | 97.8528
5.5347 | 1005.2975 | 98.5796 | 1005.7556 | 98.4895 | 1004.6819 | 97.8511
5.5417 | 1005.3204 | 98.5788 | 1005.7738 | 98.5219 | 1004.7034 | 97.8842
5.5486 | 1005.3386 | 98.5812 | 1005.8496 | 98.6005 | 1004.7448 | 97.9356
5.5556 | 1005.3477 | 98.581 | 1005.9233 | 98.6525 | 1004.7832 | 97.9766
5.5625 | 1005.3476 | 98.5787 | 1005.9776 | 98.6797 | 1004.8131 | 98.0052
5.5694 | 1005.3366 | 98.58 | 1006.0252 | 98.6997 | 1004.8309 | 98.0181
5.5764 | 1005.32 | 98.5822 | 1006.0625 | 98.708 | 1004.8384 | 98.021
5.5833 | 1005.3138 | 98.577 | 1006.0896 | 98.7105 | 1004.849 | 98.0341
5.5903 | 1005.3202 | 98.5682 | 1006.116 | 98.7164 | 1004.8601 | 98.048
5.5972 | 1005.3251 | 98.5604 | 1006.1392 | 98.7198 | 1004.8671 | 98.0555
5.6042 | 1005.3286 | 98.5534 | 1006.148 | 98.7137 | 1004.8654 | 98.051
5.6111 | 1005.3336 | 98.5481 | 1006.132 | 98.6958 | 1004.8494 | 98.0273
5.6181 | 1005.3262 | 98.5513 | 1006.0316 | 98.6235 | 1004.7142 | 97.8799
5.625 | 1005.2975 | 98.5591 | 1005.9109 | 98.5582 | 1004.5882 | 97.7682
5.6319 | 1005.2699 | 98.5657 | 1005.8023 | 98.4978 | 1004.4945 | 97.6855
5.6389 | 1005.2418 | 98.5713 | 1005.7096 | 98.4443 | 1004.434 | 97.6329
5.6458 | 1005.2307 | 98.5847 | 1005.7291 | 98.5027 | 1004.5078 | 97.7275
5.6528 | 1005.2594 | 98.5939 | 1005.7879 | 98.56 | 1004.5948 | 97.8182
5.6597 | 1005.2896 | 98.5866 | 1005.7703 | 98.5315 | 1004.6332 | 97.8466
5.6667 | 1005.3068 | 98.5811 | 1005.7224 | 98.4986 | 1004.5434 | 97.748
5.6736 | 1005.3167 | 98.5805 | 1005.7089 | 98.5056 | 1004.4599 | 97.6753
5.6806 | 1005.3251 | 98.5832 | 1005.7414 | 98.5498 | 1004.404 | 97.6216
5.6875 | 1005.33 | 98.5852 | 1005.7891 | 98.5877 | 1004.4864 | 97.7091
5.6944 | 1005.335 | 98.5856 | 1005.8425 | 98.6173 | 1004.5928 | 97.8052
5.7014 | 1005.3396 | 98.5815 | 1005.8126 | 98.5651 | 1004.6745 | 97.8768
5.7083 | 1005.3422 | 98.5811 | 1005.7841 | 98.5439 | 1004.7139 | 97.8995
5.7153 | 1005.3454 | 98.5827 | 1005.7621 | 98.5257 | 1004.6756 | 97.84
5.7222 | 1005.3488 | 98.5839 | 1005.729 | 98.4971 | 1004.5928 | 97.7548
5.7292 | 1005.3526 | 98.5891 | 1005.7523 | 98.5329 | 1004.5133 | 97.6814
5.7361 | 1005.356 | 98.5947 | 1005.7967 | 98.5736 | 1004.4556 | 97.6274
5.7431 | 1005.3548 | 98.5982 | 1005.8252 | 98.5896 | 1004.416 | 97.5879
5.75 | 1005.3486 | 98.6009 | 1005.8375 | 98.5908 | 1004.3888 | 97.5593
5.7569 | 1005.3464 | 98.6028 | 1005.8434 | 98.5826 | 1004.4745 | 97.6463
5.7639 | 1005.3511 | 98.6 | 1005.7914 | 98.515 | 1004.5937 | 97.7639
5.7708 | 1005.3604 | 98.5998 | 1005.7615 | 98.4957 | 1004.6863 | 97.8518
5.7778 | 1005.3725 | 98.6033 | 1005.7829 | 98.5227 | 1004.704 | 97.8486
5.7847 | 1005.3859 | 98.6093 | 1005.8488 | 98.592 | 1004.6163 | 97.7549
5.7917 | 1005.3977 | 98.6109 | 1005.8949 | 98.6257 | 1004.5376 | 97.6862
5.7986 | 1005.4082 | 98.6085 | 1005.9198 | 98.6341 | 1004.5327 | 97.6788
5.8056 | 1005.4189 | 98.6051 | 1005.9346 | 98.6292 | 1004.5992 | 97.7385
5.8125 | 1005.4293 | 98.6032 | 1005.9556 | 98.6336 | 1004.6713 | 97.7975
5.8194 | 1005.4383 | 98.6026 | 1005.9809 | 98.6435 | 1004.6945 | 97.8
5.8264 | 1005.4432 | 98.6015 | 1005.9609 | 98.611 | 1004.6227 | 97.7203
5.8333 | 1005.4447 | 98.5992 | 1005.8713 | 98.5288 | 1004.5561 | 97.661
5.8403 | 1005.4434 | 98.5989 | 1005.7837 | 98.4647 | 1004.51 | 97.6169
5.8472 | 1005.4396 | 98.6002 | 1005.7146 | 98.4131 | 1004.4782 | 97.5839
5.8542 | 1005.4384 | 98.6057 | 1005.7143 | 98.4259 | 1004.5499 | 97.6532
5.8611 | 1005.4466 | 98.6144 | 1005.7754 | 98.4837 | 1004.6669 | 97.7693
5.8681 | 1005.4557 | 98.62 | 1005.8177 | 98.5081 | 1004.7644 | 97.863
5.875 | 1005.4493 | 98.624 | 1005.83 | 98.5133 | 1004.8287 | 97.9218
5.8819 | 1005.4187 | 98.6296 | 1005.8347 | 98.5185 | 1004.8137 | 97.8871
5.8889 | 1005.3886 | 98.6396 | 1005.8192 | 98.5057 | 1004.7119 | 97.788
5.8958 | 1005.3859 | 98.6482 | 1005.7833 | 98.4776 | 1004.6217 | 97.7162
5.9028 | 1005.4061 | 98.6493 | 1005.7601 | 98.4616 | 1004.6763 | 97.7912
5.9097 | 1005.4312 | 98.6547 | 1005.8556 | 98.5715 | 1004.7651 | 97.8838
5.9167 | 1005.4409 | 98.6624 | 1005.9737 | 98.6668 | 1004.8309 | 97.9463
5.9236 | 1005.4356 | 98.6702 | 1006.0648 | 98.7211 | 1004.8523 | 97.9552
5.9306 | 1005.4386 | 98.6711 | 1006.1166 | 98.7339 | 1004.8507 | 97.9462
5.9375 | 1005.4549 | 98.6625 | 1006.0706 | 98.6714 | 1004.8853 | 97.9907
5.9444 | 1005.4617 | 98.66 | 1006.0298 | 98.6471 | 1004.9285 | 98.0381
5.9514 | 1005.4665 | 98.6634 | 1006.0125 | 98.6426 | 1004.9625 | 98.0727
5.9583 | 1005.4881 | 98.665 | 1006.0275 | 98.6645 | 1004.9884 | 98.0982
5.9653 | 1005.5135 | 98.6637 | 1006.0749 | 98.7056 | 1004.9851 | 98.0802
5.9722 | 1005.5288 | 98.6617 | 1006.0962 | 98.7083 | 1004.9424 | 98.0179
5.9792 | 1005.518 | 98.6647 | 1006.0861 | 98.688 | 1004.9144 | 97.98
5.9861 | 1005.4985 | 98.6729 | 1006.0711 | 98.67 | 1004.9213 | 97.9831
5.9931 | 1005.4915 | 98.6831 | 1006.1114 | 98.7081 | 1004.9462 | 98.0078
6 | 1005.5137 | 98.6851 | 1006.1794 | 98.7549 | 1004.9794 | 98.0452
6.0069 | 1005.5413 | 98.6755 | 1006.2425 | 98.7849 | 1005.0135 | 98.0819
6.0139 | 1005.5574 | 98.6661 | 1006.2947 | 98.8011 | 1005.0423 | 98.1086
6.0208 | 1005.5676 | 98.6579 | 1006.3289 | 98.8027 | 1005.0659 | 98.1273
6.0278 | 1005.5807 | 98.6502 | 1006.2886 | 98.7566 | 1005.0843 | 98.1387
6.0347 | 1005.5936 | 98.6471 | 1006.2297 | 98.7222 | 1005.0825 | 98.1211
6.0417 | 1005.6015 | 98.6475 | 1006.1749 | 98.6917 | 1005.0188 | 98.0323
6.0486 | 1005.6052 | 98.649 | 1006.1109 | 98.65 | 1004.8972 | 97.9055
6.0556 | 1005.6005 | 98.6517 | 1006.0384 | 98.6001 | 1004.7982 | 97.8115
6.0625 | 1005.5753 | 98.6557 | 1005.9686 | 98.5497 | 1004.7281 | 97.7416
6.0694 | 1005.5351 | 98.6613 | 1005.9062 | 98.5025 | 1004.6767 | 97.6899
6.0764 | 1005.4982 | 98.6685 | 1005.8524 | 98.4604 | 1004.6369 | 97.652
6.0833 | 1005.469 | 98.6742 | 1005.8068 | 98.424 | 1004.6048 | 97.6247
6.0903 | 1005.4455 | 98.6787 | 1005.7688 | 98.3935 | 1004.5781 | 97.6055
6.0972 | 1005.4265 | 98.6826 | 1005.7374 | 98.3685 | 1004.5558 | 97.5921
6.1042 | 1005.42 | 98.6927 | 1005.7788 | 98.4215 | 1004.6154 | 97.6584
6.1111 | 1005.4709 | 98.7169 | 1005.8619 | 98.4978 | 1004.7056 | 97.7493
6.1181 | 1005.536 | 98.7182 | 1005.9209 | 98.5377 | 1004.774 | 97.8119
6.125 | 1005.5834 | 98.7121 | 1005.9181 | 98.521 | 1004.7938 | 97.8194
6.1319 | 1005.6127 | 98.7088 | 1005.9107 | 98.5145 | 1004.8253 | 97.8446
6.1389 | 1005.623 | 98.7094 | 1005.9227 | 98.5235 | 1004.9023 | 97.9223
6.1458 | 1005.6276 | 98.7155 | 1005.9525 | 98.5471 | 1004.9772 | 97.9889
6.1528 | 1005.6498 | 98.7231 | 1005.987 | 98.5727 | 1005.013 | 98.0053
6.1597 | 1005.6774 | 98.7248 | 1006.0115 | 98.5864 | 1004.9943 | 97.9642
6.1667 | 1005.7002 | 98.7249 | 1006.0125 | 98.5793 | 1004.9085 | 97.8702
6.1736 | 1005.7167 | 98.7246 | 1005.9931 | 98.5559 | 1004.8392 | 97.8013
6.1806 | 1005.7281 | 98.7248 | 1005.9676 | 98.5265 | 1004.7956 | 97.7507
6.1875 | 1005.736 | 98.7257 | 1005.9428 | 98.4963 | 1004.7695 | 97.7137
6.1944 | 1005.7366 | 98.727 | 1005.9219 | 98.468 | 1004.7551 | 97.6864
6.2014 | 1005.7382 | 98.731 | 1005.919 | 98.4535 | 1004.8302 | 97.7456
6.2083 | 1005.7494 | 98.7369 | 1005.9471 | 98.4647 | 1004.9532 | 97.8553
6.2153 | 1005.7691 | 98.7437 | 1005.9976 | 98.4975 | 1005.0634 | 97.953
6.2222 | 1005.7937 | 98.7504 | 1006.0574 | 98.5413 | 1005.1505 | 98.0312
6.2292 | 1005.8202 | 98.7563 | 1006.118 | 98.5875 | 1005.217 | 98.0894
6.2361 | 1005.85 | 98.7636 | 1006.222 | 98.68 | 1005.268 | 98.1312
6.2431 | 1005.8794 | 98.7685 | 1006.3464 | 98.7776 | 1005.3025 | 98.1518
6.25 | 1005.8987 | 98.7677 | 1006.4569 | 98.8444 | 1005.3198 | 98.1506
6.2569 | 1005.9093 | 98.7619 | 1006.5305 | 98.8654 | 1005.2973 | 98.1013
6.2639 | 1005.9201 | 98.7549 | 1006.5734 | 98.8637 | 1005.2866 | 98.075
6.2708 | 1005.9321 | 98.7494 | 1006.6106 | 98.8661 | 1005.3132 | 98.0931
6.2778 | 1005.9438 | 98.7443 | 1006.6482 | 98.8722 | 1005.3535 | 98.1246
6.2847 | 1005.955 | 98.7394 | 1006.6802 | 98.876 | 1005.3921 | 98.1551
6.2917 | 1005.9645 | 98.7349 | 1006.7032 | 98.8763 | 1005.4225 | 98.1767
6.2986 | 1005.9733 | 98.7308 | 1006.7105 | 98.868 | 1005.4247 | 98.1611
6.3056 | 1005.9848 | 98.7266 | 1006.6694 | 98.8271 | 1005.3358 | 98.05
6.3125 | 1005.9924 | 98.7262 | 1006.5853 | 98.7674 | 1005.2244 | 97.9397
6.3194 | 1005.9895 | 98.7313 | 1006.5394 | 98.7552 | 1005.1391 | 97.8575
6.3264 | 1005.989 | 98.7364 | 1006.5234 | 98.758 | 1005.0788 | 97.7963
6.3333 | 1005.9927 | 98.7385 | 1006.5301 | 98.7714 | 1005.1263 | 97.8403
6.3403 | 1005.996 | 98.7394 | 1006.5601 | 98.7941 | 1005.2331 | 97.9487
6.3472 | 1005.9892 | 98.7422 | 1006.6036 | 98.8223 | 1005.3199 | 98.0292
6.3542 | 1005.967 | 98.749 | 1006.6483 | 98.8458 | 1005.3805 | 98.0881
6.3611 | 1005.9428 | 98.7555 | 1006.6817 | 98.8562 | 1005.421 | 98.1316
6.3681 | 1005.9257 | 98.7554 | 1006.6239 | 98.7982 | 1005.4466 | 98.164
6.375 | 1005.9119 | 98.7573 | 1006.5671 | 98.7736 | 1005.4585 | 98.1832
6.3819 | 1005.9113 | 98.7596 | 1006.5288 | 98.7621 | 1005.4528 | 98.1812
6.3889 | 1005.9214 | 98.7607 | 1006.5517 | 98.8026 | 1005.3698 | 98.0882
6.3958 | 1005.9299 | 98.7588 | 1006.5822 | 98.8288 | 1005.2427 | 97.972
6.4028 | 1005.9385 | 98.7525 | 1006.5839 | 98.8229 | 1005.1425 | 97.8864
6.4097 | 1005.9515 | 98.7446 | 1006.5533 | 98.792 | 1005.0729 | 97.8228
6.4167 | 1005.9664 | 98.7384 | 1006.5126 | 98.7584 | 1005.0961 | 97.842
6.4236 | 1005.9787 | 98.7356 | 1006.4805 | 98.7327 | 1005.1881 | 97.931
6.4306 | 1005.9857 | 98.7346 | 1006.4316 | 98.6923 | 1005.2793 | 98.0161
6.4375 | 1005.9856 | 98.7375 | 1006.4049 | 98.6839 | 1005.3463 | 98.076
6.4444 | 1005.978 | 98.7447 | 1006.424 | 98.7131 | 1005.3799 | 98.098
6.4514 | 1005.9504 | 98.7542 | 1006.4542 | 98.7401 | 1005.3316 | 98.0295
6.4583 | 1005.9259 | 98.7679 | 1006.4845 | 98.7676 | 1005.2234 | 97.9264
6.4653 | 1005.9298 | 98.7729 | 1006.5024 | 98.7811 | 1005.1326 | 97.8516
6.4722 | 1005.9456 | 98.7677 | 1006.4967 | 98.7703 | 1005.0682 | 97.7975
6.4792 | 1005.9582 | 98.762 | 1006.4645 | 98.7379 | 1005.0238 | 97.758
6.4861 | 1005.9567 | 98.7561 | 1006.3646 | 98.6435 | 1004.9937 | 97.7289
6.4931 | 1005.9211 | 98.7533 | 1006.2865 | 98.5872 | 1005.0684 | 97.8034
6.5 | 1005.8827 | 98.7611 | 1006.2587 | 98.5699 | 1005.1674 | 97.8967
6.5069 | 1005.8667 | 98.7771 | 1006.3206 | 98.643 | 1005.2486 | 97.9794
6.5139 | 1005.8996 | 98.7975 | 1006.4319 | 98.7511 | 1005.3044 | 98.0402
6.5208 | 1005.9394 | 98.797 | 1006.5294 | 98.8241 | 1005.3325 | 98.0685
6.5278 | 1005.9659 | 98.7892 | 1006.5904 | 98.8532 | 1005.3034 | 98.0286
6.5347 | 1005.9853 | 98.7801 | 1006.6037 | 98.8432 | 1005.2079 | 97.9348
6.5417 | 1006.0011 | 98.7732 | 1006.5869 | 98.821 | 1005.1301 | 97.8653
6.5486 | 1006.0122 | 98.7696 | 1006.5606 | 98.798 | 1005.0788 | 97.8134
6.5556 | 1006.0062 | 98.7712 | 1006.5373 | 98.7766 | 1005.1427 | 97.8726
6.5625 | 1005.9807 | 98.7746 | 1006.4723 | 98.7105 | 1005.2409 | 97.96
6.5694 | 1005.9775 | 98.7827 | 1006.4264 | 98.6809 | 1005.2841 | 97.9817
6.5764 | 1006.0018 | 98.7854 | 1006.4259 | 98.6945 | 1005.2101 | 97.8993
6.5833 | 1006.0274 | 98.7872 | 1006.4638 | 98.7443 | 1005.1397 | 97.8388
6.5903 | 1006.0458 | 98.7874 | 1006.4976 | 98.7735 | 1005.0931 | 97.7944
6.5972 | 1006.0517 | 98.7872 | 1006.514 | 98.781 | 1005.0638 | 97.7618
6.6042 | 1006.0293 | 98.79 | 1006.5116 | 98.769 | 1005.0454 | 97.7378
6.6111 | 1006.0024 | 98.7986 | 1006.5086 | 98.7629 | 1005.0323 | 97.7205
6.6181 | 1005.9996 | 98.8052 | 1006.5095 | 98.762 | 1005.0218 | 97.7085
6.625 | 1006.0223 | 98.8036 | 1006.5094 | 98.7597 | 1005.0144 | 97.7005
6.6319 | 1006.0501 | 98.798 | 1006.5085 | 98.7571 | 1005.0111 | 97.6953
6.6389 | 1006.0698 | 98.7942 | 1006.5057 | 98.752 | 1005.0119 | 97.6916
6.6458 | 1006.0761 | 98.7935 | 1006.4987 | 98.7415 | 1005.0157 | 97.6887
6.6528 | 1006.0527 | 98.7958 | 1006.4888 | 98.725 | 1005.0621 | 97.7231
6.6597 | 1006.0263 | 98.8052 | 1006.4898 | 98.7166 | 1005.1827 | 97.8415
6.6667 | 1006.0142 | 98.8117 | 1006.457 | 98.6724 | 1005.3037 | 97.9617
6.6736 | 1006.0297 | 98.8185 | 1006.4449 | 98.6688 | 1005.3952 | 98.0561
6.6806 | 1006.0595 | 98.8201 | 1006.4561 | 98.6859 | 1005.4613 | 98.1261
6.6875 | 1006.0873 | 98.821 | 1006.4784 | 98.7117 | 1005.5107 | 98.1779
6.6944 | 1006.1099 | 98.8218 | 1006.5019 | 98.7356 | 1005.5299 | 98.1865
6.7014 | 1006.1297 | 98.8252 | 1006.5758 | 98.8129 | 1005.4194 | 98.0602
6.7083 | 1006.1437 | 98.8251 | 1006.6397 | 98.8598 | 1005.3209 | 97.9677
6.7153 | 1006.1529 | 98.8211 | 1006.6699 | 98.8661 | 1005.2556 | 97.8996
6.7222 | 1006.1597 | 98.8176 | 1006.6947 | 98.8692 | 1005.3158 | 97.9537
6.7292 | 1006.1617 | 98.8173 | 1006.7316 | 98.8801 | 1005.4204 | 98.0476
6.7361 | 1006.1514 | 98.8212 | 1006.7586 | 98.881 | 1005.5074 | 98.1234
6.7431 | 1006.1461 | 98.8254 | 1006.7736 | 98.8798 | 1005.5692 | 98.1787
6.75 | 1006.1475 | 98.8289 | 1006.8251 | 98.9203 | 1005.6125 | 98.2192
6.7569 | 1006.1388 | 98.8337 | 1006.883 | 98.9482 | 1005.6427 | 98.2491
6.7639 | 1006.129 | 98.835 | 1006.9257 | 98.957 | 1005.6479 | 98.2482
6.7708 | 1006.1349 | 98.8253 | 1006.9391 | 98.9451 | 1005.5795 | 98.1638
6.7778 | 1006.161 | 98.8121 | 1006.8985 | 98.9034 | 1005.458 | 98.0466
6.7847 | 1006.1891 | 98.8016 | 1006.7726 | 98.8086 | 1005.3611 | 97.9591
6.7917 | 1006.2027 | 98.798 | 1006.6503 | 98.7363 | 1005.2945 | 97.8929
6.7986 | 1006.1948 | 98.7996 | 1006.5573 | 98.6799 | 1005.274 | 97.864
6.8056 | 1006.1642 | 98.8038 | 1006.487 | 98.634 | 1005.24 | 97.8203
6.8125 | 1006.1427 | 98.8132 | 1006.4297 | 98.5941 | 1005.2091 | 97.7876
6.8194 | 1006.1433 | 98.8192 | 1006.3838 | 98.5601 | 1005.1857 | 97.7637
6.8264 | 1006.1484 | 98.8207 | 1006.3474 | 98.5318 | 1005.1688 | 97.7465
6.8333 | 1006.1484 | 98.8224 | 1006.3329 | 98.5199 | 1005.2433 | 97.8187
6.8403 | 1006.1304 | 98.8239 | 1006.3467 | 98.529 | 1005.3279 | 97.8893
6.8472 | 1006.092 | 98.8259 | 1006.3589 | 98.5366 | 1005.2897 | 97.8412
6.8542 | 1006.071 | 98.8401 | 1006.3592 | 98.5366 | 1005.2763 | 97.8382
6.8611 | 1006.0985 | 98.8569 | 1006.3746 | 98.5508 | 1005.3649 | 97.946
6.8681 | 1006.1452 | 98.8644 | 1006.4728 | 98.6552 | 1005.4644 | 98.0533
6.875 | 1006.1936 | 98.8711 | 1006.6078 | 98.7827 | 1005.542 | 98.1337
6.8819 | 1006.2309 | 98.8724 | 1006.7299 | 98.8811 | 1005.603 | 98.1942
6.8889 | 1006.2513 | 98.8684 | 1006.828 | 98.9423 | 1005.6349 | 98.2123
6.8958 | 1006.2605 | 98.8608 | 1006.8894 | 98.9601 | 1005.5872 | 98.1386
6.9028 | 1006.2597 | 98.8588 | 1006.921 | 98.9563 | 1005.589 | 98.1353
6.9097 | 1006.247 | 98.8624 | 1006.9383 | 98.9476 | 1005.6359 | 98.1799
6.9167 | 1006.2368 | 98.8678 | 1006.9557 | 98.9489 | 1005.6828 | 98.2234
6.9236 | 1006.2333 | 98.8726 | 1006.9841 | 98.9637 | 1005.7143 | 98.2519
6.9306 | 1006.2323 | 98.8757 | 1007.0211 | 98.9816 | 1005.7232 | 98.2552
6.9375 | 1006.233 | 98.876 | 1007.0465 | 98.984 | 1005.7055 | 98.2294
6.9444 | 1006.2364 | 98.8748 | 1007.0618 | 98.9826 | 1005.7072 | 98.236
6.9514 | 1006.241 | 98.8736 | 1007.0732 | 98.983 | 1005.7321 | 98.2708
6.9583 | 1006.2455 | 98.8722 | 1007.0697 | 98.9755 | 1005.7559 | 98.2996
6.9653 | 1006.2531 | 98.8689 | 1007.0754 | 98.9836 | 1005.7735 | 98.3204
6.9722 | 1006.2655 | 98.8591 | 1007.0961 | 98.9979 | 1005.7873 | 98.3351
6.9792 | 1006.2801 | 98.8469 | 1007.1095 | 98.997 | 1005.7626 | 98.2927
6.9861 | 1006.2947 | 98.8363 | 1007.0953 | 98.9781 | 1005.6328 | 98.1509
6.9931 | 1006.3117 | 98.8283 | 1007.0429 | 98.9412 | 1005.5209 | 98.0446
7 | 1006.3281 | 98.822 | 1006.9021 | 98.8371 | 1005.4432 | 97.9643

## TSS
TSS
Time | Total suspended solids (TSS) (CSTR2)
d | g TSS/m3
0 | 1891.7683
0.0069444 | 1891.7476
0.013889 | 1891.6422
0.020833 | 1891.5457
0.027778 | 1891.4789
0.034722 | 1891.4353
0.041667 | 1891.41
0.048611 | 1891.3992
0.055556 | 1891.4001
0.0625 | 1891.4265
0.069444 | 1891.5116
0.076389 | 1891.6102
0.083333 | 1891.7011
0.090278 | 1891.7661
0.097222 | 1891.803
0.10417 | 1891.8369
0.11111 | 1891.8789
0.11806 | 1891.8832
0.125 | 1891.8574
0.13194 | 1891.8356
0.13889 | 1891.8713
0.14583 | 1891.9652
0.15278 | 1892.0687
0.15972 | 1892.1542
0.16667 | 1892.2238
0.17361 | 1892.2817
0.18056 | 1892.3128
0.1875 | 1892.2473
0.19444 | 1892.1837
0.20139 | 1892.1434
0.20833 | 1892.12
0.21528 | 1892.1771
0.22222 | 1892.2726
0.22917 | 1892.3618
0.23611 | 1892.4385
0.24306 | 1892.501
0.25 | 1892.5431
0.25694 | 1892.5598
0.26389 | 1892.57
0.27083 | 1892.6044
0.27778 | 1892.6471
0.28472 | 1892.6834
0.29167 | 1892.7136
0.29861 | 1892.7278
0.30556 | 1892.6714
0.3125 | 1892.6349
0.31944 | 1892.6433
0.32639 | 1892.655
0.33333 | 1892.6212
0.34028 | 1892.5556
0.34722 | 1892.4999
0.35417 | 1892.4636
0.36111 | 1892.4427
0.36806 | 1892.4339
0.375 | 1892.4345
0.38194 | 1892.4425
0.38889 | 1892.456
0.39583 | 1892.473
0.40278 | 1892.5149
0.40972 | 1892.584
0.41667 | 1892.6388
0.42361 | 1892.7023
0.43056 | 1892.7507
0.4375 | 1892.7413
0.44444 | 1892.7243
0.45139 | 1892.716
0.45833 | 1892.7286
0.46528 | 1892.8271
0.47222 | 1892.9481
0.47917 | 1893.0489
0.48611 | 1893.131
0.49306 | 1893.178
0.5 | 1893.1691
0.50694 | 1893.109
0.51389 | 1893.0525
0.52083 | 1893.0641
0.52778 | 1893.1208
0.53472 | 1893.1749
0.54167 | 1893.2463
0.54861 | 1893.318
0.55556 | 1893.3783
0.5625 | 1893.4295
0.56944 | 1893.4742
0.57639 | 1893.499
0.58333 | 1893.4941
0.59028 | 1893.4858
0.59722 | 1893.5105
0.60417 | 1893.5511
0.61111 | 1893.5841
0.61806 | 1893.6076
0.625 | 1893.612
0.63194 | 1893.6029
0.63889 | 1893.5952
0.64583 | 1893.593
0.65278 | 1893.5792
0.65972 | 1893.5636
0.66667 | 1893.5629
0.67361 | 1893.5638
0.68056 | 1893.5547
0.6875 | 1893.5028
0.69444 | 1893.4383
0.70139 | 1893.4283
0.70833 | 1893.4924
0.71528 | 1893.572
0.72222 | 1893.6343
0.72917 | 1893.6719
0.73611 | 1893.6773
0.74306 | 1893.6894
0.75 | 1893.7169
0.75694 | 1893.739
0.76389 | 1893.7492
0.77083 | 1893.735
0.77778 | 1893.7009
0.78472 | 1893.6635
0.79167 | 1893.6635
0.79861 | 1893.6912
0.80556 | 1893.7286
0.8125 | 1893.7634
0.81944 | 1893.7901
0.82639 | 1893.8
0.83333 | 1893.709
0.84028 | 1893.6224
0.84722 | 1893.5617
0.85417 | 1893.5194
0.86111 | 1893.4903
0.86806 | 1893.5605
0.875 | 1893.6634
0.88194 | 1893.7464
0.88889 | 1893.7665
0.89583 | 1893.7221
0.90278 | 1893.735
0.90972 | 1893.7974
0.91667 | 1893.87
0.92361 | 1893.9283
0.93056 | 1893.9397
0.9375 | 1893.9026
0.94444 | 1893.9093
0.95139 | 1893.9699
0.95833 | 1894.0371
0.96528 | 1894.0891
0.97222 | 1894.1275
0.97917 | 1894.1151
0.98611 | 1894.032
0.99306 | 1893.9552
1 | 1893.9012
1.0069 | 1893.8637
1.0139 | 1893.8381
1.0208 | 1893.8209
1.0278 | 1893.8227
1.0347 | 1893.819
1.0417 | 1893.8161
1.0486 | 1893.8203
1.0556 | 1893.8679
1.0625 | 1893.9587
1.0694 | 1894.0333
1.0764 | 1894.0285
1.0833 | 1894.0134
1.0903 | 1894.0931
1.0972 | 1894.2075
1.1042 | 1894.3015
1.1111 | 1894.3772
1.1181 | 1894.431
1.125 | 1894.4642
1.1319 | 1894.4864
1.1389 | 1894.4772
1.1458 | 1894.3993
1.1528 | 1894.3223
1.1597 | 1894.2637
1.1667 | 1894.22
1.1736 | 1894.2544
1.1806 | 1894.3387
1.1875 | 1894.4192
1.1944 | 1894.4796
1.2014 | 1894.5248
1.2083 | 1894.5652
1.2153 | 1894.6024
1.2222 | 1894.6339
1.2292 | 1894.6378
1.2361 | 1894.564
1.2431 | 1894.4897
1.25 | 1894.4326
1.2569 | 1894.4109
1.2639 | 1894.4261
1.2708 | 1894.3959
1.2778 | 1894.36
1.2847 | 1894.3344
1.2917 | 1894.3172
1.2986 | 1894.3802
1.3056 | 1894.4838
1.3125 | 1894.569
1.3194 | 1894.6176
1.3264 | 1894.6177
1.3333 | 1894.5979
1.3403 | 1894.6535
1.3472 | 1894.7332
1.3542 | 1894.7979
1.3611 | 1894.8418
1.3681 | 1894.7926
1.375 | 1894.7251
1.3819 | 1894.7616
1.3889 | 1894.837
1.3958 | 1894.8981
1.4028 | 1894.9454
1.4097 | 1894.9826
1.4167 | 1895.0051
1.4236 | 1895.0068
1.4306 | 1894.9912
1.4375 | 1895.0092
1.4444 | 1895.0476
1.4514 | 1895.0776
1.4583 | 1895.097
1.4653 | 1895.1084
1.4722 | 1895.0898
1.4792 | 1894.9876
1.4861 | 1894.8925
1.4931 | 1894.8251
1.5 | 1894.78
1.5069 | 1894.831
1.5139 | 1894.9156
1.5208 | 1894.9713
1.5278 | 1894.932
1.5347 | 1894.8863
1.5417 | 1894.8556
1.5486 | 1894.8351
1.5556 | 1894.8963
1.5625 | 1894.9935
1.5694 | 1895.0773
1.5764 | 1895.1418
1.5833 | 1895.1935
1.5903 | 1895.2374
1.5972 | 1895.2761
1.6042 | 1895.3099
1.6111 | 1895.3263
1.6181 | 1895.3265
1.625 | 1895.3206
1.6319 | 1895.2757
1.6389 | 1895.1935
1.6458 | 1895.1191
1.6528 | 1895.0949
1.6597 | 1895.1255
1.6667 | 1895.1937
1.6736 | 1895.2565
1.6806 | 1895.2922
1.6875 | 1895.3151
1.6944 | 1895.3342
1.7014 | 1895.3219
1.7083 | 1895.2536
1.7153 | 1895.2253
1.7222 | 1895.2364
1.7292 | 1895.2699
1.7361 | 1895.3218
1.7431 | 1895.3638
1.75 | 1895.3896
1.7569 | 1895.4169
1.7639 | 1895.4374
1.7708 | 1895.4514
1.7778 | 1895.4615
1.7847 | 1895.4647
1.7917 | 1895.4434
1.7986 | 1895.4222
1.8056 | 1895.431
1.8125 | 1895.4587
1.8194 | 1895.4836
1.8264 | 1895.5038
1.8333 | 1895.5199
1.8403 | 1895.5334
1.8472 | 1895.5357
1.8542 | 1895.5161
1.8611 | 1895.4701
1.8681 | 1895.402
1.875 | 1895.3168
1.8819 | 1895.2425
1.8889 | 1895.2048
1.8958 | 1895.2561
1.9028 | 1895.3409
1.9097 | 1895.4131
1.9167 | 1895.459
1.9236 | 1895.4419
1.9306 | 1895.3744
1.9375 | 1895.3779
1.9444 | 1895.4435
1.9514 | 1895.4979
1.9583 | 1895.5365
1.9653 | 1895.5551
1.9722 | 1895.5197
1.9792 | 1895.4688
1.9861 | 1895.4662
1.9931 | 1895.4948
2 | 1895.5173
2.0069 | 1895.5332
2.0139 | 1895.5458
2.0208 | 1895.5575
2.0278 | 1895.568
2.0347 | 1895.5655
2.0417 | 1895.5163
2.0486 | 1895.4253
2.0556 | 1895.346
2.0625 | 1895.2905
2.0694 | 1895.2534
2.0764 | 1895.2943
2.0833 | 1895.3906
2.0903 | 1895.4772
2.0972 | 1895.5451
2.1042 | 1895.5989
2.1111 | 1895.62
2.1181 | 1895.5467
2.125 | 1895.4742
2.1319 | 1895.4222
2.1389 | 1895.3843
2.1458 | 1895.4058
2.1528 | 1895.4981
2.1597 | 1895.5834
2.1667 | 1895.6439
2.1736 | 1895.6185
2.1806 | 1895.5554
2.1875 | 1895.5007
2.1944 | 1895.4629
2.2014 | 1895.4735
2.2083 | 1895.518
2.2153 | 1895.5649
2.2222 | 1895.6214
2.2292 | 1895.6756
2.2361 | 1895.6771
2.2431 | 1895.6225
2.25 | 1895.5685
2.2569 | 1895.5293
2.2639 | 1895.5013
2.2708 | 1895.5323
2.2778 | 1895.5925
2.2847 | 1895.6527
2.2917 | 1895.7116
2.2986 | 1895.7338
2.3056 | 1895.73
2.3125 | 1895.7592
2.3194 | 1895.783
2.3264 | 1895.7438
2.3333 | 1895.7223
2.3403 | 1895.7724
2.3472 | 1895.8551
2.3542 | 1895.938
2.3611 | 1896.003
2.3681 | 1896.0521
2.375 | 1896.0896
2.3819 | 1896.1187
2.3889 | 1896.1423
2.3958 | 1896.1401
2.4028 | 1896.1403
2.4097 | 1896.1586
2.4167 | 1896.1759
2.4236 | 1896.1786
2.4306 | 1896.1705
2.4375 | 1896.1513
2.4444 | 1896.12
2.4514 | 1896.0844
2.4583 | 1896.0149
2.4653 | 1895.9581
2.4722 | 1895.9723
2.4792 | 1896.0243
2.4861 | 1896.0761
2.4931 | 1896.1169
2.5 | 1896.1419
2.5069 | 1896.1395
2.5139 | 1896.1189
2.5208 | 1896.1182
2.5278 | 1896.1462
2.5347 | 1896.1706
2.5417 | 1896.1884
2.5486 | 1896.2021
2.5556 | 1896.2121
2.5625 | 1896.1715
2.5694 | 1896.078
2.5764 | 1895.9949
2.5833 | 1895.9351
2.5903 | 1895.8926
2.5972 | 1895.8622
2.6042 | 1895.8396
2.6111 | 1895.9058
2.6181 | 1896.0016
2.625 | 1896.0845
2.6319 | 1896.1335
2.6389 | 1896.1353
2.6458 | 1896.1512
2.6528 | 1896.1889
2.6597 | 1896.2175
2.6667 | 1896.1999
2.6736 | 1896.1279
2.6806 | 1896.0605
2.6875 | 1896.0254
2.6944 | 1896.0098
2.7014 | 1895.9839
2.7083 | 1895.9612
2.7153 | 1895.9549
2.7222 | 1895.9488
2.7292 | 1895.9443
2.7361 | 1895.9467
2.7431 | 1896.0009
2.75 | 1896.1082
2.7569 | 1896.2167
2.7639 | 1896.2972
2.7708 | 1896.3681
2.7778 | 1896.4314
2.7847 | 1896.4838
2.7917 | 1896.5177
2.7986 | 1896.5303
2.8056 | 1896.5337
2.8125 | 1896.5454
2.8194 | 1896.5527
2.8264 | 1896.5
2.8333 | 1896.4079
2.8403 | 1896.3238
2.8472 | 1896.2578
2.8542 | 1896.2065
2.8611 | 1896.2623
2.8681 | 1896.3479
2.875 | 1896.4167
2.8819 | 1896.4711
2.8889 | 1896.508
2.8958 | 1896.5393
2.9028 | 1896.5704
2.9097 | 1896.5943
2.9167 | 1896.5743
2.9236 | 1896.484
2.9306 | 1896.3979
2.9375 | 1896.3315
2.9444 | 1896.2794
2.9514 | 1896.2392
2.9583 | 1896.2102
2.9653 | 1896.1915
2.9722 | 1896.2103
2.9792 | 1896.3029
2.9861 | 1896.4001
2.9931 | 1896.4591
3 | 1896.4852
3.0069 | 1896.5047
3.0139 | 1896.539
3.0208 | 1896.5796
3.0278 | 1896.6067
3.0347 | 1896.6108
3.0417 | 1896.584
3.0486 | 1896.5177
3.0556 | 1896.4286
3.0625 | 1896.3516
3.0694 | 1896.2947
3.0764 | 1896.2539
3.0833 | 1896.2762
3.0903 | 1896.3738
3.0972 | 1896.4578
3.1042 | 1896.5209
3.1111 | 1896.5662
3.1181 | 1896.4897
3.125 | 1896.4094
3.1319 | 1896.3501
3.1389 | 1896.4042
3.1458 | 1896.4872
3.1528 | 1896.5542
3.1597 | 1896.6063
3.1667 | 1896.6462
3.1736 | 1896.6754
3.1806 | 1896.6448
3.1875 | 1896.5543
3.1944 | 1896.4731
3.2014 | 1896.416
3.2083 | 1896.3765
3.2153 | 1896.3523
3.2222 | 1896.381
3.2292 | 1896.4478
3.2361 | 1896.5267
3.2431 | 1896.5861
3.25 | 1896.6075
3.2569 | 1896.6167
3.2639 | 1896.6237
3.2708 | 1896.6285
3.2778 | 1896.6454
3.2847 | 1896.6659
3.2917 | 1896.665
3.2986 | 1896.6701
3.3056 | 1896.6897
3.3125 | 1896.6923
3.3194 | 1896.6613
3.3264 | 1896.6166
3.3333 | 1896.5677
3.3403 | 1896.5589
3.3472 | 1896.602
3.3542 | 1896.6506
3.3611 | 1896.6883
3.3681 | 1896.6973
3.375 | 1896.6322
3.3819 | 1896.5458
3.3889 | 1896.4745
3.3958 | 1896.4232
3.4028 | 1896.4452
3.4097 | 1896.5248
3.4167 | 1896.5826
3.4236 | 1896.5926
3.4306 | 1896.5798
3.4375 | 1896.5958
3.4444 | 1896.6406
3.4514 | 1896.6758
3.4583 | 1896.7009
3.4653 | 1896.7202
3.4722 | 1896.6427
3.4792 | 1896.5535
3.4861 | 1896.4846
3.4931 | 1896.4361
3.5 | 1896.4024
3.5069 | 1896.4336
3.5139 | 1896.5045
3.5208 | 1896.5703
3.5278 | 1896.6063
3.5347 | 1896.6142
3.5417 | 1896.5995
3.5486 | 1896.5398
3.5556 | 1896.4826
3.5625 | 1896.44
3.5694 | 1896.4078
3.5764 | 1896.4136
3.5833 | 1896.4576
3.5903 | 1896.4867
3.5972 | 1896.5306
3.6042 | 1896.6083
3.6111 | 1896.6889
3.6181 | 1896.7557
3.625 | 1896.8107
3.6319 | 1896.8563
3.6389 | 1896.8932
3.6458 | 1896.8903
3.6528 | 1896.8016
3.6597 | 1896.7134
3.6667 | 1896.6457
3.6736 | 1896.5957
3.6806 | 1896.6292
3.6875 | 1896.7121
3.6944 | 1896.7949
3.7014 | 1896.8606
3.7083 | 1896.9109
3.7153 | 1896.9495
3.7222 | 1896.9791
3.7292 | 1896.978
3.7361 | 1896.8841
3.7431 | 1896.7926
3.75 | 1896.7243
3.7569 | 1896.729
3.7639 | 1896.793
3.7708 | 1896.8304
3.7778 | 1896.7757
3.7847 | 1896.7169
3.7917 | 1896.6741
3.7986 | 1896.6747
3.8056 | 1896.7491
3.8125 | 1896.8162
3.8194 | 1896.8412
3.8264 | 1896.8552
3.8333 | 1896.8763
3.8403 | 1896.894
3.8472 | 1896.8758
3.8542 | 1896.8171
3.8611 | 1896.7643
3.8681 | 1896.8057
3.875 | 1896.8855
3.8819 | 1896.9171
3.8889 | 1896.8721
3.8958 | 1896.8211
3.9028 | 1896.7814
3.9097 | 1896.78
3.9167 | 1896.8393
3.9236 | 1896.8938
3.9306 | 1896.9601
3.9375 | 1897.0262
3.9444 | 1897.0741
3.9514 | 1897.0718
3.9583 | 1897.0524
3.9653 | 1897.0605
3.9722 | 1897.1058
3.9792 | 1897.1474
3.9861 | 1897.1782
3.9931 | 1897.1947
4 | 1897.1797
4.0069 | 1897.1471
4.0139 | 1897.1186
4.0208 | 1897.1106
4.0278 | 1897.1121
4.0347 | 1897.1062
4.0417 | 1897.0906
4.0486 | 1897.0792
4.0556 | 1897.082
4.0625 | 1897.1089
4.0694 | 1897.1363
4.0764 | 1897.1444
4.0833 | 1897.1282
4.0903 | 1897.0804
4.0972 | 1897.0593
4.1042 | 1897.0866
4.1111 | 1897.1203
4.1181 | 1897.1246
4.125 | 1897.0398
4.1319 | 1896.957
4.1389 | 1896.8959
4.1458 | 1896.8498
4.1528 | 1896.8143
4.1597 | 1896.7873
4.1667 | 1896.7681
4.1736 | 1896.8039
4.1806 | 1896.8489
4.1875 | 1896.8404
4.1944 | 1896.826
4.2014 | 1896.8368
4.2083 | 1896.9387
4.2153 | 1897.0499
4.2222 | 1897.1318
4.2292 | 1897.1771
4.2361 | 1897.2163
4.2431 | 1897.2607
4.25 | 1897.2934
4.2569 | 1897.3098
4.2639 | 1897.307
4.2708 | 1897.2713
4.2778 | 1897.1689
4.2847 | 1897.0715
4.2917 | 1896.9981
4.2986 | 1896.9446
4.3056 | 1896.9066
4.3125 | 1896.8802
4.3194 | 1896.8826
4.3264 | 1896.9497
4.3333 | 1897.0262
4.3403 | 1897.0845
4.3472 | 1897.1417
4.3542 | 1897.1986
4.3611 | 1897.2483
4.3681 | 1897.2867
4.375 | 1897.3124
4.3819 | 1897.3331
4.3889 | 1897.3603
4.3958 | 1897.3838
4.4028 | 1897.4026
4.4097 | 1897.4015
4.4167 | 1897.3648
4.4236 | 1897.3068
4.4306 | 1897.2258
4.4375 | 1897.1525
4.4444 | 1897.0943
4.4514 | 1897.0481
4.4583 | 1897.0826
4.4653 | 1897.1532
4.4722 | 1897.2026
4.4792 | 1897.16
4.4861 | 1897.1124
4.4931 | 1897.0801
4.5 | 1897.0579
4.5069 | 1897.0428
4.5139 | 1897.033
4.5208 | 1897.0274
4.5278 | 1897.0255
4.5347 | 1897.0608
4.5417 | 1897.1525
4.5486 | 1897.233
4.5556 | 1897.2607
4.5625 | 1897.2421
4.5694 | 1897.2033
4.5764 | 1897.1694
4.5833 | 1897.2099
4.5903 | 1897.2715
4.5972 | 1897.3041
4.6042 | 1897.291
4.6111 | 1897.2864
4.6181 | 1897.3165
4.625 | 1897.3809
4.6319 | 1897.4461
4.6389 | 1897.4822
4.6458 | 1897.4894
4.6528 | 1897.4952
4.6597 | 1897.5134
4.6667 | 1897.5362
4.6736 | 1897.571
4.6806 | 1897.6003
4.6875 | 1897.6184
4.6944 | 1897.6191
4.7014 | 1897.5827
4.7083 | 1897.5458
4.7153 | 1897.5433
4.7222 | 1897.5561
4.7292 | 1897.5638
4.7361 | 1897.5675
4.7431 | 1897.5651
4.75 | 1897.5638
4.7569 | 1897.5693
4.7639 | 1897.5748
4.7708 | 1897.5787
4.7778 | 1897.5764
4.7847 | 1897.5367
4.7917 | 1897.4637
4.7986 | 1897.444
4.8056 | 1897.4522
4.8125 | 1897.4491
4.8194 | 1897.3756
4.8264 | 1897.2915
4.8333 | 1897.2256
4.8403 | 1897.2118
4.8472 | 1897.2773
4.8542 | 1897.3273
4.8611 | 1897.2875
4.8681 | 1897.2431
4.875 | 1897.2147
4.8819 | 1897.198
4.8889 | 1897.2306
4.8958 | 1897.3084
4.9028 | 1897.3848
4.9097 | 1897.4516
4.9167 | 1897.5061
4.9236 | 1897.5299
4.9306 | 1897.4969
4.9375 | 1897.4442
4.9444 | 1897.4049
4.9514 | 1897.437
4.9583 | 1897.5144
4.9653 | 1897.5893
4.9722 | 1897.6424
4.9792 | 1897.6767
4.9861 | 1897.6685
4.9931 | 1897.6096
5 | 1897.5529
5.0069 | 1897.5492
5.0139 | 1897.5857
5.0208 | 1897.622
5.0278 | 1897.6514
5.0347 | 1897.6727
5.0417 | 1897.6675
5.0486 | 1897.6371
5.0556 | 1897.6278
5.0625 | 1897.6284
5.0694 | 1897.6255
5.0764 | 1897.6269
5.0833 | 1897.6147
5.0903 | 1897.5705
5.0972 | 1897.5562
5.1042 | 1897.5765
5.1111 | 1897.6006
5.1181 | 1897.6146
5.125 | 1897.6211
5.1319 | 1897.6218
5.1389 | 1897.5886
5.1458 | 1897.5052
5.1528 | 1897.4469
5.1597 | 1897.407
5.1667 | 1897.3974
5.1736 | 1897.4459
5.1806 | 1897.4985
5.1875 | 1897.5252
5.1944 | 1897.5433
5.2014 | 1897.5366
5.2083 | 1897.4652
5.2153 | 1897.4341
5.2222 | 1897.4504
5.2292 | 1897.4764
5.2361 | 1897.4954
5.2431 | 1897.506
5.25 | 1897.5104
5.2569 | 1897.4999
5.2639 | 1897.4701
5.2708 | 1897.4092
5.2778 | 1897.367
5.2847 | 1897.3471
5.2917 | 1897.3168
5.2986 | 1897.2257
5.3056 | 1897.1411
5.3125 | 1897.0795
5.3194 | 1897.0362
5.3264 | 1897.056
5.3333 | 1897.1465
5.3403 | 1897.2326
5.3472 | 1897.2974
5.3542 | 1897.3442
5.3611 | 1897.3765
5.3681 | 1897.3973
5.375 | 1897.3951
5.3819 | 1897.329
5.3889 | 1897.2226
5.3958 | 1897.1259
5.4028 | 1897.0496
5.4097 | 1896.99
5.4167 | 1896.9444
5.4236 | 1896.9837
5.4306 | 1897.0708
5.4375 | 1897.1462
5.4444 | 1897.202
5.4514 | 1897.2417
5.4583 | 1897.2688
5.4653 | 1897.2763
5.4722 | 1897.2763
5.4792 | 1897.2768
5.4861 | 1897.2533
5.4931 | 1897.2115
5.5 | 1897.1759
5.5069 | 1897.136
5.5139 | 1897.1363
5.5208 | 1897.1702
5.5278 | 1897.1967
5.5347 | 1897.2045
5.5417 | 1897.2342
5.5486 | 1897.2816
5.5556 | 1897.3216
5.5625 | 1897.349
5.5694 | 1897.3606
5.5764 | 1897.3612
5.5833 | 1897.3669
5.5903 | 1897.3719
5.5972 | 1897.3695
5.6042 | 1897.3546
5.6111 | 1897.322
5.6181 | 1897.2033
5.625 | 1897.0922
5.6319 | 1897.0112
5.6389 | 1896.96
5.6458 | 1897.0211
5.6528 | 1897.1078
5.6597 | 1897.1474
5.6667 | 1897.0929
5.6736 | 1897.0334
5.6806 | 1896.9897
5.6875 | 1897.0437
5.6944 | 1897.1287
5.7014 | 1897.1947
5.7083 | 1897.2197
5.7153 | 1897.1797
5.7222 | 1897.1135
5.7292 | 1897.0512
5.7361 | 1897.0041
5.7431 | 1896.9707
5.75 | 1896.9474
5.7569 | 1897.003
5.7639 | 1897.1039
5.7708 | 1897.1861
5.7778 | 1897.1966
5.7847 | 1897.1375
5.7917 | 1897.0786
5.7986 | 1897.0615
5.8056 | 1897.1023
5.8125 | 1897.1523
5.8194 | 1897.1598
5.8264 | 1897.1057
5.8333 | 1897.0496
5.8403 | 1897.0076
5.8472 | 1896.9772
5.8542 | 1897.0178
5.8611 | 1897.1158
5.8681 | 1897.2046
5.875 | 1897.2653
5.8819 | 1897.2538
5.8889 | 1897.1917
5.8958 | 1897.1365
5.9028 | 1897.185
5.9097 | 1897.2726
5.9167 | 1897.3387
5.9236 | 1897.3602
5.9306 | 1897.3611
5.9375 | 1897.3974
5.9444 | 1897.4404
5.9514 | 1897.473
5.9583 | 1897.4968
5.9653 | 1897.4861
5.9722 | 1897.4375
5.9792 | 1897.4002
5.9861 | 1897.3971
5.9931 | 1897.4176
6 | 1897.4517
6.0069 | 1897.4856
6.0139 | 1897.5086
6.0208 | 1897.5208
6.0278 | 1897.523
6.0347 | 1897.5001
6.0417 | 1897.4222
6.0486 | 1897.3143
6.0556 | 1897.2223
6.0625 | 1897.1556
6.0694 | 1897.1094
6.0764 | 1897.0802
6.0833 | 1897.0643
6.0903 | 1897.0585
6.0972 | 1897.06
6.1042 | 1897.115
6.1111 | 1897.2043
6.1181 | 1897.2754
6.125 | 1897.3009
6.1319 | 1897.3284
6.1389 | 1897.396
6.1458 | 1897.4614
6.1528 | 1897.4871
6.1597 | 1897.4652
6.1667 | 1897.402
6.1736 | 1897.3442
6.1806 | 1897.3026
6.1875 | 1897.2733
6.1944 | 1897.2533
6.2014 | 1897.2917
6.2083 | 1897.3859
6.2153 | 1897.4791
6.2222 | 1897.5567
6.2292 | 1897.6169
6.2361 | 1897.6621
6.2431 | 1897.6886
6.25 | 1897.6944
6.2569 | 1897.6595
6.2639 | 1897.6314
6.2708 | 1897.6357
6.2778 | 1897.6531
6.2847 | 1897.6692
6.2917 | 1897.6767
6.2986 | 1897.6538
6.3056 | 1897.5597
6.3125 | 1897.4551
6.3194 | 1897.3699
6.3264 | 1897.3068
6.3333 | 1897.3191
6.3403 | 1897.402
6.3472 | 1897.4732
6.3542 | 1897.5259
6.3611 | 1897.5656
6.3681 | 1897.5959
6.375 | 1897.6155
6.3819 | 1897.6181
6.3889 | 1897.5532
6.3958 | 1897.4633
6.4028 | 1897.3863
6.4097 | 1897.3269
6.4167 | 1897.3225
6.4236 | 1897.3847
6.4306 | 1897.4543
6.4375 | 1897.5052
6.4444 | 1897.5262
6.4514 | 1897.48
6.4583 | 1897.4043
6.4653 | 1897.3414
6.4722 | 1897.2969
6.4792 | 1897.2644
6.4861 | 1897.2401
6.4931 | 1897.2857
6.5 | 1897.3674
6.5069 | 1897.4465
6.5139 | 1897.5099
6.5208 | 1897.5463
6.5278 | 1897.5272
6.5347 | 1897.4619
6.5417 | 1897.3981
6.5486 | 1897.3472
6.5556 | 1897.3716
6.5625 | 1897.4393
6.5694 | 1897.4639
6.5764 | 1897.4135
6.5833 | 1897.3606
6.5903 | 1897.3225
6.5972 | 1897.2948
6.6042 | 1897.2749
6.6111 | 1897.2617
6.6181 | 1897.2544
6.625 | 1897.251
6.6319 | 1897.2491
6.6389 | 1897.2473
6.6458 | 1897.2452
6.6528 | 1897.2662
6.6597 | 1897.3565
6.6667 | 1897.4646
6.6736 | 1897.5548
6.6806 | 1897.6242
6.6875 | 1897.6769
6.6944 | 1897.6941
6.7014 | 1897.6137
6.7083 | 1897.5332
6.7153 | 1897.4727
6.7222 | 1897.4953
6.7292 | 1897.569
6.7361 | 1897.6333
6.7431 | 1897.6802
6.75 | 1897.7141
6.7569 | 1897.7385
6.7639 | 1897.7386
6.7708 | 1897.674
6.7778 | 1897.5771
6.7847 | 1897.4897
6.7917 | 1897.4209
6.7986 | 1897.3806
6.8056 | 1897.3434
6.8125 | 1897.3138
6.8194 | 1897.2957
6.8264 | 1897.286
6.8333 | 1897.3373
6.8403 | 1897.4064
6.8472 | 1897.397
6.8542 | 1897.3963
6.8611 | 1897.4842
6.8681 | 1897.5893
6.875 | 1897.6725
6.8819 | 1897.7357
6.8889 | 1897.7613
6.8958 | 1897.7122
6.9028 | 1897.6959
6.9097 | 1897.7239
6.9167 | 1897.7569
6.9236 | 1897.7791
6.9306 | 1897.7813
6.9375 | 1897.7597
6.9444 | 1897.7589
6.9514 | 1897.7835
6.9583 | 1897.8063
6.9653 | 1897.822
6.9722 | 1897.8308
6.9792 | 1897.7928
6.9861 | 1897.6795
6.9931 | 1897.5703
7 | 1897.4832

## Influent
Influent
Time | Total chemical oxygen demand (Influent) | Total suspended solids (TSS) (Influent) | Total Kjeldahl nitrogen (TKN) (Influent) | Flow rate (Pipe2) | Flow rate (Influent)
d | g COD/m3 | g TSS/m3 | g N/m3 | m3/d | m3/d
0 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.0069444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.013889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.020833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.027778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.034722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.041667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.048611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.055556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.069444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.076389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.083333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.090278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.097222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.10417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.11111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.11806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.13194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.13889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.14583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.15278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.15972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.16667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.17361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.18056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.19444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.20139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.20833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.21528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.22222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.22917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.23611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.24306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.25694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.26389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.27083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.27778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.28472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.29167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.29861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.30556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.31944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.32639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.33333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.34028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.34722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.35417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.36111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.36806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.38194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.38889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.39583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.40278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.40972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.41667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.42361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.43056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.44444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.45139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.45833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.46528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.47222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.47917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.48611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.49306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.50694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.51389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.52083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.52778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.53472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.54167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.54861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.55556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.56944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.57639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.58333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.59028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.59722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.60417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.61111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.61806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.63194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.63889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.64583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.65278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.65972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.66667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.67361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.68056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.69444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.70139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.70833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.71528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.72222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.72917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.73611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.74306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.75694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.76389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.77083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.77778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.78472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.79167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.79861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.80556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.81944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.82639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.83333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.84028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.84722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.85417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.86111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.86806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.88194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.88889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.89583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.90278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.90972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.91667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.92361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.93056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.94444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.95139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.95833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.96528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.97222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.97917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.98611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
0.99306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.0972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.1944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.2986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.3958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.4931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.5972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.6944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.7986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.8958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
1.9931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.0972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.1944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.2986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.3958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.4931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.5972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.6944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.7986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.8958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
2.9931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.0972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.1944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.2986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.3958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.4931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.5972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.6944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.7986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.8958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
3.9931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.0972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.1944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.2986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.3958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.4931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.5972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.6944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.7986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.8958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
4.9931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.0972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.1944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.2986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.3958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.4931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.5972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.6944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.7986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.8958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
5.9931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.0972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.1944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.25 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.2986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.3958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.4931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5069 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5139 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5208 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5278 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5347 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5417 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5486 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5556 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5694 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5764 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5833 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5903 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.5972 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6042 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6111 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6181 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.625 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6319 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6389 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6458 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6528 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6597 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6667 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6736 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6806 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.6944 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7014 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7083 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7153 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7222 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7292 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7361 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7431 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.75 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7569 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7639 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7708 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7778 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7847 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7917 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.7986 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8056 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8125 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8194 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8264 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8333 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8403 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8472 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8542 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8611 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8681 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.875 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8819 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8889 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.8958 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9028 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9097 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9167 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9236 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9306 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9375 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9444 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9514 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9583 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9653 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9722 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9792 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9861 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
6.9931 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000
7 | 420 | 182.9659 | 56.5 | 23473.0581 | 24000

## Timechart
Timechart
Time | Total suspended solids (TSS) (Pipe11) | Total suspended solids (TSS) (CSTR4) | Aerobic nitrifying organisms (NITO) (CSTR4) | Aerobic nitrifying organisms (NITO) (Pipe11)
d | g TSS/m3 | g TSS/m3 | g COD/m3 | g COD/m3
0 | 3670.6821 | 1884.3469 | 96.3507 | 187.6898
0.0069444 | 3670.7498 | 1884.3815 | 96.3516 | 187.6917
0.013889 | 3670.8113 | 1884.413 | 96.3553 | 187.6989
0.020833 | 3670.8879 | 1884.4523 | 96.3592 | 187.7065
0.027778 | 3670.9722 | 1884.4954 | 96.364 | 187.7159
0.034722 | 3671.0578 | 1884.5392 | 96.3698 | 187.727
0.041667 | 3671.1407 | 1884.5817 | 96.3761 | 187.7395
0.048611 | 3671.2607 | 1884.6431 | 96.3804 | 187.7478
0.055556 | 3671.3782 | 1884.7033 | 96.3863 | 187.7593
0.0625 | 3671.4723 | 1884.7515 | 96.3978 | 187.7817
0.069444 | 3671.5624 | 1884.7976 | 96.4147 | 187.8147
0.076389 | 3671.6461 | 1884.8405 | 96.4332 | 187.8508
0.083333 | 3671.7177 | 1884.8771 | 96.4479 | 187.8793
0.090278 | 3671.7345 | 1884.8857 | 96.4657 | 187.914
0.097222 | 3671.7499 | 1884.8936 | 96.4703 | 187.9229
0.10417 | 3671.7858 | 1884.912 | 96.476 | 187.9341
0.11111 | 3671.8478 | 1884.9438 | 96.486 | 187.9535
0.11806 | 3671.9252 | 1884.9834 | 96.4971 | 187.9751
0.125 | 3671.9711 | 1885.0069 | 96.5076 | 187.9956
0.13194 | 3672.0103 | 1885.027 | 96.5131 | 188.0064
0.13889 | 3672.0536 | 1885.0491 | 96.5126 | 188.0054
0.14583 | 3672.0755 | 1885.0603 | 96.5158 | 188.0117
0.15278 | 3672.1457 | 1885.0963 | 96.5191 | 188.0181
0.15972 | 3672.2101 | 1885.1292 | 96.5294 | 188.0381
0.16667 | 3672.2537 | 1885.1516 | 96.541 | 188.0607
0.17361 | 3672.2978 | 1885.1741 | 96.549 | 188.0764
0.18056 | 3672.3545 | 1885.2032 | 96.5563 | 188.0907
0.1875 | 3672.4337 | 1885.2437 | 96.5635 | 188.1047
0.19444 | 3672.493 | 1885.2741 | 96.5718 | 188.1207
0.20139 | 3672.5058 | 1885.2807 | 96.5788 | 188.1345
0.20833 | 3672.5285 | 1885.2923 | 96.5794 | 188.1356
0.21528 | 3672.5693 | 1885.3132 | 96.5806 | 188.1379
0.22222 | 3672.6188 | 1885.3385 | 96.5889 | 188.1541
0.22917 | 3672.6621 | 1885.3607 | 96.5996 | 188.175
0.23611 | 3672.6911 | 1885.3756 | 96.6087 | 188.1927
0.24306 | 3672.7225 | 1885.3916 | 96.617 | 188.2089
0.25 | 3672.7665 | 1885.4142 | 96.6257 | 188.2258
0.25694 | 3672.8131 | 1885.438 | 96.6339 | 188.2418
0.26389 | 3672.8101 | 1885.4365 | 96.6394 | 188.2525
0.27083 | 3672.8164 | 1885.4397 | 96.6421 | 188.2578
0.27778 | 3672.8716 | 1885.468 | 96.6473 | 188.2678
0.28472 | 3672.9009 | 1885.483 | 96.6537 | 188.2804
0.29167 | 3672.9199 | 1885.4927 | 96.658 | 188.2887
0.29861 | 3672.9346 | 1885.5002 | 96.6608 | 188.2942
0.30556 | 3672.9103 | 1885.4878 | 96.6597 | 188.2921
0.3125 | 3672.8557 | 1885.4598 | 96.6532 | 188.2794
0.31944 | 3672.8495 | 1885.4566 | 96.6482 | 188.2697
0.32639 | 3672.8688 | 1885.4665 | 96.6487 | 188.2706
0.33333 | 3672.9183 | 1885.4919 | 96.6537 | 188.2804
0.34028 | 3673.027 | 1885.5475 | 96.6625 | 188.2976
0.34722 | 3673.1003 | 1885.5851 | 96.6725 | 188.3171
0.35417 | 3673.169 | 1885.6202 | 96.6792 | 188.33
0.36111 | 3673.2396 | 1885.6564 | 96.6842 | 188.3399
0.36806 | 3673.3121 | 1885.6935 | 96.6895 | 188.3503
0.375 | 3673.3839 | 1885.7302 | 96.6957 | 188.3623
0.38194 | 3673.4515 | 1885.7649 | 96.699 | 188.3687
0.38889 | 3673.4665 | 1885.7726 | 96.709 | 188.3882
0.39583 | 3673.4905 | 1885.7848 | 96.7118 | 188.3937
0.40278 | 3673.5291 | 1885.8046 | 96.7143 | 188.3984
0.40972 | 3673.58 | 1885.8307 | 96.7276 | 188.4245
0.41667 | 3673.6195 | 1885.8509 | 96.7406 | 188.4497
0.42361 | 3673.6478 | 1885.8654 | 96.7488 | 188.4657
0.43056 | 3673.6713 | 1885.8774 | 96.7553 | 188.4783
0.4375 | 3673.6916 | 1885.8878 | 96.759 | 188.4857
0.44444 | 3673.7282 | 1885.9066 | 96.7598 | 188.4871
0.45139 | 3673.8314 | 1885.9594 | 96.7586 | 188.4849
0.45833 | 3673.9154 | 1886.0024 | 96.7648 | 188.497
0.46528 | 3673.9986 | 1886.045 | 96.7736 | 188.514
0.47222 | 3674.0871 | 1886.0903 | 96.7923 | 188.5506
0.47917 | 3674.1158 | 1886.105 | 96.8205 | 188.6054
0.48611 | 3674.0975 | 1886.0957 | 96.8281 | 188.6203
0.49306 | 3674.0632 | 1886.0781 | 96.8257 | 188.6156
0.5 | 3674.0482 | 1886.0704 | 96.8202 | 188.6049
0.50694 | 3674.0647 | 1886.0789 | 96.818 | 188.6005
0.51389 | 3674.1056 | 1886.0998 | 96.8232 | 188.6107
0.52083 | 3674.2314 | 1886.1642 | 96.8322 | 188.6283
0.52778 | 3674.3067 | 1886.2027 | 96.8476 | 188.6584
0.53472 | 3674.3635 | 1886.2319 | 96.8585 | 188.6796
0.54167 | 3674.4149 | 1886.2581 | 96.864 | 188.6902
0.54861 | 3674.473 | 1886.2879 | 96.8699 | 188.7018
0.55556 | 3674.5352 | 1886.3198 | 96.8783 | 188.7181
0.5625 | 3674.5958 | 1886.3508 | 96.889 | 188.7391
0.56944 | 3674.6496 | 1886.3783 | 96.8984 | 188.7573
0.57639 | 3674.6118 | 1886.359 | 96.9057 | 188.7715
0.58333 | 3674.5837 | 1886.3446 | 96.9044 | 188.7691
0.59028 | 3674.5647 | 1886.3348 | 96.9018 | 188.7638
0.59722 | 3674.5581 | 1886.3315 | 96.9009 | 188.7621
0.60417 | 3674.5574 | 1886.3311 | 96.9033 | 188.7667
0.61111 | 3674.532 | 1886.3181 | 96.9045 | 188.7691
0.61806 | 3674.499 | 1886.3012 | 96.9029 | 188.7661
0.625 | 3674.4976 | 1886.3005 | 96.8997 | 188.7597
0.63194 | 3674.5319 | 1886.3181 | 96.9006 | 188.7616
0.63889 | 3674.5792 | 1886.3423 | 96.9043 | 188.7688
0.64583 | 3674.6247 | 1886.3656 | 96.9103 | 188.7805
0.65278 | 3674.652 | 1886.3796 | 96.9169 | 188.7933
0.65972 | 3674.656 | 1886.3816 | 96.9206 | 188.8006
0.66667 | 3674.6518 | 1886.3794 | 96.9217 | 188.8027
0.67361 | 3674.6541 | 1886.3806 | 96.9221 | 188.8034
0.68056 | 3674.6843 | 1886.3961 | 96.9261 | 188.8113
0.6875 | 3674.7958 | 1886.4532 | 96.9353 | 188.8292
0.69444 | 3674.8595 | 1886.4858 | 96.9452 | 188.8486
0.70139 | 3674.9159 | 1886.5147 | 96.9525 | 188.8628
0.70833 | 3674.8515 | 1886.4817 | 96.9544 | 188.8664
0.71528 | 3674.8165 | 1886.4638 | 96.9498 | 188.8574
0.72222 | 3674.7865 | 1886.4484 | 96.9468 | 188.8515
0.72917 | 3674.7559 | 1886.4327 | 96.9445 | 188.8472
0.73611 | 3674.7532 | 1886.4314 | 96.9443 | 188.8466
0.74306 | 3674.7838 | 1886.4471 | 96.9473 | 188.8526
0.75 | 3674.7668 | 1886.4383 | 96.9486 | 188.8551
0.75694 | 3674.7393 | 1886.4243 | 96.9468 | 188.8516
0.76389 | 3674.7263 | 1886.4176 | 96.9453 | 188.8488
0.77083 | 3674.7239 | 1886.4163 | 96.9447 | 188.8476
0.77778 | 3674.8606 | 1886.4864 | 96.9534 | 188.8644
0.78472 | 3674.9366 | 1886.5253 | 96.9658 | 188.8886
0.79167 | 3674.9902 | 1886.5527 | 96.9749 | 188.9063
0.79861 | 3675.0274 | 1886.5718 | 96.9814 | 188.919
0.80556 | 3674.9522 | 1886.5333 | 96.9802 | 188.9166
0.8125 | 3674.9008 | 1886.5069 | 96.9739 | 188.9044
0.81944 | 3674.9641 | 1886.5394 | 96.9751 | 188.9068
0.82639 | 3675.0316 | 1886.5739 | 96.9819 | 188.92
0.83333 | 3675.0829 | 1886.6002 | 96.9899 | 188.9356
0.84028 | 3675.1269 | 1886.6227 | 96.9955 | 188.9465
0.84722 | 3675.083 | 1886.6003 | 96.9944 | 188.9444
0.85417 | 3675.0937 | 1886.6057 | 96.9872 | 188.9303
0.86111 | 3675.1423 | 1886.6306 | 96.985 | 188.9261
0.86806 | 3675.2012 | 1886.6607 | 96.9881 | 188.9321
0.875 | 3675.26 | 1886.6909 | 96.9954 | 188.9464
0.88194 | 3675.3178 | 1886.7205 | 97.0045 | 188.964
0.88889 | 3675.404 | 1886.7646 | 97.013 | 188.9807
0.89583 | 3675.51 | 1886.8189 | 97.0218 | 188.9978
0.90278 | 3675.5878 | 1886.8587 | 97.0348 | 189.0232
0.90972 | 3675.6574 | 1886.8943 | 97.0469 | 189.0468
0.91667 | 3675.6477 | 1886.8894 | 97.0636 | 189.0792
0.92361 | 3675.6496 | 1886.8903 | 97.065 | 189.0819
0.93056 | 3675.6692 | 1886.9004 | 97.0659 | 189.0838
0.9375 | 3675.7177 | 1886.9252 | 97.073 | 189.0976
0.94444 | 3675.7263 | 1886.9296 | 97.0827 | 189.1164
0.95139 | 3675.7008 | 1886.9166 | 97.0854 | 189.1217
0.95833 | 3675.6662 | 1886.8989 | 97.0843 | 189.1196
0.96528 | 3675.6453 | 1886.8882 | 97.082 | 189.115
0.97222 | 3675.6825 | 1886.9072 | 97.0817 | 189.1145
0.97917 | 3675.7445 | 1886.939 | 97.0867 | 189.1242
0.98611 | 3675.779 | 1886.9566 | 97.0944 | 189.1393
0.99306 | 3675.7987 | 1886.9667 | 97.0993 | 189.1487
1 | 3675.806 | 1886.9704 | 97.1014 | 189.153
1.0069 | 3675.8044 | 1886.9696 | 97.1019 | 189.1538
1.0139 | 3675.8085 | 1886.9717 | 97.1012 | 189.1525
1.0208 | 3675.8268 | 1886.9811 | 97.1007 | 189.1514
1.0278 | 3675.8669 | 1887.0016 | 97.1009 | 189.1519
1.0347 | 3675.982 | 1887.0606 | 97.1013 | 189.1527
1.0417 | 3676.0862 | 1887.1139 | 97.1067 | 189.1633
1.0486 | 3676.1733 | 1887.1585 | 97.1154 | 189.1802
1.0556 | 3676.2358 | 1887.1905 | 97.1287 | 189.2061
1.0625 | 3676.2686 | 1887.2073 | 97.1457 | 189.2392
1.0694 | 3676.2959 | 1887.2213 | 97.1547 | 189.2568
1.0764 | 3676.3257 | 1887.2365 | 97.1593 | 189.2657
1.0833 | 3676.3564 | 1887.2523 | 97.1628 | 189.2725
1.0903 | 3676.3914 | 1887.2702 | 97.1673 | 189.2813
1.0972 | 3676.4494 | 1887.2999 | 97.173 | 189.2924
1.1042 | 3676.5569 | 1887.3549 | 97.1827 | 189.3114
1.1111 | 3676.5969 | 1887.3754 | 97.2133 | 189.371
1.1181 | 3676.5534 | 1887.3531 | 97.2229 | 189.3897
1.125 | 3676.496 | 1887.3237 | 97.2185 | 189.3811
1.1319 | 3676.4426 | 1887.2964 | 97.2132 | 189.3708
1.1389 | 3676.4047 | 1887.277 | 97.2095 | 189.3636
1.1458 | 3676.3782 | 1887.2634 | 97.2065 | 189.3577
1.1528 | 3676.3756 | 1887.2621 | 97.2043 | 189.3533
1.1597 | 3676.4093 | 1887.2793 | 97.2044 | 189.3536
1.1667 | 3676.4659 | 1887.3083 | 97.2053 | 189.3555
1.1736 | 3676.5324 | 1887.3424 | 97.2078 | 189.3602
1.1806 | 3676.5956 | 1887.3747 | 97.2166 | 189.3775
1.1875 | 3676.642 | 1887.3985 | 97.2265 | 189.3967
1.1944 | 3676.6831 | 1887.4195 | 97.2321 | 189.4076
1.2014 | 3676.7871 | 1887.4728 | 97.2387 | 189.4204
1.2083 | 3676.875 | 1887.5178 | 97.2519 | 189.4461
1.2153 | 3676.9436 | 1887.5529 | 97.2676 | 189.4769
1.2222 | 3676.9108 | 1887.5361 | 97.283 | 189.5069
1.2292 | 3676.8375 | 1887.4986 | 97.2805 | 189.5019
1.2361 | 3676.761 | 1887.4594 | 97.2725 | 189.4863
1.2431 | 3676.7062 | 1887.4313 | 97.2642 | 189.4702
1.25 | 3676.6885 | 1887.4223 | 97.2584 | 189.4588
1.2569 | 3676.7 | 1887.4282 | 97.2561 | 189.4543
1.2639 | 3676.7206 | 1887.4387 | 97.2568 | 189.4558
1.2708 | 3676.7432 | 1887.4503 | 97.2589 | 189.4598
1.2778 | 3676.7663 | 1887.4621 | 97.2612 | 189.4643
1.2847 | 3676.791 | 1887.4747 | 97.2637 | 189.4692
1.2917 | 3676.8335 | 1887.4966 | 97.2676 | 189.4768
1.2986 | 3676.9613 | 1887.562 | 97.2748 | 189.4909
1.3056 | 3677.0456 | 1887.6051 | 97.2841 | 189.5089
1.3125 | 3677.1251 | 1887.6458 | 97.2938 | 189.5278
1.3194 | 3677.199 | 1887.6837 | 97.3051 | 189.5499
1.3264 | 3677.2088 | 1887.6887 | 97.3188 | 189.5766
1.3333 | 3677.2143 | 1887.6915 | 97.3252 | 189.5889
1.3403 | 3677.2066 | 1887.6876 | 97.3256 | 189.5898
1.3472 | 3677.21 | 1887.6893 | 97.3247 | 189.5881
1.3542 | 3677.2375 | 1887.7034 | 97.327 | 189.5926
1.3611 | 3677.3481 | 1887.76 | 97.3369 | 189.6119
1.3681 | 3677.4047 | 1887.789 | 97.3559 | 189.6489
1.375 | 3677.3949 | 1887.784 | 97.3642 | 189.665
1.3819 | 3677.3628 | 1887.7675 | 97.3639 | 189.6645
1.3889 | 3677.4014 | 1887.7873 | 97.3657 | 189.6679
1.3958 | 3677.4199 | 1887.7968 | 97.3704 | 189.6771
1.4028 | 3677.4469 | 1887.8106 | 97.3708 | 189.6778
1.4097 | 3677.4954 | 1887.8354 | 97.3742 | 189.6844
1.4167 | 3677.5514 | 1887.8641 | 97.3806 | 189.697
1.4236 | 3677.6066 | 1887.8924 | 97.3881 | 189.7115
1.4306 | 3677.653 | 1887.9161 | 97.4004 | 189.7356
1.4375 | 3677.5749 | 1887.8761 | 97.4045 | 189.7436
1.4444 | 3677.4809 | 1887.828 | 97.3964 | 189.7278
1.4514 | 3677.4069 | 1887.7901 | 97.3882 | 189.7118
1.4583 | 3677.3768 | 1887.7747 | 97.3839 | 189.7034
1.4653 | 3677.4461 | 1887.8102 | 97.3878 | 189.7109
1.4722 | 3677.4823 | 1887.8287 | 97.3938 | 189.7228
1.4792 | 3677.5257 | 1887.8509 | 97.3948 | 189.7246
1.4861 | 3677.5994 | 1887.8887 | 97.3966 | 189.7282
1.4931 | 3677.6796 | 1887.9298 | 97.4031 | 189.7409
1.5 | 3677.7518 | 1887.9667 | 97.414 | 189.7621
1.5069 | 3677.8061 | 1887.9945 | 97.4246 | 189.7828
1.5139 | 3677.8427 | 1888.0133 | 97.4341 | 189.8012
1.5208 | 3677.8621 | 1888.0232 | 97.4413 | 189.8153
1.5278 | 3677.8701 | 1888.0273 | 97.4453 | 189.823
1.5347 | 3677.8799 | 1888.0323 | 97.4472 | 189.8267
1.5417 | 3677.8766 | 1888.0306 | 97.4483 | 189.8289
1.5486 | 3677.8053 | 1887.9941 | 97.444 | 189.8206
1.5556 | 3677.79 | 1887.9863 | 97.436 | 189.8049
1.5625 | 3677.8114 | 1887.9972 | 97.4326 | 189.7983
1.5694 | 3677.8635 | 1888.0239 | 97.4358 | 189.8046
1.5764 | 3677.9939 | 1888.0907 | 97.4424 | 189.8174
1.5833 | 3678.085 | 1888.1373 | 97.4642 | 189.86
1.5903 | 3678.1448 | 1888.1679 | 97.4857 | 189.9019
1.5972 | 3678.1547 | 1888.173 | 97.4971 | 189.9241
1.6042 | 3678.1337 | 1888.1622 | 97.5003 | 189.9303
1.6111 | 3678.1067 | 1888.1484 | 97.4996 | 189.9289
1.6181 | 3678.0959 | 1888.1429 | 97.4971 | 189.9241
1.625 | 3678.1036 | 1888.1468 | 97.4945 | 189.9189
1.6319 | 3678.0439 | 1888.1163 | 97.4929 | 189.9159
1.6389 | 3678.0121 | 1888.1 | 97.4886 | 189.9074
1.6458 | 3678.0207 | 1888.1044 | 97.4868 | 189.9039
1.6528 | 3678.0437 | 1888.1162 | 97.4881 | 189.9064
1.6597 | 3678.0535 | 1888.1212 | 97.4903 | 189.9108
1.6667 | 3678.0662 | 1888.1277 | 97.4921 | 189.9142
1.6736 | 3678.0692 | 1888.1293 | 97.494 | 189.918
1.6806 | 3678.0873 | 1888.1385 | 97.4971 | 189.924
1.6875 | 3678.1879 | 1888.19 | 97.5033 | 189.9362
1.6944 | 3678.2513 | 1888.2225 | 97.5161 | 189.9611
1.7014 | 3678.2895 | 1888.2421 | 97.5271 | 189.9826
1.7083 | 3678.3051 | 1888.25 | 97.5327 | 189.9933
1.7153 | 3678.317 | 1888.2561 | 97.5353 | 189.9985
1.7222 | 3678.3311 | 1888.2633 | 97.5376 | 190.003
1.7292 | 3678.2306 | 1888.2119 | 97.5335 | 189.9949
1.7361 | 3678.1699 | 1888.1808 | 97.5246 | 189.9776
1.7431 | 3678.1318 | 1888.1613 | 97.5192 | 189.9671
1.75 | 3678.1071 | 1888.1486 | 97.5157 | 189.9602
1.7569 | 3678.1026 | 1888.1463 | 97.5138 | 189.9565
1.7639 | 3678.1215 | 1888.156 | 97.5148 | 189.9586
1.7708 | 3678.151 | 1888.1711 | 97.5173 | 189.9634
1.7778 | 3678.1927 | 1888.1925 | 97.5219 | 189.9724
1.7847 | 3678.2492 | 1888.2214 | 97.5285 | 189.9852
1.7917 | 3678.2967 | 1888.2457 | 97.5357 | 189.9991
1.7986 | 3678.3234 | 1888.2594 | 97.541 | 190.0096
1.8056 | 3678.3398 | 1888.2678 | 97.5443 | 190.016
1.8125 | 3678.3479 | 1888.2719 | 97.5488 | 190.0248
1.8194 | 3678.3384 | 1888.2671 | 97.5504 | 190.0279
1.8264 | 3678.3359 | 1888.2658 | 97.55 | 190.027
1.8333 | 3678.3603 | 1888.2783 | 97.5521 | 190.0311
1.8403 | 3678.4 | 1888.2986 | 97.5578 | 190.0422
1.8472 | 3678.3932 | 1888.2951 | 97.5655 | 190.0574
1.8542 | 3678.3213 | 1888.2583 | 97.5638 | 190.0539
1.8611 | 3678.25 | 1888.2218 | 97.557 | 190.0407
1.8681 | 3678.2045 | 1888.1985 | 97.5505 | 190.028
1.875 | 3678.1992 | 1888.1958 | 97.5452 | 190.0178
1.8819 | 3678.2658 | 1888.2299 | 97.5431 | 190.0136
1.8889 | 3678.4111 | 1888.3043 | 97.5467 | 190.0207
1.8958 | 3678.4983 | 1888.349 | 97.5588 | 190.0443
1.9028 | 3678.5725 | 1888.3869 | 97.5758 | 190.0774
1.9097 | 3678.6113 | 1888.4068 | 97.5908 | 190.1065
1.9167 | 3678.567 | 1888.3841 | 97.5964 | 190.1174
1.9236 | 3678.4951 | 1888.3473 | 97.5919 | 190.1088
1.9306 | 3678.4489 | 1888.3237 | 97.5862 | 190.0977
1.9375 | 3678.4576 | 1888.3281 | 97.5848 | 190.0949
1.9444 | 3678.4638 | 1888.3313 | 97.5867 | 190.0986
1.9514 | 3678.4291 | 1888.3135 | 97.5866 | 190.0984
1.9583 | 3678.3731 | 1888.2848 | 97.5826 | 190.0906
1.9653 | 3678.3282 | 1888.2619 | 97.5781 | 190.0817
1.9722 | 3678.2901 | 1888.2423 | 97.5739 | 190.0737
1.9792 | 3678.265 | 1888.2295 | 97.5704 | 190.0668
1.9861 | 3678.2547 | 1888.2242 | 97.568 | 190.0622
1.9931 | 3678.2665 | 1888.2302 | 97.5662 | 190.0586
2 | 3678.3038 | 1888.2494 | 97.5669 | 190.06
2.0069 | 3678.3547 | 1888.2754 | 97.5712 | 190.0683
2.0139 | 3678.4084 | 1888.3029 | 97.5815 | 190.0884
2.0208 | 3678.4771 | 1888.3381 | 97.593 | 190.1108
2.0278 | 3678.4867 | 1888.343 | 97.601 | 190.1264
2.0347 | 3678.5055 | 1888.3526 | 97.6053 | 190.1349
2.0417 | 3678.5121 | 1888.356 | 97.607 | 190.1381
2.0486 | 3678.5406 | 1888.3706 | 97.6055 | 190.1353
2.0556 | 3678.5963 | 1888.3991 | 97.6051 | 190.1345
2.0625 | 3678.6638 | 1888.4337 | 97.607 | 190.1381
2.0694 | 3678.6491 | 1888.4261 | 97.6119 | 190.1477
2.0764 | 3678.6678 | 1888.4358 | 97.6096 | 190.1433
2.0833 | 3678.6997 | 1888.4521 | 97.6115 | 190.147
2.0903 | 3678.7344 | 1888.4698 | 97.6171 | 190.1579
2.0972 | 3678.7728 | 1888.4895 | 97.6242 | 190.1716
2.1042 | 3678.8123 | 1888.5097 | 97.6321 | 190.1871
2.1111 | 3678.8402 | 1888.524 | 97.6399 | 190.2024
2.1181 | 3678.8405 | 1888.5242 | 97.6492 | 190.2204
2.125 | 3678.8127 | 1888.5099 | 97.6504 | 190.2228
2.1319 | 3678.7925 | 1888.4996 | 97.6467 | 190.2156
2.1389 | 3678.799 | 1888.5029 | 97.6426 | 190.2075
2.1458 | 3678.8264 | 1888.517 | 97.6451 | 190.2123
2.1528 | 3678.859 | 1888.5337 | 97.6518 | 190.2256
2.1597 | 3678.9025 | 1888.5559 | 97.6606 | 190.2425
2.1667 | 3678.978 | 1888.5946 | 97.671 | 190.263
2.1736 | 3679.0051 | 1888.6084 | 97.6811 | 190.2826
2.1806 | 3679.0185 | 1888.6153 | 97.6852 | 190.2907
2.1875 | 3679.0381 | 1888.6253 | 97.6865 | 190.293
2.1944 | 3679.0701 | 1888.6417 | 97.6876 | 190.2952
2.2014 | 3679.1106 | 1888.6624 | 97.6917 | 190.3033
2.2083 | 3679.1495 | 1888.6824 | 97.6985 | 190.3165
2.2153 | 3679.1091 | 1888.6617 | 97.7026 | 190.3245
2.2222 | 3679.0575 | 1888.6353 | 97.697 | 190.3135
2.2292 | 3679.0455 | 1888.6291 | 97.6904 | 190.3006
2.2361 | 3679.0601 | 1888.6366 | 97.6908 | 190.3015
2.2431 | 3679.0734 | 1888.6434 | 97.6952 | 190.3101
2.25 | 3679.0779 | 1888.6457 | 97.6976 | 190.3147
2.2569 | 3679.0971 | 1888.6555 | 97.6954 | 190.3104
2.2639 | 3679.1447 | 1888.6799 | 97.6957 | 190.3111
2.2708 | 3679.194 | 1888.7051 | 97.6998 | 190.319
2.2778 | 3679.2413 | 1888.7294 | 97.7061 | 190.3314
2.2847 | 3679.2906 | 1888.7546 | 97.7132 | 190.3451
2.2917 | 3679.3341 | 1888.7769 | 97.7214 | 190.3611
2.2986 | 3679.3686 | 1888.7946 | 97.7292 | 190.3763
2.3056 | 3679.4093 | 1888.8154 | 97.7349 | 190.3875
2.3125 | 3679.458 | 1888.8403 | 97.7409 | 190.3992
2.3194 | 3679.4951 | 1888.8593 | 97.7493 | 190.4154
2.3264 | 3679.5827 | 1888.9042 | 97.7534 | 190.4235
2.3333 | 3679.6444 | 1888.9358 | 97.7686 | 190.453
2.3403 | 3679.6412 | 1888.9342 | 97.7841 | 190.4833
2.3472 | 3679.6143 | 1888.9204 | 97.7857 | 190.4865
2.3542 | 3679.5962 | 1888.9111 | 97.782 | 190.4792
2.3611 | 3679.5941 | 1888.91 | 97.781 | 190.4772
2.3681 | 3679.6038 | 1888.915 | 97.7826 | 190.4803
2.375 | 3679.6168 | 1888.9217 | 97.7856 | 190.4862
2.3819 | 3679.6453 | 1888.9363 | 97.7898 | 190.4944
2.3889 | 3679.7534 | 1888.9916 | 97.7968 | 190.5081
2.3958 | 3679.8171 | 1889.0242 | 97.814 | 190.5417
2.4028 | 3679.7912 | 1889.0109 | 97.8257 | 190.5644
2.4097 | 3679.671 | 1888.9494 | 97.8203 | 190.5537
2.4167 | 3679.5783 | 1888.9019 | 97.8098 | 190.5333
2.4236 | 3679.5086 | 1888.8662 | 97.8011 | 190.5164
2.4306 | 3679.6039 | 1888.9151 | 97.8041 | 190.5223
2.4375 | 3679.6495 | 1888.9384 | 97.8116 | 190.5369
2.4444 | 3679.6824 | 1888.9552 | 97.8176 | 190.5486
2.4514 | 3679.7033 | 1888.9659 | 97.8215 | 190.5561
2.4583 | 3679.6122 | 1888.9193 | 97.8169 | 190.5471
2.4653 | 3679.5566 | 1888.8908 | 97.8078 | 190.5294
2.4722 | 3679.5648 | 1888.895 | 97.8044 | 190.5228
2.4792 | 3679.6626 | 1888.9451 | 97.8097 | 190.5331
2.4861 | 3679.72 | 1888.9745 | 97.8189 | 190.551
2.4931 | 3679.6721 | 1888.9499 | 97.8203 | 190.5539
2.5 | 3679.6455 | 1888.9363 | 97.8176 | 190.5486
2.5069 | 3679.6341 | 1888.9305 | 97.8162 | 190.5459
2.5139 | 3679.6355 | 1888.9312 | 97.8148 | 190.543
2.5208 | 3679.6539 | 1888.9406 | 97.8185 | 190.5502
2.5278 | 3679.6563 | 1888.9419 | 97.8228 | 190.5588
2.5347 | 3679.6456 | 1888.9364 | 97.8239 | 190.5609
2.5417 | 3679.6637 | 1888.9457 | 97.8257 | 190.5643
2.5486 | 3679.7606 | 1888.9953 | 97.8347 | 190.5818
2.5556 | 3679.8027 | 1889.0168 | 97.8468 | 190.6054
2.5625 | 3679.8139 | 1889.0226 | 97.8532 | 190.6179
2.5694 | 3679.8156 | 1889.0234 | 97.8546 | 190.6207
2.5764 | 3679.8272 | 1889.0294 | 97.8544 | 190.6203
2.5833 | 3679.8499 | 1889.041 | 97.8552 | 190.6219
2.5903 | 3679.8267 | 1889.0291 | 97.855 | 190.6215
2.5972 | 3679.7769 | 1889.0036 | 97.8497 | 190.611
2.6042 | 3679.7716 | 1889.0009 | 97.8428 | 190.5977
2.6111 | 3679.8046 | 1889.0178 | 97.8389 | 190.5901
2.6181 | 3679.8573 | 1889.0448 | 97.842 | 190.5961
2.625 | 3679.9345 | 1889.0843 | 97.8495 | 190.6107
2.6319 | 3680.0094 | 1889.1227 | 97.8675 | 190.6459
2.6389 | 3680.015 | 1889.1255 | 97.8821 | 190.6743
2.6458 | 3680.0022 | 1889.119 | 97.8848 | 190.6795
2.6528 | 3679.9906 | 1889.113 | 97.8847 | 190.6794
2.6597 | 3679.9829 | 1889.1091 | 97.8837 | 190.6773
2.6667 | 3679.9899 | 1889.1127 | 97.8843 | 190.6786
2.6736 | 3679.9939 | 1889.1147 | 97.886 | 190.6819
2.6806 | 3679.9964 | 1889.116 | 97.8837 | 190.6773
2.6875 | 3680.0207 | 1889.1284 | 97.8823 | 190.6746
2.6944 | 3680.0566 | 1889.1468 | 97.8834 | 190.6768
2.7014 | 3680.0935 | 1889.1657 | 97.8883 | 190.6864
2.7083 | 3680.126 | 1889.1824 | 97.8946 | 190.6986
2.7153 | 3680.1492 | 1889.1942 | 97.9013 | 190.7118
2.7222 | 3680.1642 | 1889.2019 | 97.906 | 190.7208
2.7292 | 3680.2009 | 1889.2207 | 97.906 | 190.7209
2.7361 | 3680.2908 | 1889.2668 | 97.9033 | 190.7156
2.7431 | 3680.357 | 1889.3006 | 97.9097 | 190.728
2.75 | 3680.4221 | 1889.334 | 97.9194 | 190.7469
2.7569 | 3680.4856 | 1889.3665 | 97.9322 | 190.772
2.7639 | 3680.5452 | 1889.397 | 97.9467 | 190.8001
2.7708 | 3680.598 | 1889.4241 | 97.9606 | 190.8273
2.7778 | 3680.6024 | 1889.4263 | 97.9772 | 190.8596
2.7847 | 3680.5779 | 1889.4137 | 97.9819 | 190.8688
2.7917 | 3680.5477 | 1889.3983 | 97.9833 | 190.8715
2.7986 | 3680.5043 | 1889.376 | 97.9814 | 190.8678
2.8056 | 3680.4559 | 1889.3513 | 97.9774 | 190.86
2.8125 | 3680.4165 | 1889.3311 | 97.9744 | 190.8542
2.8194 | 3680.3844 | 1889.3147 | 97.9732 | 190.8517
2.8264 | 3680.3404 | 1889.2921 | 97.971 | 190.8474
2.8333 | 3680.2884 | 1889.2655 | 97.9657 | 190.8372
2.8403 | 3680.2677 | 1889.2549 | 97.9609 | 190.8278
2.8472 | 3680.2781 | 1889.2602 | 97.957 | 190.8201
2.8542 | 3680.3222 | 1889.2828 | 97.9541 | 190.8145
2.8611 | 3680.3855 | 1889.3152 | 97.9562 | 190.8186
2.8681 | 3680.4599 | 1889.3533 | 97.9631 | 190.832
2.875 | 3680.5222 | 1889.3852 | 97.9754 | 190.8561
2.8819 | 3680.5499 | 1889.3994 | 97.9875 | 190.8796
2.8889 | 3680.5482 | 1889.3985 | 97.9941 | 190.8924
2.8958 | 3680.5696 | 1889.4095 | 98.0001 | 190.9042
2.9028 | 3680.6087 | 1889.4295 | 98.0082 | 190.9199
2.9097 | 3680.6037 | 1889.427 | 98.0143 | 190.9318
2.9167 | 3680.5843 | 1889.417 | 98.0155 | 190.9342
2.9236 | 3680.5388 | 1889.3937 | 98.0123 | 190.928
2.9306 | 3680.439 | 1889.3426 | 98.0023 | 190.9086
2.9375 | 3680.41 | 1889.3278 | 97.9935 | 190.8913
2.9444 | 3680.4339 | 1889.34 | 97.9907 | 190.8859
2.9514 | 3680.5332 | 1889.3909 | 97.994 | 190.8923
2.9583 | 3680.6042 | 1889.4272 | 98.0018 | 190.9076
2.9653 | 3680.6669 | 1889.4593 | 98.0086 | 190.9207
2.9722 | 3680.7235 | 1889.4883 | 98.0168 | 190.9368
2.9792 | 3680.7711 | 1889.5126 | 98.0274 | 190.9573
2.9861 | 3680.803 | 1889.529 | 98.0376 | 190.9772
2.9931 | 3680.7287 | 1889.491 | 98.0415 | 190.9849
3 | 3680.6433 | 1889.4472 | 98.0343 | 190.9708
3.0069 | 3680.5808 | 1889.4152 | 98.0268 | 190.9561
3.0139 | 3680.5321 | 1889.3903 | 98.0214 | 190.9457
3.0208 | 3680.4903 | 1889.3689 | 98.0178 | 190.9387
3.0278 | 3680.4746 | 1889.3608 | 98.0167 | 190.9364
3.0347 | 3680.488 | 1889.3677 | 98.0187 | 190.9404
3.0417 | 3680.4411 | 1889.3437 | 98.017 | 190.9371
3.0486 | 3680.4138 | 1889.3297 | 98.0119 | 190.9271
3.0556 | 3680.4385 | 1889.3424 | 98.0077 | 190.9189
3.0625 | 3680.4919 | 1889.3697 | 98.0091 | 190.9218
3.0694 | 3680.5363 | 1889.3924 | 98.0154 | 190.9339
3.0764 | 3680.5566 | 1889.4028 | 98.0201 | 190.9432
3.0833 | 3680.5679 | 1889.4086 | 98.0223 | 190.9475
3.0903 | 3680.5763 | 1889.4129 | 98.0241 | 190.9508
3.0972 | 3680.5909 | 1889.4204 | 98.0268 | 190.9563
3.1042 | 3680.6095 | 1889.4299 | 98.0307 | 190.9639
3.1111 | 3680.6046 | 1889.4274 | 98.0351 | 190.9724
3.1181 | 3680.5884 | 1889.4191 | 98.0358 | 190.9738
3.125 | 3680.5896 | 1889.4197 | 98.0327 | 190.9678
3.1319 | 3680.6197 | 1889.4352 | 98.0318 | 190.966
3.1389 | 3680.6915 | 1889.4719 | 98.0347 | 190.9716
3.1458 | 3680.7479 | 1889.5008 | 98.0497 | 191.0008
3.1528 | 3680.7535 | 1889.5037 | 98.0615 | 191.0238
3.1597 | 3680.7367 | 1889.4951 | 98.0652 | 191.0311
3.1667 | 3680.6913 | 1889.4718 | 98.0643 | 191.0294
3.1736 | 3680.6541 | 1889.4528 | 98.0587 | 191.0183
3.1806 | 3680.7303 | 1889.4918 | 98.0598 | 191.0205
3.1875 | 3680.7973 | 1889.5261 | 98.0698 | 191.0401
3.1944 | 3680.8375 | 1889.5466 | 98.0789 | 191.0577
3.2014 | 3680.8612 | 1889.5588 | 98.0835 | 191.0668
3.2083 | 3680.8417 | 1889.5488 | 98.0845 | 191.0687
3.2153 | 3680.768 | 1889.5111 | 98.0788 | 191.0576
3.2222 | 3680.7415 | 1889.4975 | 98.072 | 191.0444
3.2292 | 3680.7454 | 1889.4995 | 98.0708 | 191.042
3.2361 | 3680.7501 | 1889.5019 | 98.073 | 191.0462
3.2431 | 3680.7455 | 1889.4995 | 98.075 | 191.0501
3.25 | 3680.7294 | 1889.4913 | 98.0735 | 191.0471
3.2569 | 3680.729 | 1889.4911 | 98.0716 | 191.0434
3.2639 | 3680.7524 | 1889.5031 | 98.0724 | 191.045
3.2708 | 3680.7972 | 1889.5261 | 98.0762 | 191.0524
3.2778 | 3680.8329 | 1889.5443 | 98.0867 | 191.0728
3.2847 | 3680.8077 | 1889.5314 | 98.0922 | 191.0837
3.2917 | 3680.7438 | 1889.4987 | 98.0898 | 191.079
3.2986 | 3680.6802 | 1889.4661 | 98.0845 | 191.0686
3.3056 | 3680.6309 | 1889.4409 | 98.0797 | 191.0592
3.3125 | 3680.6204 | 1889.4355 | 98.0778 | 191.0555
3.3194 | 3680.7042 | 1889.4784 | 98.0832 | 191.066
3.3264 | 3680.7431 | 1889.4983 | 98.0898 | 191.079
3.3333 | 3680.7723 | 1889.5133 | 98.0938 | 191.0868
3.3403 | 3680.7977 | 1889.5263 | 98.0968 | 191.0925
3.3472 | 3680.8189 | 1889.5372 | 98.0998 | 191.0984
3.3542 | 3680.8114 | 1889.5333 | 98.101 | 191.1008
3.3611 | 3680.7615 | 1889.5078 | 98.099 | 191.0969
3.3681 | 3680.742 | 1889.4978 | 98.0969 | 191.0927
3.375 | 3680.7928 | 1889.5238 | 98.0997 | 191.0983
3.3819 | 3680.8179 | 1889.5366 | 98.1043 | 191.1071
3.3889 | 3680.8423 | 1889.5491 | 98.1072 | 191.1128
3.3958 | 3680.8698 | 1889.5632 | 98.1095 | 191.1174
3.4028 | 3680.8214 | 1889.5384 | 98.109 | 191.1163
3.4097 | 3680.7653 | 1889.5097 | 98.1034 | 191.1054
3.4167 | 3680.7307 | 1889.492 | 98.0987 | 191.0964
3.4236 | 3680.6989 | 1889.4757 | 98.0959 | 191.0908
3.4306 | 3680.6747 | 1889.4633 | 98.0938 | 191.0867
3.4375 | 3680.6602 | 1889.4559 | 98.0923 | 191.0838
3.4444 | 3680.6617 | 1889.4566 | 98.0907 | 191.0806
3.4514 | 3680.6919 | 1889.4721 | 98.0918 | 191.0829
3.4583 | 3680.7445 | 1889.499 | 98.0969 | 191.0928
3.4653 | 3680.8277 | 1889.5417 | 98.1077 | 191.1138
3.4722 | 3680.9095 | 1889.5835 | 98.1174 | 191.1327
3.4792 | 3680.8925 | 1889.5748 | 98.1229 | 191.1434
3.4861 | 3680.8869 | 1889.572 | 98.1203 | 191.1384
3.4931 | 3680.8992 | 1889.5783 | 98.1213 | 191.1403
3.5 | 3680.9009 | 1889.5791 | 98.1245 | 191.1466
3.5069 | 3680.8862 | 1889.5716 | 98.1253 | 191.1481
3.5139 | 3680.8671 | 1889.5618 | 98.1251 | 191.1477
3.5208 | 3680.8416 | 1889.5488 | 98.1248 | 191.1471
3.5278 | 3680.8162 | 1889.5358 | 98.1233 | 191.1443
3.5347 | 3680.8375 | 1889.5466 | 98.1246 | 191.1467
3.5417 | 3680.9232 | 1889.5906 | 98.1317 | 191.1606
3.5486 | 3680.8833 | 1889.5701 | 98.1372 | 191.1714
3.5556 | 3680.8538 | 1889.555 | 98.1339 | 191.1649
3.5625 | 3680.8469 | 1889.5515 | 98.1304 | 191.158
3.5694 | 3680.8516 | 1889.5539 | 98.1285 | 191.1543
3.5764 | 3680.8798 | 1889.5683 | 98.1294 | 191.1561
3.5833 | 3680.9672 | 1889.6131 | 98.1335 | 191.1641
3.5903 | 3681.0497 | 1889.6553 | 98.1389 | 191.1747
3.5972 | 3681.1186 | 1889.6906 | 98.1467 | 191.1899
3.6042 | 3681.1826 | 1889.7234 | 98.157 | 191.2099
3.6111 | 3681.2395 | 1889.7525 | 98.1687 | 191.2327
3.6181 | 3681.2872 | 1889.7769 | 98.1808 | 191.2563
3.625 | 3681.3243 | 1889.7959 | 98.1918 | 191.2778
3.6319 | 3681.2576 | 1889.7618 | 98.1995 | 191.2927
3.6389 | 3681.2041 | 1889.7344 | 98.1951 | 191.2841
3.6458 | 3681.1453 | 1889.7043 | 98.1911 | 191.2764
3.6528 | 3681.0805 | 1889.6711 | 98.1849 | 191.2642
3.6597 | 3681.0646 | 1889.6629 | 98.1769 | 191.2486
3.6667 | 3681.1601 | 1889.7118 | 98.1762 | 191.2473
3.6736 | 3681.2576 | 1889.7618 | 98.1813 | 191.2572
3.6806 | 3681.3384 | 1889.8031 | 98.1895 | 191.2732
3.6875 | 3681.3572 | 1889.8127 | 98.2094 | 191.3119
3.6944 | 3681.3485 | 1889.8083 | 98.2183 | 191.3293
3.7014 | 3681.3211 | 1889.7943 | 98.2198 | 191.3322
3.7083 | 3681.3653 | 1889.8169 | 98.223 | 191.3385
3.7153 | 3681.3795 | 1889.8242 | 98.2252 | 191.3427
3.7222 | 3681.3135 | 1889.7904 | 98.2243 | 191.3409
3.7292 | 3681.2789 | 1889.7727 | 98.2189 | 191.3305
3.7361 | 3681.2723 | 1889.7693 | 98.215 | 191.3229
3.7431 | 3681.2744 | 1889.7704 | 98.2156 | 191.3241
3.75 | 3681.2751 | 1889.7707 | 98.2151 | 191.323
3.7569 | 3681.2879 | 1889.7773 | 98.2137 | 191.3204
3.7639 | 3681.3273 | 1889.7974 | 98.2148 | 191.3225
3.7708 | 3681.3684 | 1889.8185 | 98.2221 | 191.3367
3.7778 | 3681.3744 | 1889.8216 | 98.231 | 191.354
3.7847 | 3681.3508 | 1889.8095 | 98.2324 | 191.3569
3.7917 | 3681.3298 | 1889.7988 | 98.2308 | 191.3537
3.7986 | 3681.3312 | 1889.7994 | 98.23 | 191.352
3.8056 | 3681.3499 | 1889.809 | 98.2298 | 191.3518
3.8125 | 3681.3704 | 1889.8195 | 98.2305 | 191.3531
3.8194 | 3681.3947 | 1889.832 | 98.2331 | 191.3581
3.8264 | 3681.4209 | 1889.8454 | 98.2364 | 191.3647
3.8333 | 3681.4475 | 1889.859 | 98.2402 | 191.3721
3.8403 | 3681.4707 | 1889.8709 | 98.2443 | 191.38
3.8472 | 3681.4969 | 1889.8843 | 98.248 | 191.3873
3.8542 | 3681.5418 | 1889.9073 | 98.2515 | 191.3941
3.8611 | 3681.6354 | 1889.9552 | 98.2578 | 191.4063
3.8681 | 3681.696 | 1889.9862 | 98.2748 | 191.4394
3.875 | 3681.7199 | 1889.9985 | 98.289 | 191.4671
3.8819 | 3681.6456 | 1889.9604 | 98.2925 | 191.4739
3.8889 | 3681.5655 | 1889.9194 | 98.2842 | 191.4577
3.8958 | 3681.5153 | 1889.8937 | 98.2749 | 191.4397
3.9028 | 3681.5045 | 1889.8882 | 98.2674 | 191.425
3.9097 | 3681.5337 | 1889.9031 | 98.2637 | 191.4179
3.9167 | 3681.5784 | 1889.926 | 98.2656 | 191.4216
3.9236 | 3681.6326 | 1889.9538 | 98.2713 | 191.4327
3.9306 | 3681.6824 | 1889.9793 | 98.2795 | 191.4486
3.9375 | 3681.7132 | 1889.995 | 98.2884 | 191.466
3.9444 | 3681.7384 | 1890.0079 | 98.2951 | 191.479
3.9514 | 3681.7534 | 1890.0156 | 98.3018 | 191.4921
3.9583 | 3681.7479 | 1890.0128 | 98.3081 | 191.5044
3.9653 | 3681.7225 | 1889.9998 | 98.3099 | 191.5078
3.9722 | 3681.7002 | 1889.9884 | 98.3097 | 191.5073
3.9792 | 3681.7063 | 1889.9915 | 98.3117 | 191.5113
3.9861 | 3681.7275 | 1890.0024 | 98.3161 | 191.5199
3.9931 | 3681.663 | 1889.9693 | 98.3166 | 191.5209
4 | 3681.5651 | 1889.9192 | 98.3092 | 191.5064
4.0069 | 3681.486 | 1889.8787 | 98.2997 | 191.488
4.0139 | 3681.4328 | 1889.8515 | 98.2918 | 191.4724
4.0208 | 3681.4099 | 1889.8397 | 98.2858 | 191.4608
4.0278 | 3681.4733 | 1889.8722 | 98.2855 | 191.4603
4.0347 | 3681.6048 | 1889.9395 | 98.2934 | 191.4756
4.0417 | 3681.6966 | 1889.9865 | 98.3057 | 191.4997
4.0486 | 3681.7695 | 1890.0239 | 98.3162 | 191.5201
4.0556 | 3681.8223 | 1890.0509 | 98.3303 | 191.5476
4.0625 | 3681.8349 | 1890.0574 | 98.3403 | 191.567
4.0694 | 3681.8134 | 1890.0463 | 98.3432 | 191.5727
4.0764 | 3681.7794 | 1890.0289 | 98.3422 | 191.5707
4.0833 | 3681.7028 | 1889.9897 | 98.337 | 191.5606
4.0903 | 3681.5929 | 1889.9335 | 98.3248 | 191.5368
4.0972 | 3681.5659 | 1889.9196 | 98.3156 | 191.519
4.1042 | 3681.656 | 1889.9657 | 98.3194 | 191.5264
4.1111 | 3681.6943 | 1889.9854 | 98.3287 | 191.5444
4.1181 | 3681.7078 | 1889.9923 | 98.3341 | 191.555
4.125 | 3681.7097 | 1889.9932 | 98.336 | 191.5586
4.1319 | 3681.717 | 1889.997 | 98.336 | 191.5586
4.1389 | 3681.6533 | 1889.9644 | 98.3314 | 191.5498
4.1458 | 3681.6218 | 1889.9483 | 98.3242 | 191.5358
4.1528 | 3681.6318 | 1889.9534 | 98.3207 | 191.5288
4.1597 | 3681.694 | 1889.9852 | 98.3195 | 191.5265
4.1667 | 3681.7866 | 1890.0326 | 98.32 | 191.5276
4.1736 | 3681.8607 | 1890.0706 | 98.326 | 191.5392
4.1806 | 3681.9285 | 1890.1053 | 98.3343 | 191.5553
4.1875 | 3681.9875 | 1890.1355 | 98.343 | 191.5723
4.1944 | 3681.9868 | 1890.1352 | 98.3608 | 191.6071
4.2014 | 3681.9804 | 1890.1319 | 98.3626 | 191.6104
4.2083 | 3681.9866 | 1890.135 | 98.3616 | 191.6086
4.2153 | 3682.0028 | 1890.1433 | 98.3684 | 191.6218
4.2222 | 3682.0115 | 1890.1478 | 98.3786 | 191.6416
4.2292 | 3681.9906 | 1890.1371 | 98.3844 | 191.6531
4.2361 | 3681.9484 | 1890.1155 | 98.3849 | 191.654
4.2431 | 3681.8975 | 1890.0894 | 98.383 | 191.6502
4.25 | 3681.8599 | 1890.0701 | 98.3812 | 191.6468
4.2569 | 3681.8135 | 1890.0464 | 98.3788 | 191.6421
4.2639 | 3681.7405 | 1890.009 | 98.3719 | 191.6286
4.2708 | 3681.7174 | 1889.9972 | 98.3642 | 191.6136
4.2778 | 3681.7452 | 1890.0114 | 98.3617 | 191.6087
4.2847 | 3681.7931 | 1890.0359 | 98.3623 | 191.6099
4.2917 | 3681.8392 | 1890.0595 | 98.3677 | 191.6205
4.2986 | 3681.8661 | 1890.0733 | 98.3727 | 191.6303
4.3056 | 3681.8819 | 1890.0814 | 98.3757 | 191.6361
4.3125 | 3681.9112 | 1890.0964 | 98.3784 | 191.6413
4.3194 | 3681.9952 | 1890.1395 | 98.3821 | 191.6486
4.3264 | 3682.0587 | 1890.1719 | 98.3866 | 191.6572
4.3333 | 3682.054 | 1890.1696 | 98.3963 | 191.6762
4.3403 | 3682.0531 | 1890.1691 | 98.3987 | 191.6809
4.3472 | 3682.0624 | 1890.1738 | 98.4008 | 191.685
4.3542 | 3682.0818 | 1890.1838 | 98.4082 | 191.6994
4.3611 | 3682.1077 | 1890.197 | 98.4165 | 191.7156
4.3681 | 3682.1506 | 1890.219 | 98.425 | 191.7322
4.375 | 3682.1332 | 1890.2101 | 98.4309 | 191.7437
4.3819 | 3682.0886 | 1890.1873 | 98.4297 | 191.7412
4.3889 | 3682.1225 | 1890.2046 | 98.4277 | 191.7374
4.3958 | 3682.158 | 1890.2228 | 98.4312 | 191.7441
4.4028 | 3682.1971 | 1890.2428 | 98.4364 | 191.7543
4.4097 | 3682.2339 | 1890.2617 | 98.442 | 191.7652
4.4167 | 3682.2379 | 1890.2637 | 98.4506 | 191.782
4.4236 | 3682.1269 | 1890.2069 | 98.4475 | 191.7759
4.4306 | 3682.0315 | 1890.158 | 98.4355 | 191.7525
4.4375 | 3681.9823 | 1890.1328 | 98.4249 | 191.7319
4.4444 | 3681.9855 | 1890.1345 | 98.4163 | 191.7152
4.4514 | 3682.0327 | 1890.1586 | 98.414 | 191.7106
4.4583 | 3682.1702 | 1890.2291 | 98.4207 | 191.7237
4.4653 | 3682.2571 | 1890.2735 | 98.4416 | 191.7644
4.4722 | 3682.3061 | 1890.2986 | 98.4579 | 191.7962
4.4792 | 3682.322 | 1890.3067 | 98.4651 | 191.8102
4.4861 | 3682.3251 | 1890.3083 | 98.4625 | 191.8052
4.4931 | 3682.2781 | 1890.2843 | 98.4596 | 191.7994
4.5 | 3682.2719 | 1890.2811 | 98.4557 | 191.7919
4.5069 | 3682.2866 | 1890.2887 | 98.4563 | 191.793
4.5139 | 3682.3131 | 1890.3022 | 98.4598 | 191.8
4.5208 | 3682.3431 | 1890.3176 | 98.4645 | 191.8091
4.5278 | 3682.4164 | 1890.3551 | 98.4677 | 191.8154
4.5347 | 3682.4659 | 1890.3805 | 98.478 | 191.8354
4.5417 | 3682.4309 | 1890.3625 | 98.4902 | 191.8591
4.5486 | 3682.4032 | 1890.3483 | 98.488 | 191.8549
4.5556 | 3682.3866 | 1890.3399 | 98.4848 | 191.8486
4.5625 | 3682.3857 | 1890.3394 | 98.4818 | 191.8428
4.5694 | 3682.3999 | 1890.3466 | 98.4809 | 191.8409
4.5764 | 3682.4465 | 1890.3705 | 98.4814 | 191.842
4.5833 | 3682.5109 | 1890.4035 | 98.4849 | 191.8488
4.5903 | 3682.5481 | 1890.4225 | 98.4979 | 191.8741
4.5972 | 3682.5876 | 1890.4428 | 98.51 | 191.8978
4.6042 | 3682.592 | 1890.445 | 98.5194 | 191.916
4.6111 | 3682.5832 | 1890.4405 | 98.5202 | 191.9177
4.6181 | 3682.6236 | 1890.4612 | 98.5215 | 191.9202
4.625 | 3682.682 | 1890.4911 | 98.529 | 191.9347
4.6319 | 3682.6431 | 1890.4712 | 98.5379 | 191.9522
4.6389 | 3682.6088 | 1890.4536 | 98.5348 | 191.9461
4.6458 | 3682.5898 | 1890.4439 | 98.533 | 191.9425
4.6528 | 3682.5707 | 1890.4341 | 98.5333 | 191.9432
4.6597 | 3682.5511 | 1890.4241 | 98.5345 | 191.9454
4.6667 | 3682.5147 | 1890.4054 | 98.5343 | 191.9451
4.6736 | 3682.4558 | 1890.3753 | 98.531 | 191.9386
4.6806 | 3682.4093 | 1890.3515 | 98.5261 | 191.9291
4.6875 | 3682.389 | 1890.3411 | 98.5234 | 191.9239
4.6944 | 3682.3753 | 1890.334 | 98.5239 | 191.9249
4.7014 | 3682.347 | 1890.3195 | 98.5233 | 191.9236
4.7083 | 3682.2892 | 1890.29 | 98.5187 | 191.9147
4.7153 | 3682.2426 | 1890.2661 | 98.5131 | 191.9038
4.7222 | 3682.2503 | 1890.2701 | 98.5104 | 191.8984
4.7292 | 3682.2941 | 1890.2925 | 98.5109 | 191.8994
4.7361 | 3682.3233 | 1890.3074 | 98.5156 | 191.9086
4.7431 | 3682.3837 | 1890.3383 | 98.5247 | 191.9264
4.75 | 3682.4124 | 1890.353 | 98.5325 | 191.9416
4.7569 | 3682.4039 | 1890.3487 | 98.5357 | 191.9478
4.7639 | 3682.3926 | 1890.3429 | 98.5349 | 191.9462
4.7708 | 3682.2922 | 1890.2915 | 98.5262 | 191.9292
4.7778 | 3682.2472 | 1890.2684 | 98.5172 | 191.9117
4.7847 | 3682.2333 | 1890.2614 | 98.5131 | 191.9037
4.7917 | 3682.2146 | 1890.2517 | 98.5134 | 191.9043
4.7986 | 3682.226 | 1890.2576 | 98.515 | 191.9075
4.8056 | 3682.2887 | 1890.2897 | 98.5207 | 191.9185
4.8125 | 3682.3134 | 1890.3023 | 98.5263 | 191.9294
4.8194 | 3682.339 | 1890.3154 | 98.5277 | 191.9322
4.8264 | 3682.3816 | 1890.3373 | 98.5274 | 191.9316
4.8333 | 3682.4342 | 1890.3642 | 98.531 | 191.9386
4.8403 | 3682.4834 | 1890.3894 | 98.5353 | 191.9469
4.8472 | 3682.5291 | 1890.4128 | 98.5383 | 191.9529
4.8542 | 3682.5749 | 1890.4363 | 98.5435 | 191.9631
4.8611 | 3682.6175 | 1890.4581 | 98.5495 | 191.9748
4.8681 | 3682.6547 | 1890.4771 | 98.5538 | 191.983
4.875 | 3682.6896 | 1890.495 | 98.5569 | 191.989
4.8819 | 3682.6955 | 1890.498 | 98.5636 | 192.0022
4.8889 | 3682.6809 | 1890.4905 | 98.568 | 192.0108
4.8958 | 3682.6808 | 1890.4905 | 98.5678 | 192.0104
4.9028 | 3682.701 | 1890.5008 | 98.5691 | 192.0129
4.9097 | 3682.7825 | 1890.5426 | 98.5682 | 192.0112
4.9167 | 3682.8439 | 1890.574 | 98.5861 | 192.0461
4.9236 | 3682.8922 | 1890.5987 | 98.6044 | 192.0816
4.9306 | 3682.9162 | 1890.611 | 98.6182 | 192.1085
4.9375 | 3682.9141 | 1890.6099 | 98.6246 | 192.121
4.9444 | 3682.8765 | 1890.5907 | 98.6246 | 192.121
4.9514 | 3682.7736 | 1890.538 | 98.6176 | 192.1074
4.9583 | 3682.7019 | 1890.5013 | 98.6071 | 192.0868
4.9653 | 3682.6554 | 1890.4775 | 98.6002 | 192.0735
4.9722 | 3682.6121 | 1890.4553 | 98.5966 | 192.0664
4.9792 | 3682.5604 | 1890.4288 | 98.5932 | 192.0598
4.9861 | 3682.5133 | 1890.4047 | 98.5895 | 192.0527
4.9931 | 3682.539 | 1890.4179 | 98.5903 | 192.0542
5 | 3682.6133 | 1890.4559 | 98.5943 | 192.0619
5.0069 | 3682.605 | 1890.4517 | 98.5953 | 192.064
5.0139 | 3682.6465 | 1890.4729 | 98.598 | 192.0691
5.0208 | 3682.7344 | 1890.5179 | 98.6078 | 192.0883
5.0278 | 3682.7633 | 1890.5327 | 98.6198 | 192.1117
5.0347 | 3682.7524 | 1890.5272 | 98.6247 | 192.1212
5.0417 | 3682.6208 | 1890.4597 | 98.6182 | 192.1085
5.0486 | 3682.5038 | 1890.3999 | 98.6045 | 192.0819
5.0556 | 3682.4365 | 1890.3654 | 98.5928 | 192.0591
5.0625 | 3682.4243 | 1890.3592 | 98.5858 | 192.0453
5.0694 | 3682.4591 | 1890.377 | 98.5863 | 192.0463
5.0764 | 3682.5716 | 1890.4346 | 98.5962 | 192.0657
5.0833 | 3682.6186 | 1890.4586 | 98.6084 | 192.0895
5.0903 | 3682.6032 | 1890.4508 | 98.6133 | 192.0991
5.0972 | 3682.4956 | 1890.3957 | 98.6073 | 192.0873
5.1042 | 3682.4051 | 1890.3493 | 98.5965 | 192.0663
5.1111 | 3682.3503 | 1890.3212 | 98.5875 | 192.0486
5.1181 | 3682.3515 | 1890.3219 | 98.5823 | 192.0385
5.125 | 3682.4027 | 1890.3481 | 98.5843 | 192.0425
5.1319 | 3682.4513 | 1890.373 | 98.59 | 192.0536
5.1389 | 3682.5381 | 1890.4174 | 98.5976 | 192.0684
5.1458 | 3682.6054 | 1890.4519 | 98.6102 | 192.093
5.1528 | 3682.6317 | 1890.4653 | 98.6197 | 192.1114
5.1597 | 3682.5762 | 1890.4369 | 98.6204 | 192.1128
5.1667 | 3682.4736 | 1890.3844 | 98.6111 | 192.0947
5.1736 | 3682.4075 | 1890.3505 | 98.6011 | 192.0752
5.1806 | 3682.3576 | 1890.325 | 98.5948 | 192.0628
5.1875 | 3682.3243 | 1890.3079 | 98.5913 | 192.056
5.1944 | 3682.3222 | 1890.3069 | 98.5911 | 192.0558
5.2014 | 3682.2848 | 1890.2877 | 98.5899 | 192.0534
5.2083 | 3682.231 | 1890.2602 | 98.585 | 192.0438
5.2153 | 3682.2072 | 1890.248 | 98.5802 | 192.0345
5.2222 | 3682.1981 | 1890.2433 | 98.5784 | 192.031
5.2292 | 3682.1778 | 1890.2329 | 98.5771 | 192.0284
5.2361 | 3682.1512 | 1890.2193 | 98.5748 | 192.024
5.2431 | 3682.1307 | 1890.2088 | 98.5732 | 192.0208
5.25 | 3682.1003 | 1890.1933 | 98.5712 | 192.0169
5.2569 | 3682.0538 | 1890.1694 | 98.5672 | 192.0092
5.2639 | 3682.0095 | 1890.1468 | 98.5627 | 192.0004
5.2708 | 3681.9707 | 1890.1269 | 98.558 | 191.9912
5.2778 | 3681.9395 | 1890.1109 | 98.5533 | 191.982
5.2847 | 3681.9326 | 1890.1074 | 98.55 | 191.9755
5.2917 | 3681.975 | 1890.1291 | 98.5488 | 191.9732
5.2986 | 3682.018 | 1890.1511 | 98.5505 | 191.9766
5.3056 | 3682.0572 | 1890.1712 | 98.553 | 191.9815
5.3125 | 3682.1064 | 1890.1964 | 98.5567 | 191.9887
5.3194 | 3682.1541 | 1890.2208 | 98.5636 | 192.0021
5.3264 | 3682.1634 | 1890.2256 | 98.57 | 192.0146
5.3333 | 3682.1533 | 1890.2204 | 98.5729 | 192.0202
5.3403 | 3682.1328 | 1890.2099 | 98.5744 | 192.0232
5.3472 | 3682.0934 | 1890.1897 | 98.574 | 192.0224
5.3542 | 3682.0523 | 1890.1687 | 98.5717 | 192.0179
5.3611 | 3682.0147 | 1890.1494 | 98.5696 | 192.0139
5.3681 | 3681.9428 | 1890.1126 | 98.5654 | 192.0055
5.375 | 3681.8666 | 1890.0736 | 98.5582 | 191.9915
5.3819 | 3681.8058 | 1890.0425 | 98.5506 | 191.9767
5.3889 | 3681.7678 | 1890.023 | 98.5438 | 191.9635
5.3958 | 3681.7623 | 1890.0202 | 98.5394 | 191.9548
5.4028 | 3681.7798 | 1890.0291 | 98.5376 | 191.9515
5.4097 | 3681.8087 | 1890.044 | 98.5381 | 191.9523
5.4167 | 3681.8633 | 1890.0719 | 98.5412 | 191.9585
5.4236 | 3681.9029 | 1890.0922 | 98.5463 | 191.9684
5.4306 | 3681.8944 | 1890.0878 | 98.5498 | 191.9752
5.4375 | 3681.8727 | 1890.0767 | 98.5502 | 191.9759
5.4444 | 3681.8365 | 1890.0582 | 98.549 | 191.9736
5.4514 | 3681.7976 | 1890.0383 | 98.5462 | 191.9682
5.4583 | 3681.8071 | 1890.0431 | 98.5436 | 191.963
5.4653 | 3681.8426 | 1890.0613 | 98.5458 | 191.9675
5.4722 | 3681.8597 | 1890.07 | 98.5493 | 191.9741
5.4792 | 3681.8812 | 1890.0811 | 98.5519 | 191.9793
5.4861 | 3681.9863 | 1890.1349 | 98.5573 | 191.9898
5.4931 | 3682.0455 | 1890.1652 | 98.5711 | 192.0167
5.5 | 3682.0727 | 1890.1791 | 98.5807 | 192.0355
5.5069 | 3682.079 | 1890.1823 | 98.5838 | 192.0415
5.5139 | 3682.0919 | 1890.1889 | 98.5814 | 192.0368
5.5208 | 3682.1182 | 1890.2024 | 98.5814 | 192.0367
5.5278 | 3682.0788 | 1890.1823 | 98.5835 | 192.0408
5.5347 | 3682.0596 | 1890.1724 | 98.5796 | 192.0333
5.5417 | 3682.0512 | 1890.1681 | 98.5788 | 192.0316
5.5486 | 3682.0352 | 1890.1599 | 98.5812 | 192.0365
5.5556 | 3681.9931 | 1890.1384 | 98.581 | 192.0359
5.5625 | 3681.9479 | 1890.1152 | 98.5787 | 192.0314
5.5694 | 3681.9536 | 1890.1182 | 98.58 | 192.034
5.5764 | 3681.9448 | 1890.1136 | 98.5822 | 192.0384
5.5833 | 3681.8469 | 1890.0635 | 98.577 | 192.0281
5.5903 | 3681.768 | 1890.0231 | 98.5682 | 192.0111
5.5972 | 3681.7034 | 1889.99 | 98.5604 | 191.9958
5.6042 | 3681.651 | 1889.9632 | 98.5534 | 191.9821
5.6111 | 3681.6257 | 1889.9502 | 98.5481 | 191.9719
5.6181 | 3681.7632 | 1890.0206 | 98.5513 | 191.9781
5.625 | 3681.8625 | 1890.0715 | 98.5591 | 191.9932
5.6319 | 3681.9524 | 1890.1175 | 98.5657 | 192.0063
5.6389 | 3682.0298 | 1890.1571 | 98.5713 | 192.0171
5.6458 | 3682.0801 | 1890.1829 | 98.5847 | 192.0431
5.6528 | 3682.0315 | 1890.158 | 98.5939 | 192.0611
5.6597 | 3681.9919 | 1890.1377 | 98.5866 | 192.0469
5.6667 | 3681.976 | 1890.1296 | 98.5811 | 192.0362
5.6736 | 3681.9751 | 1890.1291 | 98.5805 | 192.035
5.6806 | 3681.9734 | 1890.1283 | 98.5832 | 192.0403
5.6875 | 3681.966 | 1890.1245 | 98.5852 | 192.0441
5.6944 | 3681.9403 | 1890.1113 | 98.5856 | 192.0449
5.7014 | 3681.9268 | 1890.1044 | 98.5815 | 192.037
5.7083 | 3681.9396 | 1890.1109 | 98.5811 | 192.0362
5.7153 | 3681.9563 | 1890.1195 | 98.5827 | 192.0392
5.7222 | 3681.9785 | 1890.1309 | 98.5839 | 192.0417
5.7292 | 3682.006 | 1890.1449 | 98.5891 | 192.0517
5.7361 | 3682.0238 | 1890.1541 | 98.5947 | 192.0627
5.7431 | 3682.0367 | 1890.1607 | 98.5982 | 192.0695
5.75 | 3682.0544 | 1890.1697 | 98.6009 | 192.0748
5.7569 | 3682.0554 | 1890.1703 | 98.6028 | 192.0784
5.7639 | 3682.0524 | 1890.1687 | 98.6 | 192.0731
5.7708 | 3682.0609 | 1890.1731 | 98.5998 | 192.0726
5.7778 | 3682.0783 | 1890.182 | 98.6033 | 192.0795
5.7847 | 3682.0854 | 1890.1856 | 98.6093 | 192.0912
5.7917 | 3682.0622 | 1890.1738 | 98.6109 | 192.0943
5.7986 | 3682.0278 | 1890.1561 | 98.6085 | 192.0895
5.8056 | 3682.0028 | 1890.1433 | 98.6051 | 192.0829
5.8125 | 3681.9863 | 1890.1349 | 98.6032 | 192.0793
5.8194 | 3681.9738 | 1890.1285 | 98.6026 | 192.078
5.8264 | 3681.9819 | 1890.1326 | 98.6015 | 192.0758
5.8333 | 3682.0003 | 1890.1421 | 98.5992 | 192.0715
5.8403 | 3682.0328 | 1890.1587 | 98.5989 | 192.0708
5.8472 | 3682.0715 | 1890.1785 | 98.6002 | 192.0734
5.8542 | 3682.112 | 1890.1992 | 98.6057 | 192.0842
5.8611 | 3682.1438 | 1890.2155 | 98.6144 | 192.101
5.8681 | 3682.1658 | 1890.2268 | 98.62 | 192.1119
5.875 | 3682.2097 | 1890.2492 | 98.624 | 192.1198
5.8819 | 3682.2921 | 1890.2915 | 98.6296 | 192.1306
5.8889 | 3682.3457 | 1890.3189 | 98.6396 | 192.1501
5.8958 | 3682.3455 | 1890.3188 | 98.6482 | 192.1669
5.9028 | 3682.3299 | 1890.3108 | 98.6493 | 192.1691
5.9097 | 3682.3406 | 1890.3163 | 98.6547 | 192.1797
5.9167 | 3682.3759 | 1890.3343 | 98.6624 | 192.1946
5.9236 | 3682.3992 | 1890.3463 | 98.6702 | 192.2097
5.9306 | 3682.3317 | 1890.3117 | 98.6711 | 192.2116
5.9375 | 3682.2846 | 1890.2876 | 98.6625 | 192.1947
5.9444 | 3682.3196 | 1890.3055 | 98.66 | 192.19
5.9514 | 3682.3335 | 1890.3126 | 98.6634 | 192.1965
5.9583 | 3682.3033 | 1890.2972 | 98.665 | 192.1997
5.9653 | 3682.2743 | 1890.2823 | 98.6637 | 192.1971
5.9722 | 3682.2627 | 1890.2764 | 98.6617 | 192.1933
5.9792 | 3682.3526 | 1890.3224 | 98.6647 | 192.1991
5.9861 | 3682.4065 | 1890.35 | 98.6729 | 192.2151
5.9931 | 3682.4496 | 1890.3721 | 98.6831 | 192.2349
6 | 3682.343 | 1890.3175 | 98.6851 | 192.2389
6.0069 | 3682.2496 | 1890.2697 | 98.6755 | 192.2202
6.0139 | 3682.1607 | 1890.2242 | 98.6661 | 192.2017
6.0208 | 3682.0908 | 1890.1884 | 98.6579 | 192.1858
6.0278 | 3682.0557 | 1890.1704 | 98.6502 | 192.1707
6.0347 | 3682.0648 | 1890.1751 | 98.6471 | 192.1648
6.0417 | 3682.0943 | 1890.1902 | 98.6475 | 192.1654
6.0486 | 3682.1353 | 1890.2111 | 98.649 | 192.1684
6.0556 | 3682.1968 | 1890.2427 | 98.6517 | 192.1736
6.0625 | 3682.2931 | 1890.292 | 98.6557 | 192.1816
6.0694 | 3682.3856 | 1890.3393 | 98.6613 | 192.1925
6.0764 | 3682.4535 | 1890.3741 | 98.6685 | 192.2066
6.0833 | 3682.5082 | 1890.4021 | 98.6742 | 192.2176
6.0903 | 3682.5531 | 1890.4251 | 98.6787 | 192.2264
6.0972 | 3682.5917 | 1890.4448 | 98.6826 | 192.2339
6.1042 | 3682.6332 | 1890.4661 | 98.6927 | 192.2536
6.1111 | 3682.6189 | 1890.4588 | 98.7169 | 192.3009
6.1181 | 3682.5883 | 1890.4431 | 98.7182 | 192.3033
6.125 | 3682.5647 | 1890.431 | 98.7121 | 192.2915
6.1319 | 3682.5615 | 1890.4294 | 98.7088 | 192.285
6.1389 | 3682.5919 | 1890.445 | 98.7094 | 192.2861
6.1458 | 3682.6255 | 1890.4622 | 98.7155 | 192.2981
6.1528 | 3682.6256 | 1890.4622 | 98.7231 | 192.3128
6.1597 | 3682.6278 | 1890.4633 | 98.7248 | 192.3161
6.1667 | 3682.6329 | 1890.466 | 98.7249 | 192.3164
6.1736 | 3682.6433 | 1890.4713 | 98.7246 | 192.3159
6.1806 | 3682.6601 | 1890.4799 | 98.7248 | 192.3162
6.1875 | 3682.6819 | 1890.4911 | 98.7257 | 192.318
6.1944 | 3682.7153 | 1890.5081 | 98.727 | 192.3205
6.2014 | 3682.7446 | 1890.5231 | 98.731 | 192.3283
6.2083 | 3682.7709 | 1890.5366 | 98.7369 | 192.3398
6.2153 | 3682.7957 | 1890.5493 | 98.7437 | 192.353
6.2222 | 3682.8164 | 1890.5599 | 98.7504 | 192.3661
6.2292 | 3682.8302 | 1890.567 | 98.7563 | 192.3777
6.2361 | 3682.8337 | 1890.5688 | 98.7636 | 192.3918
6.2431 | 3682.8103 | 1890.5568 | 98.7685 | 192.4014
6.25 | 3682.7503 | 1890.5261 | 98.7677 | 192.3998
6.2569 | 3682.6712 | 1890.4855 | 98.7619 | 192.3885
6.2639 | 3682.6056 | 1890.452 | 98.7549 | 192.3748
6.2708 | 3682.5587 | 1890.428 | 98.7494 | 192.3642
6.2778 | 3682.5084 | 1890.4022 | 98.7443 | 192.3542
6.2847 | 3682.4649 | 1890.3799 | 98.7394 | 192.3446
6.2917 | 3682.4261 | 1890.3601 | 98.7349 | 192.3358
6.2986 | 3682.3948 | 1890.344 | 98.7308 | 192.3278
6.3056 | 3682.3843 | 1890.3387 | 98.7266 | 192.3197
6.3125 | 3682.435 | 1890.3646 | 98.7262 | 192.3188
6.3194 | 3682.4949 | 1890.3953 | 98.7313 | 192.3289
6.3264 | 3682.5151 | 1890.4056 | 98.7364 | 192.3388
6.3333 | 3682.5165 | 1890.4063 | 98.7385 | 192.3429
6.3403 | 3682.5063 | 1890.4011 | 98.7394 | 192.3445
6.3472 | 3682.5234 | 1890.4099 | 98.7422 | 192.3501
6.3542 | 3682.5796 | 1890.4387 | 98.749 | 192.3632
6.3611 | 3682.5909 | 1890.4444 | 98.7555 | 192.376
6.3681 | 3682.6023 | 1890.4503 | 98.7554 | 192.3758
6.375 | 3682.633 | 1890.466 | 98.7573 | 192.3795
6.3819 | 3682.6154 | 1890.457 | 98.7596 | 192.384
6.3889 | 3682.5942 | 1890.4461 | 98.7607 | 192.3862
6.3958 | 3682.5515 | 1890.4243 | 98.7588 | 192.3823
6.4028 | 3682.4909 | 1890.3932 | 98.7525 | 192.3701
6.4097 | 3682.446 | 1890.3702 | 98.7446 | 192.3546
6.4167 | 3682.4283 | 1890.3612 | 98.7384 | 192.3427
6.4236 | 3682.4344 | 1890.3643 | 98.7356 | 192.3371
6.4306 | 3682.455 | 1890.3748 | 98.7346 | 192.3352
6.4375 | 3682.4921 | 1890.3938 | 98.7375 | 192.3408
6.4444 | 3682.5428 | 1890.4198 | 98.7447 | 192.355
6.4514 | 3682.6433 | 1890.4713 | 98.7542 | 192.3735
6.4583 | 3682.6877 | 1890.494 | 98.7679 | 192.4002
6.4653 | 3682.6346 | 1890.4668 | 98.7729 | 192.4099
6.4722 | 3682.5924 | 1890.4452 | 98.7677 | 192.3997
6.4792 | 3682.5711 | 1890.4343 | 98.762 | 192.3887
6.4861 | 3682.5938 | 1890.446 | 98.7561 | 192.3771
6.4931 | 3682.6828 | 1890.4915 | 98.7533 | 192.3718
6.5 | 3682.7519 | 1890.5269 | 98.7611 | 192.387
6.5069 | 3682.8186 | 1890.5611 | 98.7771 | 192.4181
6.5139 | 3682.7987 | 1890.5508 | 98.7975 | 192.4578
6.5208 | 3682.7353 | 1890.5184 | 98.797 | 192.4568
6.5278 | 3682.6506 | 1890.475 | 98.7892 | 192.4417
6.5347 | 3682.5834 | 1890.4406 | 98.7801 | 192.4239
6.5417 | 3682.5483 | 1890.4226 | 98.7732 | 192.4105
6.5486 | 3682.5441 | 1890.4205 | 98.7696 | 192.4034
6.5556 | 3682.6122 | 1890.4554 | 98.7712 | 192.4066
6.5625 | 3682.697 | 1890.4988 | 98.7746 | 192.4133
6.5694 | 3682.7025 | 1890.5016 | 98.7827 | 192.4289
6.5764 | 3682.6963 | 1890.4984 | 98.7854 | 192.4343
6.5833 | 3682.6937 | 1890.4971 | 98.7872 | 192.4377
6.5903 | 3682.677 | 1890.4885 | 98.7874 | 192.4381
6.5972 | 3682.6792 | 1890.4897 | 98.7872 | 192.4378
6.6042 | 3682.7605 | 1890.5313 | 98.79 | 192.4433
6.6111 | 3682.8055 | 1890.5543 | 98.7986 | 192.46
6.6181 | 3682.7963 | 1890.5496 | 98.8052 | 192.4728
6.625 | 3682.7445 | 1890.5231 | 98.8036 | 192.4697
6.6319 | 3682.7109 | 1890.5059 | 98.798 | 192.4588
6.6389 | 3682.6976 | 1890.4991 | 98.7942 | 192.4514
6.6458 | 3682.7151 | 1890.508 | 98.7935 | 192.4499
6.6528 | 3682.8039 | 1890.5535 | 98.7958 | 192.4545
6.6597 | 3682.8609 | 1890.5827 | 98.8052 | 192.4728
6.6667 | 3682.894 | 1890.5997 | 98.8117 | 192.4854
6.6736 | 3682.8833 | 1890.5942 | 98.8185 | 192.4987
6.6806 | 3682.8765 | 1890.5907 | 98.8201 | 192.5019
6.6875 | 3682.8718 | 1890.5883 | 98.821 | 192.5035
6.6944 | 3682.8665 | 1890.5856 | 98.8218 | 192.5051
6.7014 | 3682.8533 | 1890.5788 | 98.8252 | 192.5118
6.7083 | 3682.8163 | 1890.5599 | 98.8251 | 192.5116
6.7153 | 3682.7707 | 1890.5365 | 98.8211 | 192.5038
6.7222 | 3682.7446 | 1890.5231 | 98.8176 | 192.497
6.7292 | 3682.7444 | 1890.5231 | 98.8173 | 192.4964
6.7361 | 3682.7995 | 1890.5512 | 98.8212 | 192.504
6.7431 | 3682.788 | 1890.5454 | 98.8254 | 192.5122
6.75 | 3682.7891 | 1890.5459 | 98.8289 | 192.5189
6.7569 | 3682.822 | 1890.5627 | 98.8337 | 192.5283
6.7639 | 3682.7793 | 1890.5409 | 98.835 | 192.5309
6.7708 | 3682.6542 | 1890.4769 | 98.8253 | 192.5119
6.7778 | 3682.5795 | 1890.4386 | 98.8121 | 192.4862
6.7847 | 3682.5745 | 1890.436 | 98.8016 | 192.4658
6.7917 | 3682.6182 | 1890.4584 | 98.798 | 192.4588
6.7986 | 3682.6936 | 1890.497 | 98.7996 | 192.4619
6.8056 | 3682.7882 | 1890.5455 | 98.8038 | 192.4702
6.8125 | 3682.8351 | 1890.5695 | 98.8132 | 192.4884
6.8194 | 3682.8555 | 1890.5799 | 98.8192 | 192.5001
6.8264 | 3682.8768 | 1890.5908 | 98.8207 | 192.503
6.8333 | 3682.9033 | 1890.6044 | 98.8224 | 192.5063
6.8403 | 3682.9573 | 1890.6321 | 98.8239 | 192.5092
6.8472 | 3683.0309 | 1890.6697 | 98.8259 | 192.5131
6.8542 | 3683.0691 | 1890.6893 | 98.8401 | 192.5408
6.8611 | 3683.063 | 1890.6862 | 98.8569 | 192.5736
6.8681 | 3683.0642 | 1890.6868 | 98.8644 | 192.5882
6.875 | 3683.0528 | 1890.681 | 98.8711 | 192.6012
6.8819 | 3683.009 | 1890.6585 | 98.8724 | 192.6039
6.8889 | 3682.9345 | 1890.6204 | 98.8684 | 192.5959
6.8958 | 3682.851 | 1890.5776 | 98.8608 | 192.5812
6.9028 | 3682.8686 | 1890.5866 | 98.8588 | 192.5773
6.9097 | 3682.917 | 1890.6114 | 98.8624 | 192.5843
6.9167 | 3682.9453 | 1890.6259 | 98.8678 | 192.5949
6.9236 | 3682.9619 | 1890.6344 | 98.8726 | 192.6041
6.9306 | 3682.962 | 1890.6344 | 98.8757 | 192.6101
6.9375 | 3682.9491 | 1890.6279 | 98.876 | 192.6107
6.9444 | 3682.9346 | 1890.6204 | 98.8748 | 192.6085
6.9514 | 3682.9218 | 1890.6139 | 98.8736 | 192.6061
6.9583 | 3682.9131 | 1890.6094 | 98.8722 | 192.6034
6.9653 | 3682.8493 | 1890.5767 | 98.8689 | 192.597
6.9722 | 3682.731 | 1890.5162 | 98.8591 | 192.5779
6.9792 | 3682.6306 | 1890.4648 | 98.8469 | 192.5541
6.9861 | 3682.5615 | 1890.4294 | 98.8363 | 192.5334
6.9931 | 3682.5339 | 1890.4153 | 98.8283 | 192.5178
7 | 3682.5617 | 1890.4295 | 98.822 | 192.5054

## OUR
OUR
Time | Oxygen uptake rate (OUR) (CSTR) | Oxygen uptake rate (OUR) (CSTR2)
d | mg O2/L/h | mg O2/L/h
0 | 0 | 59.3574
0.0069444 | 0 | 59.3898
0.013889 | 0 | 38.3317
0.020833 | 0 | 38.5142
0.027778 | 0 | 38.6309
0.034722 | 0 | 38.7096
0.041667 | 0 | 38.7656
0.048611 | 0 | 38.8069
0.055556 | 0 | 38.8401
0.0625 | 0 | 43.2957
0.069444 | 0 | 54.9046
0.076389 | 0 | 57.5545
0.083333 | 0 | 58.5152
0.090278 | 0 | 55.6978
0.097222 | 0 | 51.7874
0.10417 | 0 | 52.315
0.11111 | 0 | 54.4155
0.11806 | 0 | 46.267
0.125 | 0 | 38.7775
0.13194 | 0 | 38.8482
0.13889 | 0 | 50.5829
0.14583 | 0 | 60.7249
0.15278 | 0 | 64.4666
0.15972 | 0 | 64.3397
0.16667 | 0 | 64.1897
0.17361 | 0 | 64.0728
0.18056 | 0 | 60.3777
0.1875 | 0 | 38.5787
0.19444 | 0 | 38.73
0.20139 | 0 | 38.8304
0.20833 | 0 | 38.898
0.21528 | 0 | 55.7338
0.22222 | 0 | 61.6121
0.22917 | 0 | 63.0782
0.23611 | 0 | 63.7449
0.24306 | 0 | 63.6317
0.25 | 0 | 61.7838
0.25694 | 0 | 58.0771
0.26389 | 0 | 57.2539
0.27083 | 0 | 62.0785
0.27778 | 0 | 64.0538
0.28472 | 0 | 63.9685
0.29167 | 0 | 63.9038
0.29861 | 0 | 61.58
0.30556 | 0 | 46.7109
0.3125 | 0 | 50.7195
0.31944 | 0 | 57.4491
0.32639 | 0 | 57.2874
0.33333 | 0 | 47.6717
0.34028 | 0 | 38.7395
0.34722 | 0 | 38.8337
0.35417 | 0 | 38.8983
0.36111 | 0 | 38.944
0.36806 | 0 | 38.9779
0.375 | 0 | 39.0041
0.38194 | 0 | 39.0255
0.38889 | 0 | 39.0444
0.39583 | 0 | 39.0598
0.40278 | 0 | 45.2791
0.40972 | 0 | 50.9528
0.41667 | 0 | 48.896
0.42361 | 0 | 53.1206
0.43056 | 0 | 51.2334
0.4375 | 0 | 38.9391
0.44444 | 0 | 38.9872
0.45139 | 0 | 39.0215
0.45833 | 0 | 42.7884
0.46528 | 0 | 60.3643
0.47222 | 0 | 64.8518
0.47917 | 0 | 64.6429
0.48611 | 0 | 64.4703
0.49306 | 0 | 60.4827
0.5 | 0 | 50.9541
0.50694 | 0 | 38.7817
0.51389 | 0 | 38.8898
0.52083 | 0 | 51.7022
0.52778 | 0 | 57.7456
0.53472 | 0 | 57.8128
0.54167 | 0 | 62.8078
0.54861 | 0 | 64.4352
0.55556 | 0 | 64.2981
0.5625 | 0 | 64.194
0.56944 | 0 | 64.1166
0.57639 | 0 | 61.1352
0.58333 | 0 | 55.6875
0.59028 | 0 | 54.8948
0.59722 | 0 | 61.0358
0.60417 | 0 | 64.2236
0.61111 | 0 | 64.129
0.61806 | 0 | 63.8977
0.625 | 0 | 61.4914
0.63194 | 0 | 59.4312
0.63889 | 0 | 59.4446
0.64583 | 0 | 59.8069
0.65278 | 0 | 56.6584
0.65972 | 0 | 55.4033
0.66667 | 0 | 57.4178
0.67361 | 0 | 56.9862
0.68056 | 0 | 54.6402
0.6875 | 0 | 44.0365
0.69444 | 0 | 38.8322
0.70139 | 0 | 49.3038
0.70833 | 0 | 60.976
0.71528 | 0 | 64.598
0.72222 | 0 | 64.4178
0.72917 | 0 | 62.6137
0.73611 | 0 | 58.405
0.74306 | 0 | 60.8295
0.75 | 0 | 64.1651
0.75694 | 0 | 64.0752
0.76389 | 0 | 62.9865
0.77083 | 0 | 58.9241
0.77778 | 0 | 54.6028
0.78472 | 0 | 52.25
0.79167 | 0 | 57.8166
0.79861 | 0 | 61.5179
0.80556 | 0 | 63.4724
0.8125 | 0 | 64.1275
0.81944 | 0 | 64.0472
0.82639 | 0 | 61.833
0.83333 | 0 | 38.6029
0.84028 | 0 | 38.7764
0.84722 | 0 | 38.8892
0.85417 | 0 | 38.9635
0.86111 | 0 | 39.0144
0.86806 | 0 | 59.9948
0.875 | 0 | 64.8421
0.88194 | 0 | 64.3842
0.88889 | 0 | 54.7363
0.89583 | 0 | 40.568
0.90278 | 0 | 53.7508
0.90972 | 0 | 60.1349
0.91667 | 0 | 62.7335
0.92361 | 0 | 61.8194
0.93056 | 0 | 54.1739
0.9375 | 0 | 43.768
0.94444 | 0 | 53.3834
0.95139 | 0 | 62.104
0.95833 | 0 | 64.5447
0.96528 | 0 | 64.3973
0.97222 | 0 | 64.2802
0.97917 | 0 | 55.7665
0.98611 | 0 | 38.7467
0.99306 | 0 | 38.8895
1 | 0 | 38.9826
1.0069 | 0 | 39.0447
1.0139 | 0 | 39.087
1.0208 | 0 | 39.1163
1.0278 | 0 | 42.7186
1.0347 | 0 | 39.1347
1.0417 | 0 | 39.152
1.0486 | 0 | 39.1683
1.0556 | 0 | 48.878
1.0625 | 0 | 56.8314
1.0694 | 0 | 55.0986
1.0764 | 0 | 39.0584
1.0833 | 0 | 39.1141
1.0903 | 0 | 59.4256
1.0972 | 0 | 65.0371
1.1042 | 0 | 64.8259
1.1111 | 0 | 64.657
1.1181 | 0 | 62.8511
1.125 | 0 | 60.8353
1.1319 | 0 | 60.2092
1.1389 | 0 | 54.9776
1.1458 | 0 | 38.8416
1.1528 | 0 | 38.9666
1.1597 | 0 | 39.0473
1.1667 | 0 | 39.1004
1.1736 | 0 | 55.1756
1.1806 | 0 | 62.9518
1.1875 | 0 | 64.331
1.1944 | 0 | 63.2541
1.2014 | 0 | 62.4268
1.2083 | 0 | 62.6465
1.2153 | 0 | 62.6509
1.2222 | 0 | 61.9915
1.2292 | 0 | 56.9763
1.2361 | 0 | 38.8015
1.2431 | 0 | 38.9463
1.25 | 0 | 39.0389
1.2569 | 0 | 45.2878
1.2639 | 0 | 51.1897
1.2708 | 0 | 39.0814
1.2778 | 0 | 39.125
1.2847 | 0 | 39.1559
1.2917 | 0 | 39.2326
1.2986 | 0 | 56.8853
1.3056 | 0 | 63.5442
1.3125 | 0 | 62.8836
1.3194 | 0 | 58.5312
1.3264 | 0 | 49.8212
1.3333 | 0 | 45.289
1.3403 | 0 | 60.8493
1.3472 | 0 | 64.7729
1.3542 | 0 | 64.6073
1.3611 | 0 | 63.0949
1.3681 | 0 | 44.2236
1.375 | 0 | 38.9334
1.3819 | 0 | 60.1851
1.3889 | 0 | 64.7974
1.3958 | 0 | 64.625
1.4028 | 0 | 64.4891
1.4097 | 0 | 64.385
1.4167 | 0 | 62.7053
1.4236 | 0 | 59.0236
1.4306 | 0 | 55.0103
1.4375 | 0 | 60.8856
1.4444 | 0 | 64.4289
1.4514 | 0 | 64.3398
1.4583 | 0 | 64.2693
1.4653 | 0 | 64.2139
1.4722 | 0 | 59.0087
1.4792 | 0 | 38.7607
1.4861 | 0 | 38.9324
1.4931 | 0 | 39.0427
1.5 | 0 | 39.1173
1.5069 | 0 | 58.0314
1.5139 | 0 | 62.1341
1.5208 | 0 | 58.8052
1.5278 | 0 | 38.9993
1.5347 | 0 | 39.0944
1.5417 | 0 | 39.1601
1.5486 | 0 | 39.2061
1.5556 | 0 | 57.4551
1.5625 | 0 | 63.8714
1.5694 | 0 | 64.9622
1.5764 | 0 | 64.7654
1.5833 | 0 | 64.6138
1.5903 | 0 | 64.4997
1.5972 | 0 | 64.4136
1.6042 | 0 | 64.3478
1.6111 | 0 | 61.9228
1.6181 | 0 | 59.4447
1.625 | 0 | 58.355
1.6319 | 0 | 49.5516
1.6389 | 0 | 38.9281
1.6458 | 0 | 39.0525
1.6528 | 0 | 47.5333
1.6597 | 0 | 56.1297
1.6667 | 0 | 63.6139
1.6736 | 0 | 64.6598
1.6806 | 0 | 62.1646
1.6875 | 0 | 61.4622
1.6944 | 0 | 61.3583
1.7014 | 0 | 55.0077
1.7083 | 0 | 40.9134
1.7153 | 0 | 49.4981
1.7222 | 0 | 53.7827
1.7292 | 0 | 57.7988
1.7361 | 0 | 62.5389
1.7431 | 0 | 62.7873
1.75 | 0 | 62.1083
1.7569 | 0 | 64.281
1.7639 | 0 | 64.4165
1.7708 | 0 | 64.3361
1.7778 | 0 | 64.2765
1.7847 | 0 | 63.1575
1.7917 | 0 | 58.0034
1.7986 | 0 | 56.9944
1.8056 | 0 | 61.515
1.8125 | 0 | 64.3992
1.8194 | 0 | 64.3302
1.8264 | 0 | 64.2785
1.8333 | 0 | 64.2402
1.8403 | 0 | 64.2128
1.8472 | 0 | 62.2728
1.8542 | 0 | 57.9023
1.8611 | 0 | 51.9161
1.8681 | 0 | 45.7155
1.875 | 0 | 38.9697
1.8819 | 0 | 39.0745
1.8889 | 0 | 44.06
1.8958 | 0 | 59.8798
1.9028 | 0 | 65.0421
1.9097 | 0 | 64.8415
1.9167 | 0 | 62.1239
1.9236 | 0 | 50.8492
1.9306 | 0 | 38.9703
1.9375 | 0 | 55.6966
1.9444 | 0 | 64.9346
1.9514 | 0 | 64.7481
1.9583 | 0 | 64.5986
1.9653 | 0 | 63.035
1.9722 | 0 | 53.6557
1.9792 | 0 | 50.535
1.9861 | 0 | 59.5016
1.9931 | 0 | 64.6287
2 | 0 | 64.497
2.0069 | 0 | 64.3969
2.0139 | 0 | 64.3228
2.0208 | 0 | 64.2686
2.0278 | 0 | 63.9883
2.0347 | 0 | 61.3575
2.0417 | 0 | 51.1705
2.0486 | 0 | 38.8545
2.0556 | 0 | 39.0047
2.0625 | 0 | 39.1041
2.0694 | 0 | 39.1737
2.0764 | 0 | 55.1043
2.0833 | 0 | 64.2252
2.0903 | 0 | 64.9919
2.0972 | 0 | 64.807
2.1042 | 0 | 64.662
2.1111 | 0 | 60.0741
2.1181 | 0 | 38.9016
2.125 | 0 | 39.0502
2.1319 | 0 | 39.1462
2.1389 | 0 | 39.2098
2.1458 | 0 | 51.6593
2.1528 | 0 | 64.2795
2.1597 | 0 | 65.0661
2.1667 | 0 | 63.7864
2.1736 | 0 | 48.1668
2.1806 | 0 | 39.0424
2.1875 | 0 | 39.1432
2.1944 | 0 | 39.2119
2.2014 | 0 | 48.5531
2.2083 | 0 | 53.5086
2.2153 | 0 | 54.6366
2.2222 | 0 | 58.4785
2.2292 | 0 | 60.1437
2.2361 | 0 | 51.5384
2.2431 | 0 | 39.0951
2.25 | 0 | 39.1809
2.2569 | 0 | 39.2389
2.2639 | 0 | 39.2786
2.2708 | 0 | 51.8605
2.2778 | 0 | 56.0842
2.2847 | 0 | 57.654
2.2917 | 0 | 59.3665
2.2986 | 0 | 53.5098
2.3056 | 0 | 48.9206
2.3125 | 0 | 56.0533
2.3194 | 0 | 54.023
2.3264 | 0 | 39.1277
2.3333 | 0 | 44.3332
2.3403 | 0 | 56.7269
2.3472 | 0 | 62.4201
2.3542 | 0 | 65.071
2.3611 | 0 | 64.8951
2.3681 | 0 | 64.7544
2.375 | 0 | 64.6441
2.3819 | 0 | 64.5588
2.3889 | 0 | 64.4938
2.3958 | 0 | 59.7998
2.4028 | 0 | 59.9011
2.4097 | 0 | 62.9106
2.4167 | 0 | 63.2344
2.4236 | 0 | 61.7218
2.4306 | 0 | 60.6285
2.4375 | 0 | 58.4287
2.4444 | 0 | 55.1584
2.4514 | 0 | 52.8274
2.4583 | 0 | 42.7004
2.4653 | 0 | 44.4101
2.4722 | 0 | 57.3509
2.4792 | 0 | 63.4089
2.4861 | 0 | 64.8948
2.4931 | 0 | 64.7403
2.5 | 0 | 63.463
2.5069 | 0 | 59.3078
2.5139 | 0 | 55.9952
2.5208 | 0 | 59.5999
2.5278 | 0 | 64.6492
2.5347 | 0 | 64.5487
2.5417 | 0 | 64.4724
2.5486 | 0 | 64.4156
2.5556 | 0 | 63.9285
2.5625 | 0 | 53.3997
2.5694 | 0 | 38.9184
2.5764 | 0 | 39.0784
2.5833 | 0 | 39.1824
2.5903 | 0 | 39.2529
2.5972 | 0 | 39.3017
2.6042 | 0 | 39.3352
2.6111 | 0 | 59.1142
2.6181 | 0 | 64.0636
2.625 | 0 | 65.1619
2.6319 | 0 | 61.7594
2.6389 | 0 | 54.0006
2.6458 | 0 | 57.555
2.6528 | 0 | 61.6666
2.6597 | 0 | 60.766
2.6667 | 0 | 52.4097
2.6736 | 0 | 39.0592
2.6806 | 0 | 39.1773
2.6875 | 0 | 43.1678
2.6944 | 0 | 44.2015
2.7014 | 0 | 39.3067
2.7083 | 0 | 39.346
2.7153 | 0 | 41.5167
2.7222 | 0 | 39.3858
2.7292 | 0 | 39.4036
2.7361 | 0 | 40.1676
2.7431 | 0 | 51.9951
2.75 | 0 | 62.1721
2.7569 | 0 | 64.953
2.7639 | 0 | 63.2203
2.7708 | 0 | 64.3209
2.7778 | 0 | 64.9427
2.7847 | 0 | 64.8307
2.7917 | 0 | 63.0385
2.7986 | 0 | 60.2695
2.8056 | 0 | 59.3579
2.8125 | 0 | 61.536
2.8194 | 0 | 61.3146
2.8264 | 0 | 49.355
2.8333 | 0 | 39.0855
2.8403 | 0 | 39.2059
2.8472 | 0 | 39.2833
2.8542 | 0 | 39.3341
2.8611 | 0 | 61.465
2.8681 | 0 | 65.3594
2.875 | 0 | 65.1339
2.8819 | 0 | 64.9535
2.8889 | 0 | 63.4326
2.8958 | 0 | 63.7241
2.9028 | 0 | 64.6572
2.9097 | 0 | 64.1657
2.9167 | 0 | 56.135
2.9236 | 0 | 38.9819
2.9306 | 0 | 39.1411
2.9375 | 0 | 39.2423
2.9444 | 0 | 39.3079
2.9514 | 0 | 39.3518
2.9583 | 0 | 39.3835
2.9653 | 0 | 39.4074
2.9722 | 0 | 47.0842
2.9792 | 0 | 61.1964
2.9861 | 0 | 63.2104
2.9931 | 0 | 59.2921
3 | 0 | 55.6915
3.0069 | 0 | 56.4243
3.0139 | 0 | 60.8655
3.0208 | 0 | 63.7895
3.0278 | 0 | 63.4408
3.0347 | 0 | 60.9212
3.0417 | 0 | 55.6597
3.0486 | 0 | 46.6801
3.0556 | 0 | 39.1203
3.0625 | 0 | 39.2238
3.0694 | 0 | 39.293
3.0764 | 0 | 39.3406
3.0833 | 0 | 52.1481
3.0903 | 0 | 65.4986
3.0972 | 0 | 65.2502
3.1042 | 0 | 65.0445
3.1111 | 0 | 64.4199
3.1181 | 0 | 39.0175
3.125 | 0 | 39.16
3.1319 | 0 | 39.2529
3.1389 | 0 | 61.8847
3.1458 | 0 | 65.27
3.1528 | 0 | 65.0676
3.1597 | 0 | 64.9054
3.1667 | 0 | 64.7778
3.1736 | 0 | 64.6784
3.1806 | 0 | 54.0307
3.1875 | 0 | 39.0176
3.1944 | 0 | 39.167
3.2014 | 0 | 39.2651
3.2083 | 0 | 39.3321
3.2153 | 0 | 40.3635
3.2222 | 0 | 51.6911
3.2292 | 0 | 58.8355
3.2361 | 0 | 63.551
3.2431 | 0 | 63.0417
3.25 | 0 | 58.5594
3.2569 | 0 | 58.0023
3.2639 | 0 | 58.1888
3.2708 | 0 | 57.9713
3.2778 | 0 | 60.4623
3.2847 | 0 | 61.255
3.2917 | 0 | 57.5928
3.2986 | 0 | 59.5532
3.3056 | 0 | 62.9224
3.3125 | 0 | 60.6856
3.3194 | 0 | 54.7046
3.3264 | 0 | 51.1753
3.3333 | 0 | 48.139
3.3403 | 0 | 54.7993
3.3472 | 0 | 63.3922
3.3542 | 0 | 64.9469
3.3611 | 0 | 64.8072
3.3681 | 0 | 61.0024
3.375 | 0 | 45.7458
3.3819 | 0 | 39.1052
3.3889 | 0 | 39.2236
3.3958 | 0 | 39.3026
3.4028 | 0 | 53.9174
3.4097 | 0 | 63.4903
3.4167 | 0 | 61.7655
3.4236 | 0 | 55.4879
3.4306 | 0 | 52.5971
3.4375 | 0 | 59.1
3.4444 | 0 | 65.0375
3.4514 | 0 | 64.8754
3.4583 | 0 | 64.7501
3.4653 | 0 | 64.6562
3.4722 | 0 | 43.8373
3.4792 | 0 | 39.0928
3.4861 | 0 | 39.2189
3.4931 | 0 | 39.3025
3.5 | 0 | 39.3599
3.5069 | 0 | 53.0034
3.5139 | 0 | 59.5944
3.5208 | 0 | 61.0162
3.5278 | 0 | 58.2089
3.5347 | 0 | 54.8555
3.5417 | 0 | 50.9578
3.5486 | 0 | 39.2075
3.5556 | 0 | 39.2956
3.5625 | 0 | 39.355
3.5694 | 0 | 39.3956
3.5764 | 0 | 47.3289
3.5833 | 0 | 53.9855
3.5903 | 0 | 51.0986
3.5972 | 0 | 55.6905
3.6042 | 0 | 63.0409
3.6111 | 0 | 65.2327
3.6181 | 0 | 65.0628
3.625 | 0 | 64.931
3.6319 | 0 | 64.8309
3.6389 | 0 | 64.7515
3.6458 | 0 | 58.4529
3.6528 | 0 | 39.0438
3.6597 | 0 | 39.2035
3.6667 | 0 | 39.3045
3.6736 | 0 | 39.3722
3.6806 | 0 | 56.0253
3.6875 | 0 | 63.2644
3.6944 | 0 | 65.3374
3.7014 | 0 | 65.145
3.7083 | 0 | 64.9888
3.7153 | 0 | 64.8671
3.7222 | 0 | 64.7748
3.7292 | 0 | 60.0974
3.7361 | 0 | 39.0391
3.7431 | 0 | 39.2051
3.75 | 0 | 39.3107
3.7569 | 0 | 53.2864
3.7639 | 0 | 62.57
3.7708 | 0 | 58.6746
3.7778 | 0 | 39.2345
3.7847 | 0 | 39.3293
3.7917 | 0 | 39.3931
3.7986 | 0 | 47.9521
3.8056 | 0 | 61.7558
3.8125 | 0 | 61.5271
3.8194 | 0 | 56.2124
3.8264 | 0 | 55.763
3.8333 | 0 | 57.6908
3.8403 | 0 | 57.2917
3.8472 | 0 | 49.9094
3.8542 | 0 | 39.2446
3.8611 | 0 | 39.3387
3.8681 | 0 | 57.7479
3.875 | 0 | 62.637
3.8819 | 0 | 55.147
3.8889 | 0 | 39.2752
3.8958 | 0 | 39.3641
3.9028 | 0 | 39.4234
3.9097 | 0 | 47.4202
3.9167 | 0 | 58.7601
3.9236 | 0 | 58.5145
3.9306 | 0 | 63.2836
3.9375 | 0 | 65.2498
3.9444 | 0 | 64.055
3.9514 | 0 | 55.7434
3.9583 | 0 | 52.5881
3.9653 | 0 | 57.5885
3.9722 | 0 | 64.4647
3.9792 | 0 | 64.9844
3.9861 | 0 | 64.869
3.9931 | 0 | 63.6496
4 | 0 | 58.581
4.0069 | 0 | 55.5371
4.0139 | 0 | 56.2112
4.0208 | 0 | 59.9547
4.0278 | 0 | 61.7824
4.0347 | 0 | 60.4538
4.0417 | 0 | 58.0609
4.0486 | 0 | 57.6878
4.0556 | 0 | 59.0011
4.0625 | 0 | 62.7199
4.0694 | 0 | 62.7501
4.0764 | 0 | 59.6486
4.0833 | 0 | 55.2743
4.0903 | 0 | 48.281
4.0972 | 0 | 53.8936
4.1042 | 0 | 62.4141
4.1111 | 0 | 63.9073
4.1181 | 0 | 59.4062
4.125 | 0 | 39.1201
4.1319 | 0 | 39.2617
4.1389 | 0 | 39.3552
4.1458 | 0 | 39.4172
4.1528 | 0 | 39.4591
4.1597 | 0 | 39.4879
4.1667 | 0 | 39.509
4.1736 | 0 | 51.5
4.1806 | 0 | 51.4812
4.1875 | 0 | 39.4561
4.1944 | 0 | 39.4996
4.2014 | 0 | 44.0916
4.2083 | 0 | 62.7903
4.2153 | 0 | 65.612
4.2222 | 0 | 64.4366
4.2292 | 0 | 60.9365
4.2361 | 0 | 62.2628
4.2431 | 0 | 65.0909
4.25 | 0 | 64.9648
4.2569 | 0 | 63.9183
4.2639 | 0 | 61.7544
4.2708 | 0 | 56.0275
4.2778 | 0 | 39.6504
4.2847 | 0 | 39.2621
4.2917 | 0 | 39.3593
4.2986 | 0 | 39.4243
4.3056 | 0 | 39.4689
4.3125 | 0 | 39.5002
4.3194 | 0 | 44.919
4.3264 | 0 | 57.5012
4.3333 | 0 | 59.5581
4.3403 | 0 | 58.6849
4.3472 | 0 | 60.9788
4.3542 | 0 | 62.948
4.3611 | 0 | 63.5779
4.3681 | 0 | 63.28
4.375 | 0 | 62.2375
4.3819 | 0 | 62.3898
4.3889 | 0 | 64.5966
4.3958 | 0 | 64.8241
4.4028 | 0 | 64.7644
4.4097 | 0 | 61.2982
4.4167 | 0 | 53.684
4.4236 | 0 | 47.5556
4.4306 | 0 | 39.2374
4.4375 | 0 | 39.3545
4.4444 | 0 | 39.4303
4.4514 | 0 | 39.4805
4.4583 | 0 | 56.3898
4.4653 | 0 | 61.3328
4.4722 | 0 | 58.9442
4.4792 | 0 | 39.3334
4.4861 | 0 | 39.4208
4.4931 | 0 | 39.4827
4.5 | 0 | 39.5255
4.5069 | 0 | 39.5556
4.5139 | 0 | 39.5772
4.5208 | 0 | 39.593
4.5278 | 0 | 39.6047
4.5347 | 0 | 48.3928
4.5417 | 0 | 59.6329
4.5486 | 0 | 59.3932
4.5556 | 0 | 52.173
4.5625 | 0 | 44.1044
4.5694 | 0 | 39.4639
4.5764 | 0 | 39.5158
4.5833 | 0 | 55.2617
4.5903 | 0 | 57.6178
4.5972 | 0 | 53.5196
4.6042 | 0 | 44.65
4.6111 | 0 | 47.3908
4.6181 | 0 | 53.8394
4.625 | 0 | 60.7642
4.6319 | 0 | 62.4768
4.6389 | 0 | 59.2672
4.6458 | 0 | 55.4411
4.6528 | 0 | 56.1804
4.6597 | 0 | 59.0542
4.6667 | 0 | 60.6589
4.6736 | 0 | 64.3575
4.6806 | 0 | 65.0675
4.6875 | 0 | 64.9537
4.6944 | 0 | 63.1324
4.7014 | 0 | 56.4509
4.7083 | 0 | 56.1343
4.7153 | 0 | 62.1608
4.7222 | 0 | 64.9635
4.7292 | 0 | 64.8636
4.7361 | 0 | 64.7894
4.7431 | 0 | 63.7901
4.75 | 0 | 63.7631
4.7569 | 0 | 64.703
4.7639 | 0 | 64.673
4.7708 | 0 | 64.6518
4.7778 | 0 | 63.9897
4.7847 | 0 | 56.8818
4.7917 | 0 | 48.9288
4.7986 | 0 | 58.6047
4.8056 | 0 | 61.8376
4.8125 | 0 | 59.508
4.8194 | 0 | 43.5506
4.8264 | 0 | 39.2692
4.8333 | 0 | 39.3764
4.8403 | 0 | 47.9382
4.8472 | 0 | 61.3763
4.8542 | 0 | 58.2734
4.8611 | 0 | 39.3495
4.8681 | 0 | 39.4413
4.875 | 0 | 39.507
4.8819 | 0 | 39.5552
4.8889 | 0 | 50.1927
4.8958 | 0 | 58.4513
4.9028 | 0 | 60.1734
4.9097 | 0 | 61.3597
4.9167 | 0 | 61.4572
4.9236 | 0 | 57.056
4.9306 | 0 | 45.1422
4.9375 | 0 | 39.417
4.9444 | 0 | 40.6129
4.9514 | 0 | 54.8882
4.9583 | 0 | 62.9171
4.9653 | 0 | 65.5701
4.9722 | 0 | 65.3646
4.9792 | 0 | 65.127
4.9861 | 0 | 59.2632
4.9931 | 0 | 49.6641
5 | 0 | 49.3313
5.0069 | 0 | 58.2071
5.0139 | 0 | 64.5252
5.0208 | 0 | 65.1685
5.0278 | 0 | 65.0408
5.0347 | 0 | 64.3519
5.0417 | 0 | 59.8976
5.0486 | 0 | 55.3634
5.0556 | 0 | 59.8253
5.0625 | 0 | 61.7237
5.0694 | 0 | 61.6566
5.0764 | 0 | 62.8384
5.0833 | 0 | 59.9088
5.0903 | 0 | 52.5151
5.0972 | 0 | 57.6871
5.1042 | 0 | 63.3943
5.1111 | 0 | 65.0288
5.1181 | 0 | 64.9215
5.125 | 0 | 64.8401
5.1319 | 0 | 64.3371
5.1389 | 0 | 57.4827
5.1458 | 0 | 44.6563
5.1528 | 0 | 47.7563
5.1597 | 0 | 47.0396
5.1667 | 0 | 51.6192
5.1736 | 0 | 62.6903
5.1806 | 0 | 64.7052
5.1875 | 0 | 62.6857
5.1944 | 0 | 63.3664
5.2014 | 0 | 59.9019
5.2083 | 0 | 46.5479
5.2153 | 0 | 55.2898
5.2222 | 0 | 62.5205
5.2292 | 0 | 64.7814
5.2361 | 0 | 65.0047
5.2431 | 0 | 64.8973
5.25 | 0 | 64.8157
5.2569 | 0 | 62.7524
5.2639 | 0 | 59.3173
5.2708 | 0 | 52.4613
5.2778 | 0 | 55.3086
5.2847 | 0 | 58.1089
5.2917 | 0 | 55.0254
5.2986 | 0 | 39.2024
5.3056 | 0 | 39.3255
5.3125 | 0 | 39.4079
5.3194 | 0 | 39.4649
5.3264 | 0 | 51.929
5.3333 | 0 | 64.1997
5.3403 | 0 | 65.5204
5.3472 | 0 | 65.31
5.3542 | 0 | 65.1399
5.3611 | 0 | 65.0056
5.3681 | 0 | 64.9015
5.375 | 0 | 62.1821
5.3819 | 0 | 49.8672
5.3889 | 0 | 39.1718
5.3958 | 0 | 39.3072
5.4028 | 0 | 39.3944
5.4097 | 0 | 39.4523
5.4167 | 0 | 39.492
5.4236 | 0 | 57.1522
5.4306 | 0 | 64.7691
5.4375 | 0 | 65.469
5.4444 | 0 | 65.2615
5.4514 | 0 | 65.0948
5.4583 | 0 | 64.9637
5.4653 | 0 | 62.7442
5.4722 | 0 | 61.9982
5.4792 | 0 | 62.0936
5.4861 | 0 | 56.8748
5.4931 | 0 | 51.783
5.5 | 0 | 50.8572
5.5069 | 0 | 46.9693
5.5139 | 0 | 54.0665
5.5208 | 0 | 59.175
5.5278 | 0 | 58.0302
5.5347 | 0 | 55.3224
5.5417 | 0 | 60.6033
5.5486 | 0 | 64.6983
5.5556 | 0 | 65.0834
5.5625 | 0 | 64.7865
5.5694 | 0 | 63.5054
5.5764 | 0 | 62.4834
5.5833 | 0 | 64.1251
5.5903 | 0 | 64.7909
5.5972 | 0 | 64.4767
5.6042 | 0 | 63.0806
5.6111 | 0 | 60.1404
5.6181 | 0 | 39.4844
5.625 | 0 | 39.2409
5.6319 | 0 | 39.3576
5.6389 | 0 | 40.828
5.6458 | 0 | 62.0083
5.6528 | 0 | 64.8856
5.6597 | 0 | 58.65
5.6667 | 0 | 39.2969
5.6736 | 0 | 39.403
5.6806 | 0 | 39.4748
5.6875 | 0 | 59.8775
5.6944 | 0 | 64.5498
5.7014 | 0 | 64.5043
5.7083 | 0 | 59.8323
5.7153 | 0 | 47.7917
5.7222 | 0 | 41.0725
5.7292 | 0 | 39.4081
5.7361 | 0 | 39.4778
5.7431 | 0 | 39.5258
5.75 | 0 | 39.5596
5.7569 | 0 | 56.8797
5.7639 | 0 | 64.8824
5.7708 | 0 | 64.8618
5.7778 | 0 | 54.2123
5.7847 | 0 | 39.3345
5.7917 | 0 | 39.4319
5.7986 | 0 | 46.5717
5.8056 | 0 | 56.866
5.8125 | 0 | 59.1061
5.8194 | 0 | 52.6398
5.8264 | 0 | 39.3887
5.8333 | 0 | 39.4637
5.8403 | 0 | 39.5159
5.8472 | 0 | 39.5526
5.8542 | 0 | 54.739
5.8611 | 0 | 64.6279
5.8681 | 0 | 65.602
5.875 | 0 | 63.7897
5.8819 | 0 | 51.4396
5.8889 | 0 | 39.3195
5.8958 | 0 | 39.4298
5.9028 | 0 | 59.7789
5.9097 | 0 | 65.1944
5.9167 | 0 | 64.0201
5.9236 | 0 | 58.0239
5.9306 | 0 | 55.3356
5.9375 | 0 | 63.0815
5.9444 | 0 | 65.2032
5.9514 | 0 | 65.0785
5.9583 | 0 | 64.9836
5.9653 | 0 | 59.2905
5.9722 | 0 | 51.5692
5.9792 | 0 | 52.9074
5.9861 | 0 | 57.7796
5.9931 | 0 | 61.1237
6 | 0 | 63.8743
6.0069 | 0 | 65.0953
6.0139 | 0 | 64.9907
6.0208 | 0 | 64.9086
6.0278 | 0 | 64.6532
6.0347 | 0 | 60.8379
6.0417 | 0 | 49.0734
6.0486 | 0 | 39.2191
6.0556 | 0 | 39.3581
6.0625 | 0 | 39.4489
6.0694 | 0 | 39.5118
6.0764 | 0 | 39.5585
6.0833 | 0 | 39.5948
6.0903 | 0 | 39.6242
6.0972 | 0 | 39.6488
6.1042 | 0 | 51.8955
6.1111 | 0 | 58.1358
6.1181 | 0 | 56.9483
6.125 | 0 | 50.4755
6.1319 | 0 | 53.4189
6.1389 | 0 | 62.4664
6.1458 | 0 | 63.7102
6.1528 | 0 | 58.4868
6.1597 | 0 | 49.9381
6.1667 | 0 | 39.404
6.1736 | 0 | 39.5013
6.1806 | 0 | 39.5667
6.1875 | 0 | 39.6116
6.1944 | 0 | 39.6434
6.2014 | 0 | 52.5121
6.2083 | 0 | 62.6162
6.2153 | 0 | 64.9146
6.2222 | 0 | 65.5909
6.2292 | 0 | 65.4102
6.2361 | 0 | 64.9948
6.2431 | 0 | 63.1833
6.25 | 0 | 60.4554
6.2569 | 0 | 52.7401
6.2639 | 0 | 54.3115
6.2708 | 0 | 60.2034
6.2778 | 0 | 63.0461
6.2847 | 0 | 64.2264
6.2917 | 0 | 64.1818
6.2986 | 0 | 59.4514
6.3056 | 0 | 43.7496
6.3125 | 0 | 39.3197
6.3194 | 0 | 39.43
6.3264 | 0 | 39.5034
6.3333 | 0 | 54.0088
6.3403 | 0 | 65.628
6.3472 | 0 | 65.5428
6.3542 | 0 | 65.3421
6.3611 | 0 | 65.1845
6.3681 | 0 | 65.0631
6.375 | 0 | 64.232
6.3819 | 0 | 61.6395
6.3889 | 0 | 47.1252
6.3958 | 0 | 39.2734
6.4028 | 0 | 39.4057
6.4097 | 0 | 39.4916
6.4167 | 0 | 50.4856
6.4236 | 0 | 62.2622
6.4306 | 0 | 65.2298
6.4375 | 0 | 64.8031
6.4444 | 0 | 61.4012
6.4514 | 0 | 48.0362
6.4583 | 0 | 39.3357
6.4653 | 0 | 39.4479
6.4722 | 0 | 39.5229
6.4792 | 0 | 39.5739
6.4861 | 0 | 39.609
6.4931 | 0 | 55.1935
6.5 | 0 | 61.0838
6.5069 | 0 | 63.0422
6.5139 | 0 | 62.7159
6.5208 | 0 | 59.8107
6.5278 | 0 | 49.9885
6.5347 | 0 | 39.3952
6.5417 | 0 | 39.4926
6.5486 | 0 | 39.5567
6.5556 | 0 | 55.4694
6.5625 | 0 | 62.1995
6.5694 | 0 | 55.4564
6.5764 | 0 | 39.4421
6.5833 | 0 | 39.5232
6.5903 | 0 | 39.579
6.5972 | 0 | 39.6169
6.6042 | 0 | 39.6427
6.6111 | 0 | 39.6627
6.6181 | 0 | 39.679
6.625 | 0 | 39.6918
6.6319 | 0 | 39.7007
6.6389 | 0 | 39.7065
6.6458 | 0 | 39.71
6.6528 | 0 | 45.7734
6.6597 | 0 | 60.3766
6.6667 | 0 | 65.1505
6.6736 | 0 | 65.7181
6.6806 | 0 | 65.51
6.6875 | 0 | 65.3421
6.6944 | 0 | 60.6434
6.7014 | 0 | 39.2758
6.7083 | 0 | 39.423
6.7153 | 0 | 39.5175
6.7222 | 0 | 56.4116
6.7292 | 0 | 64.6682
6.7361 | 0 | 65.5699
6.7431 | 0 | 65.3777
6.75 | 0 | 65.2255
6.7569 | 0 | 65.1069
6.7639 | 0 | 61.4957
6.7708 | 0 | 48.2443
6.7778 | 0 | 39.3045
6.7847 | 0 | 39.4324
6.7917 | 0 | 39.5149
6.7986 | 0 | 43.1128
6.8056 | 0 | 39.5904
6.8125 | 0 | 39.6255
6.8194 | 0 | 39.6531
6.8264 | 0 | 39.6744
6.8333 | 0 | 53.3626
6.8403 | 0 | 55.9266
6.8472 | 0 | 39.586
6.8542 | 0 | 44.9228
6.8611 | 0 | 62.0658
6.8681 | 0 | 65.8683
6.875 | 0 | 65.65
6.8819 | 0 | 65.4684
6.8889 | 0 | 61.1328
6.8958 | 0 | 47.2599
6.9028 | 0 | 55.427
6.9097 | 0 | 62.7181
6.9167 | 0 | 64.2397
6.9236 | 0 | 63.579
6.9306 | 0 | 60.7356
6.9375 | 0 | 56.2439
6.9444 | 0 | 60.1637
6.9514 | 0 | 64.7035
6.9583 | 0 | 65.1102
6.9653 | 0 | 65.0226
6.9722 | 0 | 64.9557
6.9792 | 0 | 56.8466
6.9861 | 0 | 39.2088
6.9931 | 0 | 39.3738
7 | 0 | 39.4773

## Temp
Temp
Time | Temperature (Influent)
d | Â°C
0 | 20
0.0069444 | 20
0.013889 | 20
0.020833 | 20
0.027778 | 20
0.034722 | 20
0.041667 | 20
0.048611 | 20
0.055556 | 20
0.0625 | 20
0.069444 | 20
0.076389 | 20
0.083333 | 20
0.090278 | 20
0.097222 | 20
0.10417 | 20
0.11111 | 20
0.11806 | 20
0.125 | 20
0.13194 | 20
0.13889 | 20
0.14583 | 20
0.15278 | 20
0.15972 | 20
0.16667 | 20
0.17361 | 20
0.18056 | 20
0.1875 | 20
0.19444 | 20
0.20139 | 20
0.20833 | 20
0.21528 | 20
0.22222 | 20
0.22917 | 20
0.23611 | 20
0.24306 | 20
0.25 | 20
0.25694 | 20
0.26389 | 20
0.27083 | 20
0.27778 | 20
0.28472 | 20
0.29167 | 20
0.29861 | 20
0.30556 | 20
0.3125 | 20
0.31944 | 20
0.32639 | 20
0.33333 | 20
0.34028 | 20
0.34722 | 20
0.35417 | 20
0.36111 | 20
0.36806 | 20
0.375 | 20
0.38194 | 20
0.38889 | 20
0.39583 | 20
0.40278 | 20
0.40972 | 20
0.41667 | 20
0.42361 | 20
0.43056 | 20
0.4375 | 20
0.44444 | 20
0.45139 | 20
0.45833 | 20
0.46528 | 20
0.47222 | 20
0.47917 | 20
0.48611 | 20
0.49306 | 20
0.5 | 20
0.50694 | 20
0.51389 | 20
0.52083 | 20
0.52778 | 20
0.53472 | 20
0.54167 | 20
0.54861 | 20
0.55556 | 20
0.5625 | 20
0.56944 | 20
0.57639 | 20
0.58333 | 20
0.59028 | 20
0.59722 | 20
0.60417 | 20
0.61111 | 20
0.61806 | 20
0.625 | 20
0.63194 | 20
0.63889 | 20
0.64583 | 20
0.65278 | 20
0.65972 | 20
0.66667 | 20
0.67361 | 20
0.68056 | 20
0.6875 | 20
0.69444 | 20
0.70139 | 20
0.70833 | 20
0.71528 | 20
0.72222 | 20
0.72917 | 20
0.73611 | 20
0.74306 | 20
0.75 | 20
0.75694 | 20
0.76389 | 20
0.77083 | 20
0.77778 | 20
0.78472 | 20
0.79167 | 20
0.79861 | 20
0.80556 | 20
0.8125 | 20
0.81944 | 20
0.82639 | 20
0.83333 | 20
0.84028 | 20
0.84722 | 20
0.85417 | 20
0.86111 | 20
0.86806 | 20
0.875 | 20
0.88194 | 20
0.88889 | 20
0.89583 | 20
0.90278 | 20
0.90972 | 20
0.91667 | 20
0.92361 | 20
0.93056 | 20
0.9375 | 20
0.94444 | 20
0.95139 | 20
0.95833 | 20
0.96528 | 20
0.97222 | 20
0.97917 | 20
0.98611 | 20
0.99306 | 20
1 | 20
1.0069 | 20
1.0139 | 20
1.0208 | 20
1.0278 | 20
1.0347 | 20
1.0417 | 20
1.0486 | 20
1.0556 | 20
1.0625 | 20
1.0694 | 20
1.0764 | 20
1.0833 | 20
1.0903 | 20
1.0972 | 20
1.1042 | 20
1.1111 | 20
1.1181 | 20
1.125 | 20
1.1319 | 20
1.1389 | 20
1.1458 | 20
1.1528 | 20
1.1597 | 20
1.1667 | 20
1.1736 | 20
1.1806 | 20
1.1875 | 20
1.1944 | 20
1.2014 | 20
1.2083 | 20
1.2153 | 20
1.2222 | 20
1.2292 | 20
1.2361 | 20
1.2431 | 20
1.25 | 20
1.2569 | 20
1.2639 | 20
1.2708 | 20
1.2778 | 20
1.2847 | 20
1.2917 | 20
1.2986 | 20
1.3056 | 20
1.3125 | 20
1.3194 | 20
1.3264 | 20
1.3333 | 20
1.3403 | 20
1.3472 | 20
1.3542 | 20
1.3611 | 20
1.3681 | 20
1.375 | 20
1.3819 | 20
1.3889 | 20
1.3958 | 20
1.4028 | 20
1.4097 | 20
1.4167 | 20
1.4236 | 20
1.4306 | 20
1.4375 | 20
1.4444 | 20
1.4514 | 20
1.4583 | 20
1.4653 | 20
1.4722 | 20
1.4792 | 20
1.4861 | 20
1.4931 | 20
1.5 | 20
1.5069 | 20
1.5139 | 20
1.5208 | 20
1.5278 | 20
1.5347 | 20
1.5417 | 20
1.5486 | 20
1.5556 | 20
1.5625 | 20
1.5694 | 20
1.5764 | 20
1.5833 | 20
1.5903 | 20
1.5972 | 20
1.6042 | 20
1.6111 | 20
1.6181 | 20
1.625 | 20
1.6319 | 20
1.6389 | 20
1.6458 | 20
1.6528 | 20
1.6597 | 20
1.6667 | 20
1.6736 | 20
1.6806 | 20
1.6875 | 20
1.6944 | 20
1.7014 | 20
1.7083 | 20
1.7153 | 20
1.7222 | 20
1.7292 | 20
1.7361 | 20
1.7431 | 20
1.75 | 20
1.7569 | 20
1.7639 | 20
1.7708 | 20
1.7778 | 20
1.7847 | 20
1.7917 | 20
1.7986 | 20
1.8056 | 20
1.8125 | 20
1.8194 | 20
1.8264 | 20
1.8333 | 20
1.8403 | 20
1.8472 | 20
1.8542 | 20
1.8611 | 20
1.8681 | 20
1.875 | 20
1.8819 | 20
1.8889 | 20
1.8958 | 20
1.9028 | 20
1.9097 | 20
1.9167 | 20
1.9236 | 20
1.9306 | 20
1.9375 | 20
1.9444 | 20
1.9514 | 20
1.9583 | 20
1.9653 | 20
1.9722 | 20
1.9792 | 20
1.9861 | 20
1.9931 | 20
2 | 20
2.0069 | 20
2.0139 | 20
2.0208 | 20
2.0278 | 20
2.0347 | 20
2.0417 | 20
2.0486 | 20
2.0556 | 20
2.0625 | 20
2.0694 | 20
2.0764 | 20
2.0833 | 20
2.0903 | 20
2.0972 | 20
2.1042 | 20
2.1111 | 20
2.1181 | 20
2.125 | 20
2.1319 | 20
2.1389 | 20
2.1458 | 20
2.1528 | 20
2.1597 | 20
2.1667 | 20
2.1736 | 20
2.1806 | 20
2.1875 | 20
2.1944 | 20
2.2014 | 20
2.2083 | 20
2.2153 | 20
2.2222 | 20
2.2292 | 20
2.2361 | 20
2.2431 | 20
2.25 | 20
2.2569 | 20
2.2639 | 20
2.2708 | 20
2.2778 | 20
2.2847 | 20
2.2917 | 20
2.2986 | 20
2.3056 | 20
2.3125 | 20
2.3194 | 20
2.3264 | 20
2.3333 | 20
2.3403 | 20
2.3472 | 20
2.3542 | 20
2.3611 | 20
2.3681 | 20
2.375 | 20
2.3819 | 20
2.3889 | 20
2.3958 | 20
2.4028 | 20
2.4097 | 20
2.4167 | 20
2.4236 | 20
2.4306 | 20
2.4375 | 20
2.4444 | 20
2.4514 | 20
2.4583 | 20
2.4653 | 20
2.4722 | 20
2.4792 | 20
2.4861 | 20
2.4931 | 20
2.5 | 20
2.5069 | 20
2.5139 | 20
2.5208 | 20
2.5278 | 20
2.5347 | 20
2.5417 | 20
2.5486 | 20
2.5556 | 20
2.5625 | 20
2.5694 | 20
2.5764 | 20
2.5833 | 20
2.5903 | 20
2.5972 | 20
2.6042 | 20
2.6111 | 20
2.6181 | 20
2.625 | 20
2.6319 | 20
2.6389 | 20
2.6458 | 20
2.6528 | 20
2.6597 | 20
2.6667 | 20
2.6736 | 20
2.6806 | 20
2.6875 | 20
2.6944 | 20
2.7014 | 20
2.7083 | 20
2.7153 | 20
2.7222 | 20
2.7292 | 20
2.7361 | 20
2.7431 | 20
2.75 | 20
2.7569 | 20
2.7639 | 20
2.7708 | 20
2.7778 | 20
2.7847 | 20
2.7917 | 20
2.7986 | 20
2.8056 | 20
2.8125 | 20
2.8194 | 20
2.8264 | 20
2.8333 | 20
2.8403 | 20
2.8472 | 20
2.8542 | 20
2.8611 | 20
2.8681 | 20
2.875 | 20
2.8819 | 20
2.8889 | 20
2.8958 | 20
2.9028 | 20
2.9097 | 20
2.9167 | 20
2.9236 | 20
2.9306 | 20
2.9375 | 20
2.9444 | 20
2.9514 | 20
2.9583 | 20
2.9653 | 20
2.9722 | 20
2.9792 | 20
2.9861 | 20
2.9931 | 20
3 | 20
3.0069 | 20
3.0139 | 20
3.0208 | 20
3.0278 | 20
3.0347 | 20
3.0417 | 20
3.0486 | 20
3.0556 | 20
3.0625 | 20
3.0694 | 20
3.0764 | 20
3.0833 | 20
3.0903 | 20
3.0972 | 20
3.1042 | 20
3.1111 | 20
3.1181 | 20
3.125 | 20
3.1319 | 20
3.1389 | 20
3.1458 | 20
3.1528 | 20
3.1597 | 20
3.1667 | 20
3.1736 | 20
3.1806 | 20
3.1875 | 20
3.1944 | 20
3.2014 | 20
3.2083 | 20
3.2153 | 20
3.2222 | 20
3.2292 | 20
3.2361 | 20
3.2431 | 20
3.25 | 20
3.2569 | 20
3.2639 | 20
3.2708 | 20
3.2778 | 20
3.2847 | 20
3.2917 | 20
3.2986 | 20
3.3056 | 20
3.3125 | 20
3.3194 | 20
3.3264 | 20
3.3333 | 20
3.3403 | 20
3.3472 | 20
3.3542 | 20
3.3611 | 20
3.3681 | 20
3.375 | 20
3.3819 | 20
3.3889 | 20
3.3958 | 20
3.4028 | 20
3.4097 | 20
3.4167 | 20
3.4236 | 20
3.4306 | 20
3.4375 | 20
3.4444 | 20
3.4514 | 20
3.4583 | 20
3.4653 | 20
3.4722 | 20
3.4792 | 20
3.4861 | 20
3.4931 | 20
3.5 | 20
3.5069 | 20
3.5139 | 20
3.5208 | 20
3.5278 | 20
3.5347 | 20
3.5417 | 20
3.5486 | 20
3.5556 | 20
3.5625 | 20
3.5694 | 20
3.5764 | 20
3.5833 | 20
3.5903 | 20
3.5972 | 20
3.6042 | 20
3.6111 | 20
3.6181 | 20
3.625 | 20
3.6319 | 20
3.6389 | 20
3.6458 | 20
3.6528 | 20
3.6597 | 20
3.6667 | 20
3.6736 | 20
3.6806 | 20
3.6875 | 20
3.6944 | 20
3.7014 | 20
3.7083 | 20
3.7153 | 20
3.7222 | 20
3.7292 | 20
3.7361 | 20
3.7431 | 20
3.75 | 20
3.7569 | 20
3.7639 | 20
3.7708 | 20
3.7778 | 20
3.7847 | 20
3.7917 | 20
3.7986 | 20
3.8056 | 20
3.8125 | 20
3.8194 | 20
3.8264 | 20
3.8333 | 20
3.8403 | 20
3.8472 | 20
3.8542 | 20
3.8611 | 20
3.8681 | 20
3.875 | 20
3.8819 | 20
3.8889 | 20
3.8958 | 20
3.9028 | 20
3.9097 | 20
3.9167 | 20
3.9236 | 20
3.9306 | 20
3.9375 | 20
3.9444 | 20
3.9514 | 20
3.9583 | 20
3.9653 | 20
3.9722 | 20
3.9792 | 20
3.9861 | 20
3.9931 | 20
4 | 20
4.0069 | 20
4.0139 | 20
4.0208 | 20
4.0278 | 20
4.0347 | 20
4.0417 | 20
4.0486 | 20
4.0556 | 20
4.0625 | 20
4.0694 | 20
4.0764 | 20
4.0833 | 20
4.0903 | 20
4.0972 | 20
4.1042 | 20
4.1111 | 20
4.1181 | 20
4.125 | 20
4.1319 | 20
4.1389 | 20
4.1458 | 20
4.1528 | 20
4.1597 | 20
4.1667 | 20
4.1736 | 20
4.1806 | 20
4.1875 | 20
4.1944 | 20
4.2014 | 20
4.2083 | 20
4.2153 | 20
4.2222 | 20
4.2292 | 20
4.2361 | 20
4.2431 | 20
4.25 | 20
4.2569 | 20
4.2639 | 20
4.2708 | 20
4.2778 | 20
4.2847 | 20
4.2917 | 20
4.2986 | 20
4.3056 | 20
4.3125 | 20
4.3194 | 20
4.3264 | 20
4.3333 | 20
4.3403 | 20
4.3472 | 20
4.3542 | 20
4.3611 | 20
4.3681 | 20
4.375 | 20
4.3819 | 20
4.3889 | 20
4.3958 | 20
4.4028 | 20
4.4097 | 20
4.4167 | 20
4.4236 | 20
4.4306 | 20
4.4375 | 20
4.4444 | 20
4.4514 | 20
4.4583 | 20
4.4653 | 20
4.4722 | 20
4.4792 | 20
4.4861 | 20
4.4931 | 20
4.5 | 20
4.5069 | 20
4.5139 | 20
4.5208 | 20
4.5278 | 20
4.5347 | 20
4.5417 | 20
4.5486 | 20
4.5556 | 20
4.5625 | 20
4.5694 | 20
4.5764 | 20
4.5833 | 20
4.5903 | 20
4.5972 | 20
4.6042 | 20
4.6111 | 20
4.6181 | 20
4.625 | 20
4.6319 | 20
4.6389 | 20
4.6458 | 20
4.6528 | 20
4.6597 | 20
4.6667 | 20
4.6736 | 20
4.6806 | 20
4.6875 | 20
4.6944 | 20
4.7014 | 20
4.7083 | 20
4.7153 | 20
4.7222 | 20
4.7292 | 20
4.7361 | 20
4.7431 | 20
4.75 | 20
4.7569 | 20
4.7639 | 20
4.7708 | 20
4.7778 | 20
4.7847 | 20
4.7917 | 20
4.7986 | 20
4.8056 | 20
4.8125 | 20
4.8194 | 20
4.8264 | 20
4.8333 | 20
4.8403 | 20
4.8472 | 20
4.8542 | 20
4.8611 | 20
4.8681 | 20
4.875 | 20
4.8819 | 20
4.8889 | 20
4.8958 | 20
4.9028 | 20
4.9097 | 20
4.9167 | 20
4.9236 | 20
4.9306 | 20
4.9375 | 20
4.9444 | 20
4.9514 | 20
4.9583 | 20
4.9653 | 20
4.9722 | 20
4.9792 | 20
4.9861 | 20
4.9931 | 20
5 | 20
5.0069 | 20
5.0139 | 20
5.0208 | 20
5.0278 | 20
5.0347 | 20
5.0417 | 20
5.0486 | 20
5.0556 | 20
5.0625 | 20
5.0694 | 20
5.0764 | 20
5.0833 | 20
5.0903 | 20
5.0972 | 20
5.1042 | 20
5.1111 | 20
5.1181 | 20
5.125 | 20
5.1319 | 20
5.1389 | 20
5.1458 | 20
5.1528 | 20
5.1597 | 20
5.1667 | 20
5.1736 | 20
5.1806 | 20
5.1875 | 20
5.1944 | 20
5.2014 | 20
5.2083 | 20
5.2153 | 20
5.2222 | 20
5.2292 | 20
5.2361 | 20
5.2431 | 20
5.25 | 20
5.2569 | 20
5.2639 | 20
5.2708 | 20
5.2778 | 20
5.2847 | 20
5.2917 | 20
5.2986 | 20
5.3056 | 20
5.3125 | 20
5.3194 | 20
5.3264 | 20
5.3333 | 20
5.3403 | 20
5.3472 | 20
5.3542 | 20
5.3611 | 20
5.3681 | 20
5.375 | 20
5.3819 | 20
5.3889 | 20
5.3958 | 20
5.4028 | 20
5.4097 | 20
5.4167 | 20
5.4236 | 20
5.4306 | 20
5.4375 | 20
5.4444 | 20
5.4514 | 20
5.4583 | 20
5.4653 | 20
5.4722 | 20
5.4792 | 20
5.4861 | 20
5.4931 | 20
5.5 | 20
5.5069 | 20
5.5139 | 20
5.5208 | 20
5.5278 | 20
5.5347 | 20
5.5417 | 20
5.5486 | 20
5.5556 | 20
5.5625 | 20
5.5694 | 20
5.5764 | 20
5.5833 | 20
5.5903 | 20
5.5972 | 20
5.6042 | 20
5.6111 | 20
5.6181 | 20
5.625 | 20
5.6319 | 20
5.6389 | 20
5.6458 | 20
5.6528 | 20
5.6597 | 20
5.6667 | 20
5.6736 | 20
5.6806 | 20
5.6875 | 20
5.6944 | 20
5.7014 | 20
5.7083 | 20
5.7153 | 20
5.7222 | 20
5.7292 | 20
5.7361 | 20
5.7431 | 20
5.75 | 20
5.7569 | 20
5.7639 | 20
5.7708 | 20
5.7778 | 20
5.7847 | 20
5.7917 | 20
5.7986 | 20
5.8056 | 20
5.8125 | 20
5.8194 | 20
5.8264 | 20
5.8333 | 20
5.8403 | 20
5.8472 | 20
5.8542 | 20
5.8611 | 20
5.8681 | 20
5.875 | 20
5.8819 | 20
5.8889 | 20
5.8958 | 20
5.9028 | 20
5.9097 | 20
5.9167 | 20
5.9236 | 20
5.9306 | 20
5.9375 | 20
5.9444 | 20
5.9514 | 20
5.9583 | 20
5.9653 | 20
5.9722 | 20
5.9792 | 20
5.9861 | 20
5.9931 | 20
6 | 20
6.0069 | 20
6.0139 | 20
6.0208 | 20
6.0278 | 20
6.0347 | 20
6.0417 | 20
6.0486 | 20
6.0556 | 20
6.0625 | 20
6.0694 | 20
6.0764 | 20
6.0833 | 20
6.0903 | 20
6.0972 | 20
6.1042 | 20
6.1111 | 20
6.1181 | 20
6.125 | 20
6.1319 | 20
6.1389 | 20
6.1458 | 20
6.1528 | 20
6.1597 | 20
6.1667 | 20
6.1736 | 20
6.1806 | 20
6.1875 | 20
6.1944 | 20
6.2014 | 20
6.2083 | 20
6.2153 | 20
6.2222 | 20
6.2292 | 20
6.2361 | 20
6.2431 | 20
6.25 | 20
6.2569 | 20
6.2639 | 20
6.2708 | 20
6.2778 | 20
6.2847 | 20
6.2917 | 20
6.2986 | 20
6.3056 | 20
6.3125 | 20
6.3194 | 20
6.3264 | 20
6.3333 | 20
6.3403 | 20
6.3472 | 20
6.3542 | 20
6.3611 | 20
6.3681 | 20
6.375 | 20
6.3819 | 20
6.3889 | 20
6.3958 | 20
6.4028 | 20
6.4097 | 20
6.4167 | 20
6.4236 | 20
6.4306 | 20
6.4375 | 20
6.4444 | 20
6.4514 | 20
6.4583 | 20
6.4653 | 20
6.4722 | 20
6.4792 | 20
6.4861 | 20
6.4931 | 20
6.5 | 20
6.5069 | 20
6.5139 | 20
6.5208 | 20
6.5278 | 20
6.5347 | 20
6.5417 | 20
6.5486 | 20
6.5556 | 20
6.5625 | 20
6.5694 | 20
6.5764 | 20
6.5833 | 20
6.5903 | 20
6.5972 | 20
6.6042 | 20
6.6111 | 20
6.6181 | 20
6.625 | 20
6.6319 | 20
6.6389 | 20
6.6458 | 20
6.6528 | 20
6.6597 | 20
6.6667 | 20
6.6736 | 20
6.6806 | 20
6.6875 | 20
6.6944 | 20
6.7014 | 20
6.7083 | 20
6.7153 | 20
6.7222 | 20
6.7292 | 20
6.7361 | 20
6.7431 | 20
6.75 | 20
6.7569 | 20
6.7639 | 20
6.7708 | 20
6.7778 | 20
6.7847 | 20
6.7917 | 20
6.7986 | 20
6.8056 | 20
6.8125 | 20
6.8194 | 20
6.8264 | 20
6.8333 | 20
6.8403 | 20
6.8472 | 20
6.8542 | 20
6.8611 | 20
6.8681 | 20
6.875 | 20
6.8819 | 20
6.8889 | 20
6.8958 | 20
6.9028 | 20
6.9097 | 20
6.9167 | 20
6.9236 | 20
6.9306 | 20
6.9375 | 20
6.9444 | 20
6.9514 | 20
6.9583 | 20
6.9653 | 20
6.9722 | 20
6.9792 | 20
6.9861 | 20
6.9931 | 20
7 | 20

## Model
Model overview
Name: | Sumo1
Settings
Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
KNHx,NITO,AS | Half-saturation of NHx for NITOs (AS) | 0.5 | g N/m3
iCV,XB | COD of biodegradable substrate in volatile solids | 1.8 | g COD.g VSS-1
iCV,XU | COD of particulate unbiodegradable organics in volatile solids | 1.3 | g COD.g VSS-1
iCV,BIO | COD of biomass in volatile solids | 1.42 | g COD.g VSS-1
iCV,XE | COD of endogenous products in volatile solids | 1.42 | g COD.g VSS-1
μNITO | Maximum specific growth rate of NITOs | 0.9 | 1/d
μOHO | Maximum specific growth rate of OHOs | 4 | 1/d
KSB,AS | Half-saturation of readily biodegradable substrate for OHOs (AS) | 5 | g COD/m3
KO2,OHO,AS | Half-saturation of O2 for OHOs (AS) | 0.15 | g O2/m3
μCASTO | Maximum specific growth rate of CASTOs | 1 | 1/d
qPAO,PP | Maximum polyphosphate uptake rate of PAOs | 0.1 | 1/d
KPO4,PAO,AS | Half-saturation of PO4 for PAOs (AS) | 0.3 | g P/m3
qHYD | Rate of hydrolysis | 2 | 1/d
Ordinary heterotrophic organism kinetics (OHO)
Symbol | Name | Value | Unit | Comment
μOHO | Maximum specific growth rate of OHOs | 4 | 1/d
μFERM,OHO | Fermentation growth rate of OHOs | 0.3 | 1/d
bOHO | Decay rate of OHOs | 0.62 | 1/d
ηOHO,anox | Reduction factor for anoxic growth of OHOs | 0.6
KSB,AS | Half-saturation of readily biodegradable substrate for OHOs (AS) | 5 | g COD/m3
KO2,OHO,AS | Half-saturation of O2 for OHOs (AS) | 0.15 | g O2/m3
KVFA,AS | Half-saturation of VFA for OHOs (AS) | 0.5 | g COD/m3
KMEOL,OHO,AS | Half-saturation of methanol for OHOs (AS) | 0.1 | g COD/m3
KNOx,OHO,AS | Half-saturation of NOx for OHOs (AS) | 0.03 | g N/m3
KVFA,FERM,AS | Half-saturation of VFA in fermentation of OHOs (AS) | 50 | g COD/m3
KSB,ana,AS | Half-saturation of readily biodegradable substrate in fermentation by OHOs in mainstream (AS) | 5 | g COD/m3
KSB,ana,DIG | Half-saturation of readily biodegradable substrate in fermentation by OHOs in digester (AS) | 350 | g COD/m3
Anoxic methanol utilizer kinetics (MEOLO)
Symbol | Name | Value | Unit | Comment
μMEOLO | Maximum specific growth rate of MEOLOs | 1.3 | 1/d
bMEOLO | Decay rate of MEOLOs | 0.05 | 1/d
qMEOL | Rate of methanol degradation by MEOLOs under anaerobic conditions | 10 | 1/d | To clean up any remaining methanol in digesters without having to ferment mechanistically
KMEOL,AS | Half-saturation of methanol for MEOLOs (AS) | 0.5 | g COD/m3
KiO2,MEOLO,AS | Half-inhibition of O2 for MEOLOs (AS) | 0.05 | g O2/m3
KNOx,MEOLO,AS | Half-saturation of NOx for MEOLOs (AS) | 0.03 | g N/m3
Carbon storing organism kinetics (CASTO)
Symbol | Name | Value | Unit | Comment
μCASTO | Maximum specific growth rate of CASTOs | 1 | 1/d
qPAO,PP | Maximum polyphosphate uptake rate of PAOs | 0.1 | 1/d
μFERM,PAO | Fermentation growth rate of PAOs | 0.45 | 1/d
μPAO,lim | Maximum specific growth rate of PAOs under P limited | 0.49 | 1/d
bCASTO | Decay rate of CASTOs | 0.08 | 1/d | previously 0.05 (0.15 for Lopez et al. 2006; Hao et al., 2010)
bSTC | Rate of CASTOs maintenance on PHA and GLY | 0.07 | 1/d
bPP,ana | Rate of PAOs maintenance under anaerobic conditions (PP cleavage) | 0.005 | 1/d
qPAO,PHA | Rate of VFA storage into PHA for PAOs | 7 | 1/d
qGAO,GLY | Rate of VFA storage into glycogen for GAOs | 4 | 1/d
ηCASTO,anox | Reduction factor for anoxic growth of CASTOs | 0.66
ηbCASTO,anox | Reduction factor for anoxic decay of CASTOs | 0.5
ηbCASTO,ana | Reduction factor for anaerobic decay of CASTOs | 0.25
ηbSTC,anox | Reduction factor for anoxic maintenance of CASTOs on PHA and GLY | 0.66
ηbPP,aer | Reduction factor for aerobic maintenance of PAOs on PP | 0.25
ηbPP,anox | Reduction factor for anoxic maintenance of PAOs on PP | 0.5
KPO4,PAO,AS | Half-saturation of PO4 for PAOs (AS) | 0.3 | g P/m3
LogsatPO4,PAO,Slope | Logistic slope of PO4 uptake switching of PAO | 20 | g P-1.m3
KPHA,cle | Half-saturation of PHA for PAOs at PP cleavage | 0.1 | g COD.g COD-1
KPHA | Half-saturation of PHA for PAOs | 0.01 | g COD.g COD-1
KSTC | Half-saturation of PHA and GLY for PAOs | 0.1 | g COD.g COD-1
KO2,CASTO,AS | Half-saturation of O2 for CASTOs (AS) | 0.05 | g O2/m3
KNOx,CASTO,AS | Half-saturation of NOx for CASTOs (AS) | 0.03 | g N/m3
KVFA,CASTO,AS | Half-saturation of VFA storage for CASTOs (AS) | 5 | g COD/m3
KPP | Half-saturation of PP for PAOs | 0.01 | g COD.g COD-1
KiPP,PAO,max | Half-inhibition of maximum PP content of PAOs | 0.35 | g P.g COD-1
LoginhPP,PAO,slope | Slope of logistic inhibition term for PP/PAO | 100 | g COD.g P-1
KiPHA,PAO,max | Half-inhibition of maximum PHA content of PAOs | 0.6 | g COD.g COD-1
LoginhPHA,PAO,slope | Slope of logistic inhibition term for PHA/PAO | 100 | g COD.g COD-1
KMg,PAO,AS | Half-saturation of Mg (counter-ion in PP storage) for PAOs (AS) | 0.001 | g Mg/m3
KK,PAO,AS | Half-saturation of K (counter-ion in PP storage) for PAOs (AS) | 0.001 | g K/m3
KCa,PAO,AS | Half-saturation of Ca (counter-ion in PP storage) for PAOs (AS) | 0.001 | g Ca/m3
KPP,lim | Half-saturation of PP (nutrient) for PAOs under PO4 limitation (AS) | 0.002 | g P/m3
KiPO4,lim,AS | Half-inhibition of PO4 for PAOs under PO4 limitation (AS) | 0.005 | g P/m3
LogsatORP,PAO,Half | Logistic half-saturation of ORP switching in fermentation of PAO | -170 | mV | previously -100
LogsatORP,PAO,Slope | Logistic slope of ORP switching in fermentation of PAO | 0.1 | mV-1
ηbGLY,ana | Reduction factor for anaerobic maintenance of GAOs on glycogen | 0.1
KGLY | Half-saturation of glycogen for GAOs (AS) | 0.05 | g COD.g COD-1
KiGLY,GAO,max | Half-inhibition of maximum glycogen content of GAOs (AS) | 0.5 | g COD.g COD-1
LoginhGLY,GAO,slope | Slope of logistic inhibition term for GLY/GAO | 100 | g COD.g COD-1
LogsatORP,GAO,Half,15 | Half-value of ORP switch of glycogen storage by GAO at 15°C / 59°F | -30 | mV
LogsatORP,GAO,Half,25 | Half-value of ORP switch of glycogen storage by GAO at 25°C / 77°F | -110 | mV
LogsatORP,GAO,Slope | Logistic slope of ORP switching of GAOs | 0.035 | mV-1
Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KNHx,NITO,AS | Half-saturation of NHx for NITOs (AS) | 0.5 | g N/m3
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
μNITO | Maximum specific growth rate of NITOs | 0.9 | 1/d
bNITO | Decay rate of NITOs | 0.17 | 1/d
KCO2,NITO,AS | Half-saturation of CO2 for NITOs (AS) | 12 | g TIC/m3 | if pH is not calculated
KCO2,NITO,sidestream | Half-saturation of CO2 for NITOs (Sidestream) | 48 | g TIC/m3 | if pH is not calculated
KCO2,NITO,pH,AS | Half-saturation of bicarbonate for NITOs (AS) | 1 | mmol [HCO3-]/L | if pH is calculated
KCO2,NITO,pH,sidestream | Half-saturation of bicarbonate for NITOs (Sidestream) | 4 | mmol [HCO3-]/L | if pH is calculated
KO2,NITO,sidestream | Half-saturation of O2 for NITOs (Sidestream) | 0.5 | g O2/m3
KNOx,NITO,AS | Half-saturation of NOx for NITOs (AS) | 0.03 | g N/m3
KiNH3,NITO,pH,AS | Half-inhibition of NH3 for NITOs (AS) | 9999 | mol [NH3].L-1 | if pH is calculated
Acidoclastic methanogen kinetics (AMETO)
Symbol | Name | Value | Unit | Comment
μAMETO | Maximum specific growth rate of AMETO | 0.3 | 1/d
bAMETO | Decay rate of AMETOs | 0.03 | 1/d
KVFA,AMETO,AS | Half-saturation of VFA for AMETOs (AS) | 400 | g COD/m3 | Non-pH
KiVFA,AMETO,AS | Haldane inhibition of VFA for AMETOs (AS) | 99999 | g COD/m3 | Non-pH
KiO2,AMETO,AS | Half-inhibition of O2 for AMETOs (AS) | 0.05 | g O2/m3
KNOx,AMETO,AS | Half-saturation of NOx for AMETOs (AS) | 0.05 | g N/m3
pHlow,AMETO | pH inhibition low value for AMETOs | 4.5 | pHunit
pHhigh,AMETO | pH inhibition high value for AMETOs | 9.5 | pHunit
Hydrogenotrophic methanogen kinetics (HMETO)
Symbol | Name | Value | Unit | Comment
μHMETO | Maximum specific growth rate of HMETO | 1.3 | 1/d
bHMETO | Decay rate of HMETOs | 0.13 | 1/d
KH2,HMETO,AS | Half-saturation of H2 for HMETOs (AS) | 0.1 | g COD/m3
KiO2,HMETO,AS | Half-inhibition of O2 for HMETOs (AS) | 0.05 | g O2/m3
KNOx,HMETO,AS | Half-saturation of NOx for HMETOs (AS) | 0.05 | g N/m3
pHlow,HMETO | pH inhibition low value for HMETOs | 4.5 | pHunit
pHhigh,HMETO | pH inhibition high value for HMETOs | 9.5 | pHunit
Precipitation kinetics
Symbol | Name | Value | Unit | Comment
qCaCO3,PREC | Rate of CaCO3 precipitation | 0.1 | g/m3/d
qCaCO3,DISS | Rate of CaCO3 dissolution | 0.1 | g/m3/d
qSTR,PREC | Rate of struvite precipitation | 10 | g/m3/d
qSTR,DISS | Rate of struvite dissolution | 10 | g/m3/d
qACP,PREC | Rate of ACP precipitation | 5 | g/m3/d
qACP,DISS | Rate of ACP dissolution | 5 | g/m3/d
qBSH,PREC | Rate of brushite precipitation | 500 | g/m3/d
qBSH,DISS | Rate of brushite dissolution | 500 | g/m3/d
qVivi,PREC | Rate of vivianite precipitation | 0.01 | g/m3/d
qVivi,DISS | Rate of vivianite dissolution | 0.01 | g/m3/d
KSTR,DISS | Half-saturation of struvite redissolution | 0.01 | g TSS/m3
KACP,DISS | Half-saturation of ACP redissolution | 0.01 | g TSS/m3
KBSH,DISS | Half-saturation of brushite redissolution | 0.01 | g TSS/m3
KCaCO3,DISS | Half-saturation of CaCO3 redissolution | 0.01 | g TSS/m3
KVivi,DISS | Half-saturation of vivianite redissolution | 0.01 | g TSS/m3
HFO kinetics
Symbol | Name | Value | Unit | Comment
qHFOH,AGING | Rate of XHFO,H aging | 250 | 1/d
qHFOL,AGING | Rate of XHFO,L aging | 1 | 1/d
qP,HFO,COPREC | Rate of P binding and coprecipitation on XHFO,H | 150 | 1/d
qP,HFO,BIND | Rate of P binding on XHFO,L | 1 | 1/d
qHFOH,DESORP | Rate of XHFO,H,P desorption | 100 | 1/d
qHFOL,DESORP | Rate of XHFO,L,P desorption | 10 | 1/d
qHFO,DISS | Rate of XHFO,H,P,old and XHFO,L,P,old redissolution | 100 | 1/d
qHFO,RED | Rate of HFO reduction with organics | 2 | 1/d
LogsatORP,HFO,Half | Logistic half-saturation of ORP switching in HFO reduction | -100 | mV
LogsatORP,HFO,Slope | Logistic slope of ORP switching in HFO reduction | 0.1
qFe2,OX | Rate of Fe2 oxidation | 1 | 1/d
KiP,HFO,DISS | Half-inhibition of PO4 in HFO redissolution | 0.01 | g P/m3
KiP,HFO,DESORP | Half-inhibition of PO4 in HFO desorption | 0.1 | g P/m3
KP,HFO,BIND | Half-saturation of PO4 in binding on HFO | 0.1 | g P/m3
HAO kinetics
Symbol | Name | Value | Unit | Comment
qHAOH,AGING | Rate of XHAO,H aging | 100 | 1/d
qHAOL,AGING | Rate of XHAO,L aging | 1 | 1/d
qP,HAO,COPREC | Rate of P binding and coprecipitation on XHAO,H | 50 | 1/d
qP,HAO,BIND | Rate of P binding on XHAO,L | 1 | 1/d
qHAOH,DESORP | Rate of XHAO,H,P desorption | 100 | 1/d
qHAOL,DESORP | Rate of XHAO,L,P desorption | 10 | 1/d
qHAO,DISS | Rate of XHAO,H,P,old and XHAO,L,P,old redissolution | 100 | 1/d
KP,HAO,BIND | Half-saturation of PO4 for binding on HAO | 0.1 | g P/m3
KiP,HAO,DISS | Half-inhibition of PO4 in HAO redissolution | 0.001 | g P/m3
KiP,HAO,DESORP | Half-inhibition of PO4 in HAO desorption | 0.1 | g P/m3
Common switches
Symbol | Name | Value | Unit | Comment
KNHx,BIO,AS | Half-saturation of NHx as nutrient for biomasses (AS) | 0.005 | g N/m3
KPO4,BIO,AS | Half-saturation of PO4 as nutrient for biomasses (AS) | 0.002 | g P/m3
KCO2,BIO,AS | Half-saturation of CO2 for biomasses (except NITOs) | 1.2 | g TIC/m3
KCAT,AS | Half-saturation of strong cations (as Na+) | 0.1 | g Na/m3
KAN,AS | Half-saturation of strong anions (as Cl-) | 0.1 | g Cl/m3
KMg,BIO,AS | Half-saturation of Mg for biomasses (AS) | 0.0001 | g Mg/m3
KCa,BIO,AS | Half-saturation of Ca for biomasses (AS) | 0.0001 | g Ca/m3
ηb,anox | Reduction factor for anoxic decay | 0.5
ηb,ana | Reduction factor for anaerobic decay | 0.25
mtox,anox | Toxicity factor of anaerobes under anoxic conditions | 5
mtox,aer | Toxicity factor of anaerobes under aerobic conditions | 10
mtox,ana,max | Toxicity factor of aerobes under anaerobic conditions (maximum) | 10
pHlow | pH inhibition low value | 3 | pHunit
pHhigh | pH inhibition high value | 11 | pHunit
Conversion kinetics
Symbol | Name | Value | Unit | Comment
qHYD | Rate of hydrolysis | 2 | 1/d
ηHYD,anox | Reduction factor for anoxic hydrolysis | 0.5
ηHYD,ana | Reduction factor for anaerobic hydrolysis | 0.5
qFLOC | Rate of flocculation | 50 | 1/d
KFLOC,AS | Half-saturation of colloids in flocculation (AS) | 0.001 | g COD.g COD-1
KHYD,AS | Half-saturation of particulates in hydrolysis (AS) | 0.05 | g COD.g COD-1
qAMMON | Rate of ammonification | 0.05 | 1/d
qSPB | Rate of soluble biodegradable organic P conversion | 0.5 | 1/d
qXE | Rate of endogenous decay products conversion | 0.007 | 1/d
qASSIM | Rate of assimilative nutrient production | 1 | 1/d
KiNHx,ASSIM,AS | Half-inhibition of NHx in NOx assimilative reduction | 0.0005 | g N/m3
KNOx,ASSIM,AS | Half-saturation of NOx in NOx assimilative reduction (AS) | 0.001 | g N/m3
Parameters for half saturation coefficients in biofilms
Symbol | Name | Value | Unit | Comment
fKS,biofilm | Diffusion factor for half-saturation coefficients | 0.1
Temperature dependency
Symbol | Name | Value | Unit | Comment
θμ,OHO | Arrhenius coefficient for OHO growth | 1.04
θFERM,OHO | Arrhenius coefficient for fermentation (OHO) | 1.04
θb,OHO | Arrhenius coefficient for OHO decay | 1.03
θμ,MEOLO | Arrhenius coefficient for MEOLO growth | 1.06
θb,MEOLO | Arrhenius coefficient for MEOLO decay | 1.03
θμ,CASTO | Arrhenius coefficient for CASTO growth | 1.04
θμ,PAO,lim | Arrhenius coefficient for PAO growth (P limited) | 1.04
θFERM,PAO | Arrhenius coefficient for fermentation (PAO) | 1.04
θq,PAO,PP | Arrhenius coefficient for PP storage | 1.04
θq,PAO,PHA | Arrhenius coefficient for PHA storage | 1.04
θb,CASTO | Arrhenius coefficient for CASTO decay | 1.03
θb,STC | Arrhenius coefficient for PHA and GLY storage use for maintenance | 1.06 |  | based on Lopez Vazquez et al., 2009
θb,PP,ana | Arrhenius coefficient for anaerobic PP storage | 1.03
θq,GAO,GLY | Arrhenius coefficient for GLY storage | 1.072
θμ,NITO | Arrhenius coefficient for NITO growth | 1.072
θb,NITO | Arrhenius coefficient for NITO decay | 1.03
θμ,AMETO | Arrhenius coefficient for AMETO growth | 1.03
θb,AMETO | Arrhenius coefficient for AMETO decay | 1.03
θμ,HMETO | Arrhenius coefficient for HMETO growth | 1.03
θb,HMETO | Arrhenius coefficient for HMETO decay | 1.03
θq,FLOC | Arrhenius coefficient for flocculation | 1.03
θq,HYD | Arrhenius coefficient for hydrolysis | 1.03
θq,AMMON | Arrhenius coefficient for ammonification | 1.03
θq,SPB | Arrhenius coefficient for PO4 conversion | 1.03
θq,XE | Arrhenius coefficient endogenous residual conversion | 1.03
θq,ASSIM | Arrhenius coefficient assimilative kinetics | 1.03
θq,Fe2,OX | Arrhenius coefficient for ferrous iron oxidation kinetics | 1.04
θq,HFO,RED | Arrhenius coefficient for ferric iron reduction kinetics | 1.04
Tbase | Arrhenius base temperature | 20 | Co
Stoichiometric yields
Symbol | Name | Value | Unit | Comment
YOHO,VFA,ox | Yield of OHOs on VFA under aerobic conditions | 0.6 | g XOHO.g SVFA-1
YOHO,VFA,anox | Yield of OHOs on VFA under anoxic conditions | 0.45 | g XOHO.g SVFA-1
YOHO,SB,ox | Yield of OHOs on readily biodegradable substrate under aerobic conditions | 0.67 | g XOHO.g SB-1
YOHO,SB,anox | Yield of OHOs on readily biodegradable substrate under anoxic conditions | 0.54 | g XOHO.g SB-1
YOHO,SB,ana | Yield of OHOs on readily biodegradable substrate under anaerobic conditions | 0.1 | g XOHO.g SB-1
YOHO,H2,ana,high | Yield of H2 production in fermentation with high VFA concentration (OHO) | 0.35 | g SH2.g SB-1
YOHO,H2,ana,low | Yield of H2 production in fermentation with low VFA concentration (OHO) | 0.1 | g SH2.g SB-1
YOHO,SMEOL,ox | Yield of OHOs on methanol under aerobic conditions | 0.4 | g XOHO.g SMEOL-1
YMEOLO | Yield of MEOLOs on methanol | 0.4 | g XMEOLO.g SMEOL-1
YCASTO,PHA,ox | Yield of CASTOs on PHA under aerobic conditions | 0.639 | g XCASTO.g XPHA-1
YCASTO,PHA,anox | Yield of CASTOs on PHA under anoxic conditions | 0.52 | g XCASTO.g XPHA-1
YCASTO,SB,ana | Yield of CASTOs on readily biodegradable substrate under anaerobic conditions | 0.1 | g XCASTO.g SB-1
YCASTO,H2,ana,high | Yield of H2 production in fermentation with high VFA concentration (CASTO) | 0.35 | g SH2.g SB-1
YCASTO,H2,ana,low | Yield of H2 production in fermentation with low VFA concentration (CASTO) | 0.1 | g SH2.g SB-1
YPP,CASTO,ox | Yield of CASTOs consumed per PP uptake under aerobic conditions | 0.33 | g XCASTO.g XPP-1
YPP,CASTO,anox | Yield of CASTOs consumed per PP uptake under anoxic conditions | 0.23 | g XCASTO.g XPP-1
fP,VFA | Ratio of P released per VFA stored | 0.65 | g XPP.g SVFA-1
iTSS,PP | TSS content of PP | 3.5161 | g XTSS.g XPP-1
YCASTO,GLY,ox | Yield of CASTOs on glycogen under aerobic conditions | 0.6 | g XCASTO.g XGLY-1
YCASTO,GLY,anox | Yield of CASTOs on glycogen under anoxic conditions | 0.5 | g XCASTO.g XGLY-1
YNITO | Yield of NITOs on NHx | 0.24 | g XNITO.g SNHx-1
YAMETO | Yield of AMETOs on VFA | 0.1 | g XAMETO.g SVFA-1
YHMETO | Yield of HMETOs on H2 | 0.1 | g XHMETO.g SH2-1
General stoichiometry
Symbol | Name | Value | Unit | Comment
fE | Fraction of endogenous products produced in biomass decay | 0.08 | g XE.g XBIO-1
iN,BIO | N content of biomasses | 0.07 | g N.g COD-1
iN,XE | N content of endogenous products | 0.06 | g N.g COD-1
iN,CB | N content of colloidal biodegradable substrate | 0.03 | g N.g COD-1
iN,CU | N content of colloidal unbiodegradable organics | 0.01 | g N.g COD-1
iN,SU | N content of soluble unbiodegradable organics | 0.05 | g N.g COD-1
iN,XSTR | N content of struvite | 0.057076 | g N.g TSS-1 | A_MN/M_MSTR
iP,BIO | P content of biomasses | 0.02 | g P.g COD-1
iP,CB | P content of colloidal biodegradable substrate | 0.005 | g P.g COD-1
iP,CU | P content of colloidal unbiodegradable organics | 0.005 | g P.g COD-1
iP,SU | P content of soluble unbiodegradable organics | 0.002 | g P.g COD-1
iP,XSTR | P content of struvite | 0.12621 | g P.g TSS-1 | A_MP/M_MSTR
iP,XACP | P content of ACP | 0.16207 | g P.g TSS-1 | 2*A_MP/M_MACP
iP,XBSH | P content of BSH | 0.17999 | g P.g TSS-1 | 2*A_MP/M_MACP
iP,XVivi | P content of vivianite | 0.1235 | g P.g TSS-1 | 2*A_MP/M_MVivi
iCV,XB | COD of biodegradable substrate in volatile solids | 1.8 | g COD.g VSS-1
iCV,XU | COD of particulate unbiodegradable organics in volatile solids | 1.3 | g COD.g VSS-1
iCV,BIO | COD of biomass in volatile solids | 1.42 | g COD.g VSS-1
iCV,XE | COD of endogenous products in volatile solids | 1.42 | g COD.g VSS-1
iCV,VFA | COD of VFA in volatile solids | 1.066 | g COD.g VS-1
iCV,SB | COD of readily biodegradable substrate in volatile solids | 1.066 | g COD.g VS-1
iCV,MEOL | COD of methanol in volatile solids | 1.5 | g COD.g VS-1
iCV,SU | COD of soluble unbiodegradable organics in volatile solids | 0.926 | g COD.g VS-1
iCV,CB | COD of colloidal biodegradable substrate in volatile solids | 1.8 | g COD.g VS-1
iCV,CU | COD of colloidal unbiodegradable organics in volatile solids | 1.3 | g COD.g VS-1
iCV,PHA | COD of PHA in volatile solids | 1.67 | g COD.g VSS-1
iCV,GLY | COD of glycogen in volatile solids | 1.19 | g COD.g VSS-1
iCIT,BIO | Inorganic carbon content of biomass | 0.352 | g TIC.g COD-1 | C5H7O2N: 32 g COD/mol C
iCIT,SB | Inorganic carbon content of SB and SU | 0.286 | g TIC.g COD-1 | C5H7O2N: 32 g COD/mol C
iCIT,MEOL | Inorganic carbon content of methanol | 0.25 | g TIC.g COD-1 | CH4O: 48 g COD/mol C
iCIT,CH4 | Inorganic carbon content of CH4 | 0.188 | g TIC.g COD-1 | CH4: 64 g COD/mol C
iCIT,VFA | Inorganic carbon content of VFA | 0.375 | g TIC.g COD-1 | C2H4O2: 32 g COD/mol C
iCIT,PHA | Inorganic carbon content of PHA | 0.333 | g TIC.g COD-1 | H[C4H6O2]nOH: 36 g COD/mol C
iCIT,GLY | Inorganic carbon content of glycogen | 0.375 | g TIC.g COD-1 | [C6H10O5]n: 32 g COD/mol C
iINORG | Inorganic content of biomass | 0.11 | g TSS.g COD-1 | 15% of VSS - Ekama
iCa,PP | Calcium content of PP | 0.1 | mol Ca.mol P-1 | sum of the charges of Ca, Mg and K content of PP…
iMg,PP | Magnesium content of PP | 0.35 | mol Mg.mol P-1 | ...should be equal to 1…
iK,PP | Potassium content of PP | 0.1 | mol K.mol P-1 | ...e.g.: 2*0.1 + 2*0.35 + 1*0.1=1
fNa | Fraction of Na in NaCl | 0.39337 | g Na.g NaCl-1
iCa,INORG | Ca content of XINORG | 0.05 | g Ca.g TSS-1
iMg,INORG | Mg content of XINORG | 0.05 | g Mg.g TSS-1
fVFA,DM | fraction of SVFA not volatilized in Dry Matter analysis | 50 | %
BOD stoichiometry
Symbol | Name | Value | Unit | Comment
YBOD,ult | Yield on ultimate BOD | 0.95 | g O2.g COD-1
fS,BOD5,BODult | Fraction of BOD5 to ultimate BOD in soluble biodegradable substrates | 0.9
fC,BOD5,BODult | Fraction of BOD5 to ultimate BOD in colloidal biodegradable substrates | 0.6
fX,BOD5,BODult | Fraction of BOD5 to ultimate BOD in particulate biodegradable substrates | 0.5
HFO stoichiometry
Symbol | Name | Value | Unit | Comment
ASFHFO,H | Active site factor for HFO,H | 1.2 | mol P.mol Fe-1
ASFHFO,L | Active site factor for HFO,L | 0.2 | mol P.mol Fe-1
fH2O,HFO,TSS | Fraction of H2O loss in TSS test for HFO | 0.0829 | g H2O.g FeOH-1
fH2O,HFO,VSS | Fraction of H2O loss in VSS test for HFO | 0.17 | g H2O.g FeOH-1 | Me(OH)3 -> Me2O3 + 3H2O
HAO stoichiometry
Symbol | Name | Value | Unit | Comment
ASFHAO,H | Active site factor for HAO,H | 1 | mol P.mol Al-1
ASFHAO,L | Active site factor for HAO,L | 0.1 | mol P.mol Al-1
fH2O,HAO,TSS | Fraction of H2O loss in TSS test for HAO | 0.17322 | g H2O.g AlOH3-1
fH2O,HAO,VSS | Fraction of H2O loss in VSS test for HAO | 0.34643 | g H2O.g AlOH3-1 | 2Al(OH)3 -> Al2O3 + 3H2O
Parameters for gas transfer
Symbol | Name | Value | Unit | Comment
kL,GO2,bub | Liquid-side mass transfer coefficient of O2 for gas bubbles | 13 | m/d
kL,GO2,sur | Liquid-side mass transfer coefficient of O2 at liquid surface | 7.6 | m/d
fkL,GN2 | Correction factor for mass transfer of N2 | 100 | %
fkL,GCO2 | Correction factor for mass transfer of CO2 | 100 | %
fkL,GCH4 | Correction factor for mass transfer of CH4 | 100 | %
fkL,GH2 | Correction factor for mass transfer of H2 | 100 | %
fkL,GNH3 | Correction factor for mass transfer of NH3 | 5 | % | Used to compensate for the high solubility of NH3 gas
qALPHA | Sludge retention-based alpha improvement rate component | 0.0017 | m3.g-1.d-1
SALPHA,sat | Alpha indicator saturation value | 1
KSO2,ALPHA | Half-saturation of dissolved oxygen for anoxic/anaerobic alpha enhancement | 0.05 | g O2/m3
fSO2,max,ALPHA | Maximum anaerobic/anoxic alpha enhancement factor (at 0 mg/l DO) | 2.5
coeffdamp,ALPHA | Coefficient of alpha first order limitation damping term | 3
powdamp,ALPHA | Power of alpha first order limitation damping term | 9
slTSS,α,def | Slope of solids-related alpha correction, default | -0.0711 | m3.kg-1
slTSS,α,coarse | Slope of solids-related alpha correction, coarse bubbles | -0.0474 | m3.kg-1
coefflead,TSS,α,mech | Leading coefficient of solids-related alpha correction, mechanical aeration | -0.000787 | (kg.m-3)-2
coefflin,TSS,α,mech | Linear coefficient of solids-related alpha correction, mechanical aeration | 0.0232 | m3.kg-1
constTSS,α,mech | Constant of solids-related alpha correction, mechanical aeration | 0.877
Oxidation-reduction potential constants
Symbol | Name | Value | Unit | Comment
ORPbase | Base ORP value | -300 | mV
ORPmax,SO2 | ORP max for dissolved oxygen | 300 | mV
ORPmax,SNOx | ORP max for dissolved nitrate | 70 | mV
KORP,SO2 | Half-saturation of dissolved oxygen for ORP | 0.05 | g O2/m3
KORP,SNOx | Half-saturation of NOx for anoxic ORP | 0.1 | g N/m3
KORP,H2,CH4 | Half-saturation of dissolved hydrogen and methane for anaerobic ORP | 5 | g COD/m3
IS correction factor
Symbol | Name | Value | Unit | Comment
ISlim | IS cut-off threshold for Davies activity coefficient correction | 0.2 | ISunit | The fmono/fdi/ftri curves have minima at 0.3 and literally couldn't be used above that
SlopeIS,corr | Slope of correction | -0.001
TOC calculation coefficients
Symbol | Name | Value | Unit | Comment
fTOC,1 | fTOC,1 | 0.33445 | g C.g COD-1
fTOC,2 | fTOC,2 | 2.4247 | g C.m-3
Interstitial water content
Symbol | Name | Value | Unit | Comment
iiw,BIO | Interstitial water of biomass in volatile solids | 2.33 | g H2O.g VS-1 | Assuming 70% of biomass cytoplasm is water
Vicinal water content
Symbol | Name | Value | Unit | Comment
ivw,XB | Vicinal water of biodegradable substrate in volatile solids | 0.052 | g H2O.g VS-1 | Assuming 5% of H2O is associated with vicinal water for these organics
ivw,XU | Vicinal water of particulate unbiodegradable organics in volatile solids | 0.052 | g H2O.g VS-1
ivw,BIO | Vicinal water of biomass in volatile solids | 0.052 | g H2O.g VS-1
ivw,XE | Vicinal water of endogenous products in volatile solids | 0.052 | g H2O.g VS-1
ivw,CB | Vicinal water of colloidal biodegradable substrate in volatile solids | 0.052 | g H2O.g VS-1
ivw,CU | Vicinal water of colloidal unbiodegradable organics in volatile solids | 0.052 | g H2O.g VS-1
ivw,PHA | Vicinal water of PHA in volatile solids | 0.052 | g H2O.g VS-1
ivw,GLY | Vicinal water of glycogen in volatile solids | 0.052 | g H2O.g VS-1
ivw,EPS | Vicinal water correction of EPS in volatile solids | 0.052 | g H2O.g VS-1
Water of Hydration content
Symbol | Name | Value | Unit | Comment
iwh,XB | Water of hydration of biodegradable substrate in volatile solids | 0.11 | g H2O.g VS-1 | Assuming 10% of H2O is associated with water of hydration
iwh,XU | Water of hydration of particulate unbiodegradable organics in volatile solids | 0.11 | g H2O.g VS-1
iwh,BIO | Water of hydration of biomass in volatile solids | 0.11 | g H2O.g VS-1
iwh,XE | Water of hydration of endogenous products in volatile solids | 0.11 | g H2O.g VS-1
iwh,PHA | Water of hydration of PHA in volatile solids | 0.17 | g H2O.g VS-1 | Assuming 15% of H2O is associated with water of hydration
iwh,GLY | Water of hydration of glycogen in volatile solids | 0.17 | g H2O.g VS-1
iwh,EPS | Water of hydration correction of EPS in volatile solids | 0.33 | g H2O.g VS-1 | Assuming 25% of H2O is associated with water of hydration

## Plantwide
Unit overview
Name: | Plantwide
Sumo name:
Category: | Other units
Unit: | PlantFactory
Type: | PlantFactory
Settings

## Energy center
Unit overview
Name: | Energy center
Sumo name: | EnergyCenter
Category: | Other units
Unit: | Energy center
Type: | Energy center
Settings
Periphery consumer settings
Symbol | Name | Value | Unit | Comment
Pel,vent | Ventilation fixed power demand | 4.6667 | kW
Pel,water | Water supply fixed power demand | 14.4475 | kW
Pel,misc | Miscellaneous fixed power demand | 2.4546 | kW
Other variable consumers
Symbol | Name | Value | Unit | Comment
esize,ovc | Variable specific energy demand based on PE load | 0 | kWh/PED.a
eflow,ovc | Variable specific energy demand based on flow | 0 | Wh/m3
eCOD,ovc | Variable specific energy demand based on COD load | 0 | Wh/kg COD
esolids,ovc | Variable specific energy demand based on solids load | 0 | Wh/kg TSS
Other fixed consumers
Symbol | Name | Value | Unit | Comment
Pel,other | Additional fixed other power demand | 0 | kW
Pel,special | Additional fixed special power demand | 0 | kW
Photovoltalic power producers
Symbol | Name | Value | Unit | Comment
pvp | Photovoltaic peak power | 0 | kW
dy_0 | Day of the year starting value | 0 | d
msrh | Midsummer sunrise hour | 5 | h
mssh | Midsummer sunset hour | 21 | h
osp | Off season peak power factor | 30 | %
wpv | Weather factor photovoltaic | 50 | % | 1 = Sunny every day, 0 = total Darkness
Other producers
Symbol | Name | Value | Unit | Comment
Pel,prod,other | Other fixed power production | 0 | kW

## Cost center
Unit overview
Name: | Cost center
Sumo name: | CostCenter
Category: | Other units
Unit: | Cost center
Type: | Cost center
Settings
Specific prices for purchase
Symbol | Name | Value | Unit | Comment
eEL,spec,flow | Specific energy consumption based on flow | 0.21 | kWh.m-3
PriceEL,purch | Electricity price when purchased | 0.00012 | kUSD.kWh-1
Water purchase price
Symbol | Name | Value | Unit | Comment
Pricewater,cons | Additional water usage cost | 0.0001 | kUSD.m-3
Polymer purchase price
Symbol | Name | Value | Unit | Comment
PricePolymer | Polymer purhase cost | 0.003 | kUSD.kg-1
Disposal prices
Symbol | Name | Value | Unit | Comment
Pricescreenings,disp | Screenings disposal cost based on solids mass | 0.5 | kUSD.TSS ton-1
Pricegrit,disp | Grit disposal cost based on solids mass | 0.5 | kUSD.TSS ton-1
Pricegrease,disp | Grease disposal cost based on solids mass | 0.5 | kUSD.m-3
Pricesludge,disp | Sludge disposal cost based on solids mass | 0.5 | kUSD.TSS ton-1
Product sale prices
Symbol | Name | Value | Unit | Comment
PriceXCaCO3,sale | Calcium carbonate (CaCO3) sale price | 0.05 | kUSD.TSS ton-1
PriceXACP,sale | Amorphous calcium phosphate (ACP) sale price | 0.03 | kUSD.TSS ton-1
PriceXSTR,sale | Struvite (STR) sale price | 0.055 | kUSD.TSS ton-1
PriceXVivi,sale | Vivianite (Vivi) sale price | 0.05 | kUSD.TSS ton-1

## Influent (2)
Unit overview
Name: | Influent
Sumo name: | Influent1
Category: | Flow elements
Unit: | Influent
Type: | Sumo1 concentration based influent
Settings
Influent specifications
Symbol | Name | Value | Unit | Comment
TKN | Total Kjeldahl nitrogen (TKN) | 56.5 | g N/m3
Q | Flow rate | 24000 | m3/d
TCOD | Total chemical oxygen demand | 420 | g COD/m3
TP | Total phosphorus | 4.3 | g P/m3
T | Temperature | 20 | °C
Influent fractions
Symbol | Name | Value | Unit | Comment
frVSS,TSS | Fraction of VSS/TSS | 84.8649 | %
frSCCOD,TCOD | Fraction of filtered COD (SCCOD, 1.5 µm, incl. colloids) in total COD | 40.4762 | %
frSCOD,TCOD | Fraction of flocculated filtered (SCOD, wo colloids) COD in total COD | 20.2381 | %
frVFA,SCCOD | Fraction of VFA in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.7647 | %
frSU,SCCOD | Fraction of soluble unbiodegradable organics (SU) in filtered COD (SCCOD, 1.5 µm, incl. colloids) | 11.7647 | % | Fraction of filtered COD, not total COD!
frXU,TCOD | Fraction of particulate unbiodegradable organics (XU) in total COD | 14 | %
frXOHO,TCOD | Fraction of heterotrophs (OHO) in total COD | 5 | %
frXE,XOHO | Fraction of endogenous products (XE) of OHOs | 20 | %
frCU,CCOD | Fraction of colloidal unbiodegradable organics (CU) in colloidal COD | 20 | %
frSNHx,TKN | Fraction of NHx in total Kjeldahl nitrogen (TKN) | 69.7674 | %
frSPO4,TP | Fraction of PO4 in total phosphorus (TP) | 58.1395 | %
frN,SB | Fraction of N in readily biodegradable substrate (SB) | 4 | %
frN,XU | Fraction of N in particulate unbiodegradable substrate (XU) | 1 | %
frP,SB | Fraction of P in readily biodegradable substrate (SB) | 1 | %
frP,XU | Fraction of P in particulate unbiodegradable substrate (XU) | 0.1 | %
Alpha indicator - SCCOD correlation parameters
Symbol | Name | Value | Unit | Comment
KI,SCCOD,ALPHA | Half-value in filtered COD-based alpha indicator correlation | 165 | g COD/m3
slSCCOD,ALPHA | Slope of filtered COD-based alpha indicator correlation | 0.1
MinSCCOD,ALPHA | Minimum of filtered COD-based alpha indicator correlation | 0
Maxww,SCCOD,ALPHA | Maximum of filtered COD-based alpha indicator correlation, waste water | 0.5
expcw,SCCOD,ALPHA | Clean water exponent of filtered COD-based alpha indicator correlation | 0.05
Ionic components
Symbol | Name | Value | Unit | Comment
SCa | Calcium | 150 | g Ca/m3
SMg | Magnesium | 15 | g Mg/m3
SK | Potassium | 16 | g K/m3
SAN | Other strong anions (as Cl-) | 300 | g Cl/m3
SCAT | Other strong cations (as Na+) | 109.9 | g Na/m3
Other influent constituents (usually zero)
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) | 1e-40 | g O2/m3
SMEOL | Methanol (MEOL) | 1e-40 | g COD/m3
XPHA | Stored polyhydroxyalkanoates (PHA) | 1e-40 | g COD/m3
XGLY | Stored glycogen (GLY) | 1e-40 | g COD/m3
XE,ana | Anaerobic endogenous decay products | 1e-40 | g COD/m3
XCASTO | Carbon storing organisms (CASTO) | 0.1 | g COD/m3
XMEOLO | Anoxic methanol utilizers (MEOLO) | 0.1 | g COD/m3
XNITO | Aerobic nitrifying organisms (NITO) | 0.1 | g COD/m3
XAMETO | Acidoclastic methanogens (AMETO) | 0.1 | g COD/m3
XHMETO | Hydrogenotrophic methanogens (HMETO) | 0.1 | g COD/m3
SNOx | Nitrate and nitrite (NOx) | 1e-40 | g N/m3
SN2 | Dissolved nitrogen (N2) | 16 | g N/m3
XPP | Stored polyphosphate (PP) | 1e-40 | g P/m3
SCH4 | Dissolved methane (CH4) | 1e-40 | g COD/m3
SH2 | Dissolved hydrogen (H2) | 1e-40 | g COD/m3
SFe3 | Ferric ion (Fe3) | 1e-40 | g Fe/m3
SFe2 | Ferrous ion (Fe2) | 1e-40 | g Fe/m3
SAl | Aluminium (Al) | 1e-40 | g Al/m3
XHFO,old | Aged unused hydrous ferric oxide (HFO,old) | 1e-40 | g Fe/m3
XHFO,H,P | P-bound hydrous ferric oxide, high surface (HFO,H,P) | 1e-40 | g Fe/m3
XHFO,L,P | P-bound hydrous ferric oxide, low surface (HFO,L,P) | 1e-40 | g Fe/m3
XHFO,H,P,old | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) | 1e-40 | g Fe/m3
XHFO,L,P,old | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) | 1e-40 | g Fe/m3
XHAO,old | Aged unused hydrous aluminium oxide (HAO,old) | 1e-40 | g Al/m3
XHAO,H,P | P-bound hydrous aluminium oxide, high surface (HAO,H,P) | 1e-40 | g Al/m3
XHAO,L,P | P-bound hydrous aluminium oxide, low surface (HAO,L,P) | 1e-40 | g Al/m3
XHAO,H,P,old | Aged P-bound hydrous aluminium oxide, high surface (HAO,H,P,old) | 1e-40 | g Al/m3
XHAO,L,P,old | Aged P-bound hydrous aluminium oxide, low surface (HAO,L,P,old) | 1e-40 | g Al/m3
XCaCO3 | Calcium carbonate (CaCO3) | 1e-40 | g TSS/m3
XACP | Amorphous calcium phosphate (ACP) | 1e-40 | g TSS/m3
XBSH | Brushite (BSH) | 1e-40 | g TSS/m3
XSTR | Struvite (STR) | 1e-40 | g TSS/m3
XVivi | Vivianite (Vivi) | 1e-40 | g TSS/m3
Total inorganic carbon (CO2)
Symbol | Name | Value | Unit | Comment
SCO2 | Total inorganic carbon (CO2) | 90 | g TIC/m3
Mixing - precipitation parameters
Symbol | Name | Value | Unit | Comment
G | Average velocity gradient in mixing tank | 425 | 1/s
KG,HFO | Half-saturation for G value for HFO | 45 | 1/s
KG,HAO | Half-saturation for G value for HAO | 10 | 1/s
Table1 | Disabled
No interpolation | Repeated every 144 hours
Time | Q | TKN | TCOD
d | m3/d | g N/m3 | g COD/m3
0 | 24000 | 77.6274 | 414.9684
0.0069444 | 24185.3856 | 75.9772 | 413.5355
0.013889 | 24370.4379 | 74.3669 | 412.3264
0.020833 | 24554.8239 | 72.7945 | 411.327
0.027778 | 24738.2121 | 71.2573 | 410.5214
0.034722 | 24920.273 | 69.7528 | 409.8919
0.041667 | 25100.6793 | 68.2798 | 409.4187
0.048611 | 25279.1072 | 66.8387 | 409.0842
0.055556 | 25455.2363 | 65.4316 | 408.8744
0.0625 | 25628.7509 | 64.0615 | 408.7772
0.069444 | 25799.3399 | 62.7321 | 408.7806
0.076389 | 25966.6981 | 61.4475 | 408.874
0.083333 | 26130.5262 | 60.2117 | 409.0523
0.090278 | 26290.5316 | 59.029 | 409.3178
0.097222 | 26446.4291 | 57.9039 | 409.6818
0.10417 | 26597.9412 | 56.8406 | 410.1634
0.11111 | 26744.7986 | 55.8433 | 410.7875
0.11806 | 26886.7411 | 54.9167 | 411.5838
0.125 | 27023.5174 | 54.0651 | 412.5895
0.13194 | 27154.8866 | 53.2893 | 413.8465
0.13889 | 27280.6174 | 52.5845 | 415.4078
0.14583 | 27400.4896 | 51.9339 | 417.3382
0.15278 | 27514.2941 | 51.3012 | 419.7028
0.15972 | 27621.833 | 50.6181 | 422.5158
0.16667 | 27722.9207 | 49.761 | 425.5709
0.17361 | 27817.3834 | 48.5784 | 428.0963
0.18056 | 27905.0602 | 47.5943 | 428.2772
0.1875 | 27985.8028 | 46.7446 | 427.7276
0.19444 | 28059.4763 | 46.1047 | 426.6002
0.20139 | 28125.9589 | 45.7482 | 425.0908
0.20833 | 28185.1428 | 45.6936 | 423.3891
0.21528 | 28236.9336 | 45.8721 | 421.5281
0.22222 | 28281.2512 | 46.1751 | 419.488
0.22917 | 28318.0295 | 46.5518 | 417.4567
0.23611 | 28347.2168 | 46.9663 | 415.7145
0.24306 | 28368.7758 | 47.402 | 414.329
0.25 | 28382.6834 | 47.9135 | 413.1708
0.25694 | 28388.9313 | 48.5503 | 412.0929
0.26389 | 28387.5255 | 49.3455 | 411.0532
0.27083 | 28378.4865 | 50.3271 | 410.0341
0.27778 | 28361.8493 | 51.4426 | 409.0492
0.28472 | 28337.6632 | 52.6194 | 408.2207
0.29167 | 28305.992 | 53.8014 | 407.5737
0.29861 | 28266.9133 | 54.9863 | 407.2409
0.30556 | 28220.5191 | 56.1739 | 407.2003
0.3125 | 28166.9149 | 57.3578 | 407.3884
0.31944 | 28106.2199 | 58.4501 | 407.8042
0.32639 | 28038.5669 | 59.3358 | 408.4853
0.33333 | 27964.1016 | 59.972 | 409.462
0.34028 | 27882.9827 | 60.3673 | 410.7129
0.34722 | 27795.3814 | 60.5492 | 412.0214
0.35417 | 27701.4812 | 60.5788 | 413.1597
0.36111 | 27601.4774 | 60.5035 | 414.1203
0.36806 | 27495.5768 | 60.3791 | 414.9966
0.375 | 27383.9974 | 60.2486 | 415.7811
0.38194 | 27266.9678 | 60.1767 | 416.4247
0.38889 | 27144.7269 | 60.2311 | 417.0182
0.39583 | 27017.5234 | 60.3971 | 417.5359
0.40278 | 26885.6154 | 60.6206 | 418.0137
0.40972 | 26749.2697 | 60.8655 | 418.5442
0.41667 | 26608.7614 | 61.0763 | 419.1149
0.42361 | 26464.3736 | 61.2258 | 419.7126
0.43056 | 26316.3965 | 61.2491 | 420.3393
0.4375 | 26165.127 | 61.0953 | 421.0086
0.44444 | 26010.8682 | 60.789 | 421.595
0.45139 | 25853.9287 | 60.3534 | 421.8634
0.45833 | 25694.622 | 59.8049 | 421.6586
0.46528 | 25533.2662 | 59.1602 | 420.8117
0.47222 | 25370.1829 | 58.4588 | 419.3273
0.47917 | 25205.6971 | 57.8169 | 417.3243
0.48611 | 25040.136 | 57.3588 | 414.8675
0.49306 | 24873.8291 | 57.1827 | 412.0511
0.5 | 24707.1068 | 57.3174 | 409.1883
0.50694 | 24540.3004 | 57.7821 | 406.671
0.51389 | 24373.741 | 58.5847 | 404.7626
0.52083 | 24207.7593 | 59.6698 | 403.6206
0.52778 | 24042.6846 | 60.9418 | 403.2742
0.53472 | 23878.8444 | 62.2574 | 403.5483
0.54167 | 23716.5636 | 63.4367 | 404.1171
0.54861 | 23556.1641 | 64.3255 | 404.7069
0.55556 | 23397.9639 | 64.8542 | 405.088
0.5625 | 23242.2767 | 65.0236 | 405.0743
0.56944 | 23089.4114 | 64.8622 | 404.5156
0.57639 | 22939.6713 | 64.4343 | 403.3593
0.58333 | 22793.3533 | 63.8524 | 401.7213
0.59028 | 22650.7481 | 63.2394 | 399.8787
0.59722 | 22512.1389 | 62.7046 | 398.111
0.60417 | 22377.801 | 62.2982 | 396.5765
0.61111 | 22248.0016 | 62.026 | 395.4769
0.61806 | 22122.9991 | 61.8827 | 394.8961
0.625 | 22003.0425 | 61.8293 | 394.7908
0.63194 | 21888.371 | 61.8324 | 395.2757
0.63889 | 21779.2137 | 61.8339 | 396.3013
0.64583 | 21675.7888 | 61.7775 | 397.7266
0.65278 | 21578.3037 | 61.6007 | 399.4057
0.65972 | 21486.9541 | 61.2661 | 401.0521
0.66667 | 21401.9238 | 60.7544 | 402.3696
0.67361 | 21323.3846 | 60.0526 | 403.2068
0.68056 | 21251.4956 | 59.2069 | 403.6673
0.6875 | 21186.4031 | 58.3416 | 403.9823
0.69444 | 21128.2404 | 57.5806 | 404.2278
0.70139 | 21077.127 | 57.0545 | 404.3286
0.70833 | 21033.1694 | 56.8641 | 404.2573
0.71528 | 20996.4599 | 57.0752 | 404.1648
0.72222 | 20967.0768 | 57.6737 | 404.2605
0.72917 | 20945.0844 | 58.5753 | 404.5772
0.73611 | 20930.5327 | 59.662 | 405.1846
0.74306 | 20923.4573 | 60.8306 | 406.1868
0.75 | 20923.8795 | 61.9839 | 407.7363
0.75694 | 20931.806 | 63.0607 | 409.8698
0.76389 | 20947.2291 | 63.9901 | 412.3608
0.77083 | 20970.1265 | 64.7308 | 414.8401
0.77778 | 21000.4616 | 65.2389 | 417.0917
0.78472 | 21038.1835 | 65.4968 | 419.03
0.79167 | 21083.2268 | 65.518 | 420.6189
0.79861 | 21135.5123 | 65.2906 | 421.7863
0.80556 | 21194.9465 | 64.8558 | 422.5848
0.8125 | 21261.4222 | 64.266 | 423.076
0.81944 | 21334.8187 | 63.5319 | 423.4452
0.82639 | 21415.0018 | 62.6909 | 424.0014
0.83333 | 21501.8242 | 61.8079 | 424.9861
0.84028 | 21595.1258 | 60.9344 | 426.3432
0.84722 | 21694.7339 | 60.1012 | 427.9826
0.85417 | 21800.4636 | 59.3197 | 429.7398
0.86111 | 21912.1182 | 58.5812 | 431.3272
0.86806 | 22029.4895 | 57.8493 | 432.6093
0.875 | 22152.3582 | 57.1159 | 433.6005
0.88194 | 22280.4942 | 56.3953 | 434.3625
0.88889 | 22413.6573 | 55.7136 | 434.773
0.89583 | 22551.5976 | 55.1034 | 434.7839
0.90278 | 22694.0558 | 54.6102 | 434.3363
0.90972 | 22840.7637 | 54.28 | 433.3918
0.91667 | 22991.4449 | 54.1526 | 432.0769
0.92361 | 23145.8152 | 54.1912 | 430.6268
0.93056 | 23303.5833 | 54.3036 | 429.1531
0.9375 | 23464.451 | 54.4115 | 427.7129
0.94444 | 23628.1141 | 54.4863 | 426.304
0.95139 | 23794.2629 | 54.5194 | 424.7649
0.95833 | 23962.5827 | 54.5123 | 423.0184
0.96528 | 24132.7545 | 54.4712 | 420.9497
0.97222 | 24304.4555 | 54.362 | 418.3086
0.97917 | 24477.3598 | 54.0964 | 415.0059
0.98611 | 24651.1391 | 53.5708 | 411.2595
0.99306 | 24825.463 | 52.7432 | 407.3875
1 | 25000 | 51.6155 | 403.6912
1.0069 | 25174.4181 | 50.2047 | 400.49
1.0139 | 25348.385 | 48.5709 | 397.8318
1.0208 | 25521.5694 | 46.8392 | 395.5585
1.0278 | 25693.6409 | 45.106 | 393.5283
1.0347 | 25864.2714 | 43.4726 | 391.7295
1.0417 | 26033.1351 | 41.9773 | 390.2979
1.0486 | 26199.9093 | 40.6437 | 389.3309
1.0556 | 26364.2753 | 39.5019 | 388.878
1.0625 | 26525.9185 | 38.5934 | 388.9605
1.0694 | 26684.5294 | 37.928 | 389.6425
1.0764 | 26839.8041 | 37.5447 | 390.9192
1.0833 | 26991.4449 | 37.5108 | 392.6582
1.0903 | 27139.1605 | 37.889 | 394.5949
1.0972 | 27282.6673 | 38.6709 | 396.5246
1.1042 | 27421.6891 | 39.7889 | 398.3492
1.1111 | 27555.9582 | 41.162 | 400.0647
1.1181 | 27685.2158 | 42.765 | 401.6064
1.125 | 27809.2124 | 44.5686 | 402.9366
1.1319 | 27927.7082 | 46.5271 | 404.0201
1.1389 | 28040.4738 | 48.5811 | 404.8984
1.1458 | 28147.2903 | 50.6087 | 405.5773
1.1528 | 28247.9503 | 52.5211 | 405.8752
1.1597 | 28342.2574 | 54.2733 | 405.5538
1.1667 | 28430.0274 | 55.8303 | 404.4987
1.1736 | 28511.0885 | 57.1415 | 402.6309
1.1806 | 28585.281 | 58.1364 | 400.042
1.1875 | 28652.4585 | 58.7516 | 396.8788
1.1944 | 28712.4874 | 59.0075 | 393.4809
1.2014 | 28765.2479 | 58.9429 | 390.2521
1.2083 | 28810.6334 | 58.607 | 387.3937
1.2153 | 28848.5515 | 58.036 | 384.9746
1.2222 | 28878.9236 | 57.2915 | 383.0609
1.2292 | 28901.6854 | 56.4917 | 381.764
1.2361 | 28916.7867 | 55.7513 | 381.0685
1.2431 | 28924.1918 | 55.1388 | 380.9117
1.25 | 28923.8795 | 54.6744 | 381.2717
1.2569 | 28915.8431 | 54.3511 | 382.0956
1.2639 | 28900.0903 | 54.1784 | 383.3044
1.2708 | 28876.6433 | 54.1786 | 384.7785
1.2778 | 28845.5388 | 54.3208 | 386.3551
1.2847 | 28806.8279 | 54.5613 | 387.8602
1.2917 | 28760.576 | 54.9037 | 389.1914
1.2986 | 28706.8627 | 55.3277 | 390.2068
1.3056 | 28645.7813 | 55.7796 | 390.9197
1.3125 | 28577.4394 | 56.2318 | 391.4955
1.3194 | 28501.9579 | 56.6779 | 392.1046
1.3264 | 28419.4713 | 57.1232 | 392.7686
1.3333 | 28330.127 | 57.5855 | 393.323
1.3403 | 28234.0856 | 58.0875 | 393.6387
1.3472 | 28131.52 | 58.673 | 393.5789
1.3542 | 28022.6155 | 59.3501 | 393.114
1.3611 | 27907.5692 | 60.1028 | 392.4326
1.3681 | 27786.5897 | 60.9125 | 391.8007
1.375 | 27659.8967 | 61.7275 | 391.3714
1.3819 | 27527.7208 | 62.5289 | 391.0264
1.3889 | 27390.3025 | 63.2881 | 390.6549
1.3958 | 27247.8924 | 63.9159 | 390.2297
1.4028 | 27100.7503 | 64.3229 | 389.8668
1.4097 | 26949.145 | 64.4843 | 389.8398
1.4167 | 26793.3533 | 64.4175 | 390.4096
1.4236 | 26633.6602 | 64.1412 | 391.69
1.4306 | 26470.3575 | 63.7308 | 393.5681
1.4375 | 26303.7442 | 63.3132 | 395.8176
1.4444 | 26134.125 | 63.0107 | 398.2834
1.4514 | 25961.8105 | 62.9179 | 400.8914
1.4583 | 25787.116 | 63.0436 | 403.5756
1.4653 | 25610.3613 | 63.3364 | 406.2122
1.4722 | 25431.8701 | 63.6918 | 408.6379
1.4792 | 25251.9688 | 63.9978 | 410.6644
1.4861 | 25070.9869 | 64.2026 | 412.1718
1.4931 | 24889.2555 | 64.2636 | 413.1834
1.5 | 24707.1068 | 64.1525 | 413.6912
1.5069 | 24524.874 | 63.8339 | 413.6071
1.5139 | 24342.8901 | 63.2578 | 412.9518
1.5208 | 24161.4875 | 62.3947 | 411.8371
1.5278 | 23980.9975 | 61.213 | 410.3941
1.5347 | 23801.7493 | 59.7105 | 408.6028
1.5417 | 23624.0696 | 57.9894 | 406.3579
1.5486 | 23448.2823 | 56.2172 | 403.6302
1.5556 | 23274.707 | 54.5719 | 400.5126
1.5625 | 23103.6596 | 53.1932 | 397.0811
1.5694 | 22935.4504 | 52.117 | 393.4496
1.5764 | 22770.3847 | 51.2817 | 389.8449
1.5833 | 22608.7614 | 50.5864 | 386.5644
1.5903 | 22450.8728 | 49.9341 | 383.8034
1.5972 | 22297.0039 | 49.2544 | 381.5374
1.6042 | 22147.432 | 48.5291 | 379.5999
1.6111 | 22002.426 | 47.7781 | 377.8797
1.6181 | 21862.2461 | 47.0669 | 376.4052
1.625 | 21727.1431 | 46.4536 | 375.2953
1.6319 | 21597.3581 | 45.9658 | 374.5486
1.6389 | 21473.1218 | 45.6464 | 374.1214
1.6458 | 21354.6545 | 45.5284 | 373.8268
1.6528 | 21242.1651 | 45.6069 | 373.5215
1.6597 | 21135.8511 | 45.8398 | 373.1419
1.6667 | 21035.8984 | 46.1634 | 372.7512
1.6736 | 20942.4802 | 46.5033 | 372.5618
1.6806 | 20855.7576 | 46.8122 | 372.6888
1.6875 | 20775.8786 | 47.0767 | 373.1827
1.6944 | 20702.9781 | 47.3463 | 374.1565
1.7014 | 20637.1777 | 47.6126 | 375.5779
1.7083 | 20578.5854 | 47.853 | 377.3447
1.7153 | 20527.2952 | 48.0519 | 379.3192
1.7222 | 20483.3872 | 48.1582 | 381.4105
1.7292 | 20446.9276 | 48.1357 | 383.5685
1.7361 | 20417.9679 | 48.0346 | 385.8552
1.7431 | 20396.5455 | 47.9594 | 388.2849
1.75 | 20382.6834 | 48.0475 | 390.7059
1.7569 | 20376.39 | 48.3797 | 392.8393
1.7639 | 20377.6593 | 48.9814 | 394.5918
1.7708 | 20386.4706 | 49.8312 | 396.0351
1.7778 | 20402.7891 | 50.9229 | 397.1819
1.7847 | 20426.5655 | 52.296 | 398.0583
1.7917 | 20457.7362 | 53.9351 | 398.8449
1.7986 | 20496.2233 | 55.7661 | 399.7527
1.8056 | 20541.9353 | 57.7152 | 400.9123
1.8125 | 20594.7666 | 59.7258 | 402.3499
1.8194 | 20654.5979 | 61.7689 | 403.9677
1.8264 | 20721.2967 | 63.7749 | 405.6119
1.8333 | 20794.7174 | 65.6471 | 407.2085
1.8403 | 20874.7015 | 67.3264 | 408.7902
1.8472 | 20961.0777 | 68.8167 | 410.4631
1.8542 | 21053.6629 | 70.1527 | 412.2738
1.8611 | 21152.2618 | 71.3517 | 414.1619
1.8681 | 21256.6679 | 72.4173 | 415.9914
1.875 | 21366.6632 | 73.3235 | 417.6657
1.8819 | 21482.0194 | 74.0238 | 419.1066
1.8889 | 21602.4977 | 74.4946 | 420.2405
1.8958 | 21727.8498 | 74.6959 | 421.0586
1.9028 | 21857.8176 | 74.5717 | 421.6058
1.9097 | 21992.1348 | 74.0915 | 421.8457
1.9167 | 22130.5262 | 73.2585 | 421.6639
1.9236 | 22272.7092 | 72.1312 | 420.9524
1.9306 | 22418.3938 | 70.7963 | 419.7
1.9375 | 22567.2834 | 69.3509 | 418.0387
1.9444 | 22719.0752 | 67.8459 | 416.0588
1.9514 | 22873.4608 | 66.33 | 413.7173
1.9583 | 23030.127 | 64.8686 | 410.9459
1.9653 | 23188.756 | 63.4997 | 407.8539
1.9722 | 23349.0267 | 62.2177 | 404.7139
1.9792 | 23510.6143 | 61.0107 | 401.8356
1.9861 | 23673.1919 | 59.8909 | 399.4694
1.9931 | 23836.4305 | 58.8937 | 397.7435
2 | 24000 | 58.0878 | 396.747
2.0069 | 24163.5695 | 57.5081 | 396.5419
2.0139 | 24326.8081 | 57.1632 | 397.1623
2.0208 | 24489.3857 | 57.0275 | 398.5861
2.0278 | 24650.9733 | 57.0567 | 400.6803
2.0347 | 24811.244 | 57.1722 | 403.1786
2.0417 | 24969.873 | 57.3159 | 405.7898
2.0486 | 25126.5392 | 57.4567 | 408.2558
2.0556 | 25280.9248 | 57.5734 | 410.5148
2.0625 | 25432.7166 | 57.6441 | 412.5211
2.0694 | 25581.6062 | 57.6531 | 414.1795
2.0764 | 25727.2908 | 57.6264 | 415.3997
2.0833 | 25869.4738 | 57.6044 | 416.1562
2.0903 | 26007.8652 | 57.6046 | 416.4952
2.0972 | 26142.1824 | 57.6778 | 416.5074
2.1042 | 26272.1502 | 57.885 | 416.0892
2.1111 | 26397.5023 | 58.2705 | 415.1334
2.1181 | 26517.9806 | 58.8495 | 413.6893
2.125 | 26633.3368 | 59.5814 | 411.8439
2.1319 | 26743.3321 | 60.407 | 409.6352
2.1389 | 26847.7382 | 61.2937 | 407.1717
2.1458 | 26946.3371 | 62.1966 | 404.5614
2.1528 | 27038.9223 | 63.0619 | 401.848
2.1597 | 27125.2985 | 63.8563 | 399.0892
2.1667 | 27205.2826 | 64.5487 | 396.3404
2.1736 | 27278.7033 | 65.0787 | 393.666
2.1806 | 27345.4021 | 65.331 | 391.09
2.1875 | 27405.2334 | 65.2032 | 388.7382
2.1944 | 27458.0647 | 64.6579 | 386.6859
2.2014 | 27503.7767 | 63.7761 | 385.1359
2.2083 | 27542.2638 | 62.7037 | 384.345
2.2153 | 27573.4345 | 61.5795 | 384.6298
2.2222 | 27597.2109 | 60.499 | 386.3107
2.2292 | 27613.5294 | 59.5036 | 389.4779
2.2361 | 27622.3407 | 58.6183 | 393.8709
2.2431 | 27623.61 | 57.8408 | 399.0106
2.25 | 27617.3166 | 57.1904 | 404.4348
2.2569 | 27603.4545 | 56.6962 | 409.6829
2.2639 | 27582.0321 | 56.3058 | 414.2701
2.2708 | 27553.0724 | 55.9466 | 417.8143
2.2778 | 27516.6128 | 55.5323 | 420.1522
2.2847 | 27472.7048 | 55.0322 | 421.274
2.2917 | 27421.4146 | 54.5022 | 421.1958
2.2986 | 27362.8223 | 54.0426 | 420.0565
2.3056 | 27297.0219 | 53.7661 | 418.0398
2.3125 | 27224.1214 | 53.7838 | 415.4013
2.3194 | 27144.2424 | 54.1404 | 412.3862
2.3264 | 27057.5198 | 54.7611 | 409.2143
2.3333 | 26964.1016 | 55.5431 | 406.0524
2.3403 | 26864.1489 | 56.405 | 402.9655
2.3472 | 26757.8349 | 57.2916 | 400.075
2.3542 | 26645.3455 | 58.1775 | 397.5607
2.3611 | 26526.8782 | 59.0455 | 395.5471
2.3681 | 26402.6419 | 59.8279 | 394.0886
2.375 | 26272.8569 | 60.4153 | 393.2166
2.3819 | 26137.7539 | 60.7257 | 392.9266
2.3889 | 25997.574 | 60.7214 | 393.1358
2.3958 | 25852.568 | 60.3592 | 393.5925
2.4028 | 25702.9961 | 59.6287 | 394.0969
2.4097 | 25549.1272 | 58.5387 | 394.6127
2.4167 | 25391.2386 | 57.0998 | 395.2383
2.4236 | 25229.6153 | 55.3857 | 396.0944
2.4306 | 25064.5496 | 53.5667 | 397.305
2.4375 | 24896.3404 | 51.8376 | 398.9795
2.4444 | 24725.293 | 50.359 | 401.2246
2.4514 | 24551.7177 | 49.2134 | 404.0052
2.4583 | 24375.9304 | 48.4255 | 407.1661
2.4653 | 24198.2507 | 47.9944 | 410.3386
2.4722 | 24019.0025 | 47.885 | 412.9984
2.4792 | 23838.5125 | 47.9895 | 414.6827
2.4861 | 23657.1099 | 48.1826 | 415.1464
2.4931 | 23475.126 | 48.3737 | 414.3758
2.5 | 23292.8932 | 48.479 | 412.5535
2.5069 | 23110.7445 | 48.4513 | 410.0353
2.5139 | 22929.0131 | 48.3228 | 407.1355
2.5208 | 22748.0312 | 48.1822 | 404.2353
2.5278 | 22568.1299 | 48.1196 | 401.5862
2.5347 | 22389.6387 | 48.2371 | 399.2603
2.5417 | 22212.884 | 48.5956 | 397.2103
2.5486 | 22038.1895 | 49.1824 | 395.5094
2.5556 | 21865.875 | 49.9517 | 394.2491
2.5625 | 21696.2558 | 50.8878 | 393.3262
2.5694 | 21529.6425 | 51.9337 | 392.5604
2.5764 | 21366.3398 | 53.0059 | 391.8335
2.5833 | 21206.6467 | 54.013 | 391.0882
2.5903 | 21050.855 | 54.86 | 390.334
2.5972 | 20899.2497 | 55.5027 | 389.7047
2.6042 | 20752.1076 | 55.9838 | 389.4422
2.6111 | 20609.6975 | 56.3691 | 389.7736
2.6181 | 20472.2792 | 56.7421 | 390.7889
2.625 | 20340.1033 | 57.1713 | 392.5706
2.6319 | 20213.4103 | 57.6311 | 395.1462
2.6389 | 20092.4308 | 58.1108 | 398.3822
2.6458 | 19977.3845 | 58.6241 | 401.995
2.6528 | 19868.48 | 59.1467 | 405.5886
2.6597 | 19765.9144 | 59.6787 | 408.7832
2.6667 | 19669.873 | 60.274 | 411.388
2.6736 | 19580.5287 | 60.9453 | 413.3206
2.6806 | 19498.0421 | 61.6404 | 414.5483
2.6875 | 19422.5606 | 62.293 | 415.0622
2.6944 | 19354.2187 | 62.8021 | 414.8648
2.7014 | 19293.1373 | 63.0408 | 414.1166
2.7083 | 19239.424 | 62.9166 | 413.0399
2.7153 | 19193.1721 | 62.3988 | 411.8542
2.7222 | 19154.4612 | 61.5106 | 410.6568
2.7292 | 19123.3567 | 60.2893 | 409.5379
2.7361 | 19099.9097 | 58.8077 | 408.7346
2.7431 | 19084.1569 | 57.1997 | 408.5113
2.75 | 19076.1205 | 55.5978 | 409.0092
2.7569 | 19075.8082 | 54.1335 | 410.2529
2.7639 | 19083.2133 | 52.9129 | 412.1321
2.7708 | 19098.3146 | 51.9424 | 414.5242
2.7778 | 19121.0764 | 51.2214 | 417.2936
2.7847 | 19151.4485 | 50.7573 | 420.2163
2.7917 | 19189.3666 | 50.5187 | 423.0462
2.7986 | 19234.7521 | 50.4631 | 425.4938
2.8056 | 19287.5126 | 50.5474 | 427.5236
2.8125 | 19347.5415 | 50.723 | 429.3133
2.8194 | 19414.719 | 50.9857 | 431.0884
2.8264 | 19488.9115 | 51.3097 | 432.9334
2.8333 | 19569.9726 | 51.6466 | 434.8835
2.8403 | 19657.7426 | 51.9796 | 436.9196
2.8472 | 19752.0497 | 52.3089 | 439.0014
2.8542 | 19852.7097 | 52.6416 | 441.0831
2.8611 | 19959.5262 | 53.0224 | 442.9705
2.8681 | 20072.2918 | 53.4844 | 444.3773
2.875 | 20190.7876 | 53.9719 | 445.1365
2.8819 | 20314.7842 | 54.4443 | 445.1001
2.8889 | 20444.0418 | 54.8552 | 444.1008
2.8958 | 20578.3109 | 55.147 | 441.9655
2.9028 | 20717.3327 | 55.2621 | 438.6907
2.9097 | 20860.8395 | 55.1881 | 434.493
2.9167 | 21008.5551 | 54.9486 | 429.6903
2.9236 | 21160.1959 | 54.5972 | 424.6563
2.9306 | 21315.4706 | 54.179 | 419.678
2.9375 | 21474.0815 | 53.7543 | 414.9857
2.9444 | 21635.7247 | 53.3923 | 410.8797
2.9514 | 21800.0907 | 53.1407 | 407.5676
2.9583 | 21966.8649 | 53.0414 | 405.1946
2.9653 | 22135.7286 | 53.1493 | 403.7807
2.9722 | 22306.3591 | 53.5111 | 403.2607
2.9792 | 22478.4306 | 54.0961 | 403.4739
2.9861 | 22651.615 | 54.8442 | 404.2271
2.9931 | 22825.5819 | 55.7302 | 405.4153
3 | 23000 | 56.7429 | 406.8675
3.0069 | 23174.537 | 57.8667 | 408.3729
3.0139 | 23348.8609 | 59.0814 | 409.8377
3.0208 | 23522.6402 | 60.3425 | 411.216
3.0278 | 23695.5445 | 61.6253 | 412.5044
3.0347 | 23867.2455 | 62.9351 | 413.749
3.0417 | 24037.4173 | 64.2888 | 414.9962
3.0486 | 24205.7371 | 65.6286 | 416.1858
3.0556 | 24371.8859 | 66.8461 | 417.1533
3.0625 | 24535.549 | 67.8259 | 417.7671
3.0694 | 24696.4167 | 68.502 | 418.0636
3.0764 | 24854.1848 | 68.8814 | 418.0541
3.0833 | 25008.5551 | 68.9586 | 417.8052
3.0903 | 25159.2363 | 68.7242 | 417.3972
3.0972 | 25305.9442 | 68.1866 | 416.8643
3.1042 | 25448.4024 | 67.3711 | 416.3231
3.1111 | 25586.3427 | 66.3701 | 415.8358
3.1181 | 25719.5058 | 65.234 | 415.4209
3.125 | 25847.6418 | 63.9764 | 415.1721
3.1319 | 25970.5105 | 62.6337 | 415.2264
3.1389 | 26087.8818 | 61.2419 | 415.5958
3.1458 | 26199.5364 | 59.8433 | 416.1189
3.1528 | 26305.2661 | 58.5055 | 416.7361
3.1597 | 26404.8742 | 57.2823 | 417.485
3.1667 | 26498.1758 | 56.2444 | 418.4265
3.1736 | 26584.9982 | 55.4479 | 419.4627
3.1806 | 26665.1813 | 54.9025 | 420.3704
3.1875 | 26738.5778 | 54.6471 | 420.8905
3.1944 | 26805.0535 | 54.686 | 420.8244
3.2014 | 26864.4877 | 54.9618 | 420.1877
3.2083 | 26916.7732 | 55.4172 | 419.126
3.2153 | 26961.8165 | 55.9986 | 417.8272
3.2222 | 26999.5384 | 56.6214 | 416.4734
3.2292 | 27029.8735 | 57.2056 | 415.2056
3.2361 | 27052.7709 | 57.7286 | 414.1135
3.2431 | 27068.194 | 58.1872 | 413.3073
3.25 | 27076.1205 | 58.5817 | 412.7585
3.2569 | 27076.5427 | 58.9019 | 412.3845
3.2639 | 27069.4673 | 59.1503 | 412.11
3.2708 | 27054.9156 | 59.2966 | 411.8877
3.2778 | 27032.9232 | 59.278 | 411.5145
3.2847 | 27003.5401 | 59.0366 | 410.7074
3.2917 | 26966.8306 | 58.5862 | 409.3409
3.2986 | 26922.873 | 57.9322 | 407.4984
3.3056 | 26871.7596 | 57.0346 | 405.3215
3.3125 | 26813.5969 | 55.9218 | 403.0104
3.3194 | 26748.5044 | 54.6771 | 400.766
3.3264 | 26676.6154 | 53.3993 | 398.8016
3.3333 | 26598.0762 | 52.1836 | 397.1916
3.3403 | 26513.0459 | 51.1225 | 395.8671
3.3472 | 26421.6963 | 50.2796 | 394.7198
3.3542 | 26324.2112 | 49.6975 | 393.5959
3.3611 | 26220.7863 | 49.3787 | 392.4182
3.3681 | 26111.629 | 49.2306 | 391.236
3.375 | 25996.9575 | 49.144 | 390.0762
3.3819 | 25877.0009 | 49.0713 | 388.859
3.3889 | 25751.9984 | 49.0647 | 387.5426
3.3958 | 25622.199 | 49.2207 | 386.1421
3.4028 | 25487.8611 | 49.6119 | 384.6314
3.4097 | 25349.2519 | 50.2239 | 382.8613
3.4167 | 25206.6467 | 50.974 | 380.8425
3.4236 | 25060.3287 | 51.7774 | 378.7076
3.4306 | 24910.5886 | 52.6098 | 376.6438
3.4375 | 24757.7233 | 53.4684 | 374.8604
3.4444 | 24602.0361 | 54.3507 | 373.5765
3.4514 | 24443.8359 | 55.2199 | 372.9153
3.4583 | 24283.4364 | 56.0267 | 373.041
3.4653 | 24121.1556 | 56.7187 | 374.1066
3.4722 | 23957.3154 | 57.261 | 376.1672
3.4792 | 23792.2407 | 57.6214 | 379.2903
3.4861 | 23626.259 | 57.79 | 383.4061
3.4931 | 23459.6996 | 57.7439 | 388.2054
3.5 | 23292.8932 | 57.4592 | 393.2028
3.5069 | 23126.1709 | 56.9506 | 397.9418
3.5139 | 22959.864 | 56.2855 | 402.1338
3.5208 | 22794.3029 | 55.5183 | 405.5301
3.5278 | 22629.8171 | 54.6773 | 407.9881
3.5347 | 22466.7338 | 53.8035 | 409.4849
3.5417 | 22305.378 | 52.9446 | 410.0929
3.5486 | 22146.0713 | 52.1759 | 409.9765
3.5556 | 21989.1318 | 51.6075 | 409.3044
3.5625 | 21834.873 | 51.3125 | 408.2882
3.5694 | 21683.6035 | 51.3283 | 407.2128
3.5764 | 21535.6264 | 51.6081 | 406.3836
3.5833 | 21391.2386 | 52.0835 | 405.9605
3.5903 | 21250.7303 | 52.7353 | 406.0159
3.5972 | 21114.3846 | 53.5469 | 406.4947
3.6042 | 20982.4766 | 54.4947 | 407.2119
3.6111 | 20855.2731 | 55.5893 | 408.0145
3.6181 | 20733.0322 | 56.8335 | 409.0018
3.625 | 20616.0026 | 58.1831 | 410.2771
3.6319 | 20504.4232 | 59.5553 | 411.7397
3.6389 | 20398.5226 | 60.8966 | 413.1671
3.6458 | 20298.5188 | 62.1973 | 414.4342
3.6528 | 20204.6186 | 63.451 | 415.476
3.6597 | 20117.0173 | 64.6465 | 416.1754
3.6667 | 20035.8984 | 65.7785 | 416.4669
3.6736 | 19961.4331 | 66.8011 | 416.3555
3.6806 | 19893.7801 | 67.6397 | 416.0525
3.6875 | 19833.0851 | 68.2601 | 415.7088
3.6944 | 19779.4809 | 68.6387 | 415.5304
3.7014 | 19733.0867 | 68.7848 | 415.7112
3.7083 | 19694.008 | 68.7502 | 416.2451
3.7153 | 19662.3368 | 68.5738 | 417.204
3.7222 | 19638.1507 | 68.2514 | 418.4943
3.7292 | 19621.5135 | 67.7725 | 419.8676
3.7361 | 19612.4745 | 67.1317 | 421.0705
3.7431 | 19611.0687 | 66.3105 | 422.0001
3.75 | 19617.3166 | 65.3077 | 422.5498
3.7569 | 19631.2242 | 64.1698 | 422.5654
3.7639 | 19652.7832 | 62.9231 | 421.9039
3.7708 | 19681.9705 | 61.561 | 420.5466
3.7778 | 19718.7488 | 60.0666 | 418.6438
3.7847 | 19763.0664 | 58.419 | 416.4434
3.7917 | 19814.8572 | 56.6614 | 414.443
3.7986 | 19874.0411 | 54.8667 | 413.1206
3.8056 | 19940.5237 | 53.1234 | 412.7124
3.8125 | 20014.1972 | 51.5019 | 413.2803
3.8194 | 20094.9398 | 50.0448 | 414.6591
3.8264 | 20182.6166 | 48.801 | 416.5778
3.8333 | 20277.0793 | 47.8113 | 418.7517
3.8403 | 20378.167 | 47.0734 | 420.9518
3.8472 | 20485.7059 | 46.5588 | 423.12
3.8542 | 20599.5104 | 46.2384 | 425.2087
3.8611 | 20719.3826 | 46.1197 | 427.1008
3.8681 | 20845.1134 | 46.1783 | 428.6388
3.875 | 20976.4826 | 46.3811 | 429.7777
3.8819 | 21113.2589 | 46.7095 | 430.5812
3.8889 | 21255.2014 | 47.1428 | 431.1536
3.8958 | 21402.0588 | 47.6262 | 431.665
3.9028 | 21553.5709 | 48.1518 | 432.2037
3.9097 | 21709.4684 | 48.783 | 432.748
3.9167 | 21869.4738 | 49.6081 | 433.2859
3.9236 | 22033.3019 | 50.6807 | 433.7808
3.9306 | 22200.6601 | 51.9714 | 434.1382
3.9375 | 22371.2491 | 53.4051 | 434.2535
3.9444 | 22544.7637 | 54.8795 | 434.0628
3.9514 | 22720.8928 | 56.273 | 433.3348
3.9583 | 22899.3207 | 57.5053 | 431.7522
3.9653 | 23079.727 | 58.5655 | 429.2673
3.9722 | 23261.7879 | 59.4728 | 426.2116
3.9792 | 23445.1761 | 60.2462 | 422.9609
3.9861 | 23629.5621 | 60.867 | 419.6527
3.9931 | 23814.6144 | 61.2518 | 416.3712
4 | 24000 | 61.321 | 413.2097
4.0069 | 24185.3856 | 61.0147 | 410.1744
4.0139 | 24370.4379 | 60.3375 | 407.2484
4.0208 | 24554.8239 | 59.351 | 404.2821
4.0278 | 24738.2121 | 58.1321 | 401.2625
4.0347 | 24920.273 | 56.8318 | 398.2614
4.0417 | 25100.6793 | 55.5875 | 395.41
4.0486 | 25279.1072 | 54.5111 | 392.8178
4.0556 | 25455.2363 | 53.6963 | 390.6013
4.0625 | 25628.7509 | 53.2101 | 388.9385
4.0694 | 25799.3399 | 53.0126 | 387.8827
4.0764 | 25966.6981 | 53.0247 | 387.2836
4.0833 | 26130.5262 | 53.1648 | 386.946
4.0903 | 26290.5316 | 53.376 | 386.8691
4.0972 | 26446.4291 | 53.6179 | 387.1035
4.1042 | 26597.9412 | 53.8963 | 387.7959
4.1111 | 26744.7986 | 54.2111 | 389.112
4.1181 | 26886.7411 | 54.5507 | 391.1702
4.125 | 27023.5174 | 54.927 | 393.9624
4.1319 | 27154.8866 | 55.3466 | 397.2159
4.1389 | 27280.6174 | 55.8466 | 400.5391
4.1458 | 27400.4896 | 56.4313 | 403.6246
4.1528 | 27514.2941 | 57.0655 | 406.2126
4.1597 | 27621.833 | 57.704 | 408.0816
4.1667 | 27722.9207 | 58.2716 | 409.1495
4.1736 | 27817.3834 | 58.7227 | 409.3702
4.1806 | 27905.0602 | 59.0451 | 408.6435
4.1875 | 27985.8028 | 59.2142 | 406.7944
4.1944 | 28059.4763 | 59.2001 | 403.8422
4.2014 | 28125.9589 | 59.006 | 400.1377
4.2083 | 28185.1428 | 58.7134 | 396.0376
4.2153 | 28236.9336 | 58.402 | 391.8206
4.2222 | 28281.2512 | 58.1471 | 387.5812
4.2292 | 28318.0295 | 58.0152 | 383.4594
4.2361 | 28347.2168 | 58.1068 | 379.6295
4.2431 | 28368.7758 | 58.486 | 376.291
4.25 | 28382.6834 | 59.1743 | 373.5867
4.2569 | 28388.9313 | 60.1521 | 371.4514
4.2639 | 28387.5255 | 61.3644 | 369.8429
4.2708 | 28378.4865 | 62.7734 | 368.7918
4.2778 | 28361.8493 | 64.3605 | 368.3189
4.2847 | 28337.6632 | 66.0788 | 368.4658
4.2917 | 28305.992 | 67.8874 | 369.3478
4.2986 | 28266.9133 | 69.6766 | 371.1263
4.3056 | 28220.5191 | 71.3168 | 373.8488
4.3125 | 28166.9149 | 72.6767 | 377.4479
4.3194 | 28106.2199 | 73.615 | 381.7925
4.3264 | 28038.5669 | 74.037 | 386.6278
4.3333 | 27964.1016 | 73.9237 | 391.541
4.3403 | 27882.9827 | 73.303 | 396.2519
4.3472 | 27795.3814 | 72.2348 | 400.6476
4.3542 | 27701.4812 | 70.8053 | 404.7412
4.3611 | 27601.4774 | 69.1172 | 408.4964
4.3681 | 27495.5768 | 67.2858 | 411.8124
4.375 | 27383.9974 | 65.3767 | 414.5612
4.3819 | 27266.9678 | 63.4752 | 416.6868
4.3889 | 27144.7269 | 61.6167 | 418.275
4.3958 | 27017.5234 | 59.8042 | 419.2964
4.4028 | 26885.6154 | 58.04 | 419.597
4.4097 | 26749.2697 | 56.3497 | 419.1518
4.4167 | 26608.7614 | 54.7741 | 418.1144
4.4236 | 26464.3736 | 53.3682 | 416.624
4.4306 | 26316.3965 | 52.2311 | 414.6907
4.4375 | 26165.127 | 51.4452 | 412.4517
4.4444 | 26010.8682 | 51.0778 | 410.1336
4.4514 | 25853.9287 | 51.2156 | 408.0251
4.4583 | 25694.622 | 51.8944 | 406.3283
4.4653 | 25533.2662 | 53.051 | 405.1557
4.4722 | 25370.1829 | 54.5527 | 404.553
4.4792 | 25205.6971 | 56.2165 | 404.4344
4.4861 | 25040.136 | 57.9161 | 404.6748
4.4931 | 24873.8291 | 59.5977 | 405.1999
4.5 | 24707.1068 | 61.2211 | 405.9723
4.5069 | 24540.3004 | 62.7333 | 406.9076
4.5139 | 24373.741 | 64.0624 | 407.9401
4.5208 | 24207.7593 | 65.1236 | 409.1443
4.5278 | 24042.6846 | 65.8184 | 410.6236
4.5347 | 23878.8444 | 66.0845 | 412.2759
4.5417 | 23716.5636 | 65.8919 | 413.8334
4.5486 | 23556.1641 | 65.2166 | 415.1657
4.5556 | 23397.9639 | 64.1084 | 416.1823
4.5625 | 23242.2767 | 62.648 | 416.9474
4.5694 | 23089.4114 | 60.9163 | 417.4518
4.5764 | 22939.6713 | 59 | 417.5541
4.5833 | 22793.3533 | 56.9963 | 417.1909
4.5903 | 22650.7481 | 54.9908 | 416.3391
4.5972 | 22512.1389 | 53.0446 | 415.0866
4.6042 | 22377.801 | 51.2237 | 413.617
4.6111 | 22248.0016 | 49.5808 | 412.104
4.6181 | 22122.9991 | 48.1565 | 410.676
4.625 | 22003.0425 | 46.9713 | 409.4046
4.6319 | 21888.371 | 46.0228 | 408.4711
4.6389 | 21779.2137 | 45.3397 | 407.9563
4.6458 | 21675.7888 | 44.8999 | 407.7717
4.6528 | 21578.3037 | 44.6763 | 407.6774
4.6597 | 21486.9541 | 44.6527 | 407.3252
4.6667 | 21401.9238 | 44.7935 | 406.5048
4.6736 | 21323.3846 | 45.0469 | 405.0705
4.6806 | 21251.4956 | 45.324 | 402.932
4.6875 | 21186.4031 | 45.5458 | 400.1686
4.6944 | 21128.2404 | 45.6741 | 396.9838
4.7014 | 21077.127 | 45.6819 | 393.8167
4.7083 | 21033.1694 | 45.5828 | 390.9875
4.7153 | 20996.4599 | 45.4139 | 388.5592
4.7222 | 20967.0768 | 45.1714 | 386.5284
4.7292 | 20945.0844 | 44.8562 | 384.88
4.7361 | 20930.5327 | 44.4825 | 383.5347
4.7431 | 20923.4573 | 44.0944 | 382.4746
4.75 | 20923.8795 | 43.7706 | 381.6549
4.7569 | 20931.806 | 43.5581 | 381.053
4.7639 | 20947.2291 | 43.5065 | 380.7616
4.7708 | 20970.1265 | 43.6386 | 380.9326
4.7778 | 21000.4616 | 43.9515 | 381.7207
4.7847 | 21038.1835 | 44.4592 | 383.1011
4.7917 | 21083.2268 | 45.1476 | 384.9433
4.7986 | 21135.5123 | 45.9712 | 387.0289
4.8056 | 21194.9465 | 46.8916 | 389.2271
4.8125 | 21261.4222 | 47.8925 | 391.5335
4.8194 | 21334.8187 | 49.0088 | 394.1384
4.8264 | 21415.0018 | 50.2156 | 397.1765
4.8333 | 21501.8242 | 51.4469 | 400.5665
4.8403 | 21595.1258 | 52.6762 | 404.121
4.8472 | 21694.7339 | 53.8845 | 407.6326
4.8542 | 21800.4636 | 55.0695 | 410.9776
4.8611 | 21912.1182 | 56.235 | 414.0659
4.8681 | 22029.4895 | 57.3834 | 416.7878
4.875 | 22152.3582 | 58.4875 | 419.1193
4.8819 | 22280.4942 | 59.5123 | 420.9395
4.8889 | 22413.6573 | 60.4577 | 421.9701
4.8958 | 22551.5976 | 61.3118 | 422.0352
4.9028 | 22694.0558 | 62.0587 | 420.9968
4.9097 | 22840.7637 | 62.6748 | 418.9078
4.9167 | 22991.4449 | 63.1344 | 415.9986
4.9236 | 23145.8152 | 63.3722 | 412.4802
4.9306 | 23303.5833 | 63.3342 | 408.5738
4.9375 | 23464.451 | 63.0489 | 404.5374
4.9444 | 23628.1141 | 62.5711 | 400.532
4.9514 | 23794.2629 | 61.9596 | 396.7302
4.9583 | 23962.5827 | 61.2805 | 393.3816
4.9653 | 24132.7545 | 60.6122 | 390.5924
4.9722 | 24304.4555 | 59.9716 | 388.3432
4.9792 | 24477.3598 | 59.3228 | 386.5109
4.9861 | 24651.1391 | 58.6539 | 384.9069
4.9931 | 24825.463 | 57.9588 | 383.3862
5 | 25000 | 57.1981 | 381.988
5.0069 | 25174.4181 | 56.3393 | 380.8958
5.0139 | 25348.385 | 55.381 | 380.3413
5.0208 | 25521.5694 | 54.3918 | 380.4697
5.0278 | 25693.6409 | 53.4719 | 381.4116
5.0347 | 25864.2714 | 52.6994 | 383.2588
5.0417 | 26033.1351 | 52.0943 | 385.9693
5.0486 | 26199.9093 | 51.6078 | 389.4484
5.0556 | 26364.2753 | 51.1801 | 393.5461
5.0625 | 26525.9185 | 50.8329 | 397.9841
5.0694 | 26684.5294 | 50.6178 | 402.3747
5.0764 | 26839.8041 | 50.5736 | 406.5137
5.0833 | 26991.4449 | 50.7229 | 410.3878
5.0903 | 27139.1605 | 51.0717 | 413.9911
5.0972 | 27282.6673 | 51.5788 | 417.3035
5.1042 | 27421.6891 | 52.1748 | 420.2472
5.1111 | 27555.9582 | 52.8016 | 422.8275
5.1181 | 27685.2158 | 53.4472 | 424.955
5.125 | 27809.2124 | 54.04 | 426.6967
5.1319 | 27927.7082 | 54.5306 | 428.1315
5.1389 | 28040.4738 | 54.8928 | 429.3692
5.1458 | 28147.2903 | 55.1229 | 430.4438
5.1528 | 28247.9503 | 55.2542 | 431.2278
5.1597 | 28342.2574 | 55.333 | 431.5015
5.1667 | 28430.0274 | 55.4242 | 431.1196
5.1736 | 28511.0885 | 55.5465 | 430.0504
5.1806 | 28585.281 | 55.6791 | 428.3499
5.1875 | 28652.4585 | 55.8059 | 426.192
5.1944 | 28712.4874 | 55.874 | 423.7314
5.2014 | 28765.2479 | 55.8281 | 420.9983
5.2083 | 28810.6334 | 55.6653 | 418.0648
5.2153 | 28848.5515 | 55.393 | 415.0009
5.2222 | 28878.9236 | 54.9935 | 412.0573
5.2292 | 28901.6854 | 54.4392 | 409.481
5.2361 | 28916.7867 | 53.7077 | 407.2776
5.2431 | 28924.1918 | 52.809 | 405.3395
5.25 | 28923.8795 | 51.8145 | 403.5589
5.2569 | 28915.8431 | 50.8327 | 401.9558
5.2639 | 28900.0903 | 50.012 | 400.6396
5.2708 | 28876.6433 | 49.4394 | 399.7994
5.2778 | 28845.5388 | 49.1263 | 399.5006
5.2847 | 28806.8279 | 49.0738 | 399.6785
5.2917 | 28760.576 | 49.2562 | 400.2786
5.2986 | 28706.8627 | 49.5836 | 401.3095
5.3056 | 28645.7813 | 49.9446 | 402.8052
5.3125 | 28577.4394 | 50.2794 | 404.5982
5.3194 | 28501.9579 | 50.5796 | 406.4541
5.3264 | 28419.4713 | 50.8727 | 408.2353
5.3333 | 28330.127 | 51.1711 | 409.8438
5.3403 | 28234.0856 | 51.4845 | 411.1445
5.3472 | 28131.52 | 51.8169 | 412.1201
5.3542 | 28022.6155 | 52.1719 | 412.8442
5.3611 | 27907.5692 | 52.5466 | 413.3501
5.3681 | 27786.5897 | 52.9009 | 413.4528
5.375 | 27659.8967 | 53.1854 | 412.8977
5.3819 | 27527.7208 | 53.399 | 411.506
5.3889 | 27390.3025 | 53.5766 | 409.2561
5.3958 | 27247.8924 | 53.7636 | 406.3078
5.4028 | 27100.7503 | 53.9787 | 402.9479
5.4097 | 26949.145 | 54.2069 | 399.4723
5.4167 | 26793.3533 | 54.4219 | 396.1403
5.4236 | 26633.6602 | 54.5863 | 393.2719
5.4306 | 26470.3575 | 54.6631 | 391.2268
5.4375 | 26303.7442 | 54.7003 | 390.1988
5.4444 | 26134.125 | 54.7375 | 390.2495
5.4514 | 25961.8105 | 54.7906 | 391.2594
5.4583 | 25787.116 | 54.8918 | 393.0658
5.4653 | 25610.3613 | 55.1101 | 395.4382
5.4722 | 25431.8701 | 55.4909 | 398.3056
5.4792 | 25251.9688 | 56.051 | 401.6153
5.4861 | 25070.9869 | 56.7609 | 405.1727
5.4931 | 24889.2555 | 57.5227 | 408.9183
5.5 | 24707.1068 | 58.2541 | 412.814
5.5069 | 24524.874 | 58.9321 | 416.8742
5.5139 | 24342.8901 | 59.5733 | 421.0644
5.5208 | 24161.4875 | 60.1576 | 425.3681
5.5278 | 23980.9975 | 60.6557 | 429.679
5.5347 | 23801.7493 | 61.0783 | 433.8387
5.5417 | 23624.0696 | 61.4631 | 437.6771
5.5486 | 23448.2823 | 61.8137 | 440.9504
5.5556 | 23274.707 | 62.1043 | 443.4569
5.5625 | 23103.6596 | 62.3444 | 445.054
5.5694 | 22935.4504 | 62.5387 | 445.6824
5.5764 | 22770.3847 | 62.6955 | 445.3857
5.5833 | 22608.7614 | 62.761 | 444.2386
5.5903 | 22450.8728 | 62.6496 | 442.2092
5.5972 | 22297.0039 | 62.273 | 439.2337
5.6042 | 22147.432 | 61.6233 | 435.434
5.6111 | 22002.426 | 60.7673 | 430.9036
5.6181 | 21862.2461 | 59.7512 | 425.8468
5.625 | 21727.1431 | 58.5821 | 420.5709
5.6319 | 21597.3581 | 57.2997 | 415.3743
5.6389 | 21473.1218 | 55.999 | 410.4183
5.6458 | 21354.6545 | 54.7877 | 405.7587
5.6528 | 21242.1651 | 53.7227 | 401.4267
5.6597 | 21135.8511 | 52.8038 | 397.464
5.6667 | 21035.8984 | 52.0246 | 393.8631
5.6736 | 20942.4802 | 51.4048 | 390.7432
5.6806 | 20855.7576 | 50.9966 | 388.3155
5.6875 | 20775.8786 | 50.8232 | 386.5798
5.6944 | 20702.9781 | 50.8597 | 385.3831
5.7014 | 20637.1777 | 51.0425 | 384.6394
5.7083 | 20578.5854 | 51.2619 | 384.3185
5.7153 | 20527.2952 | 51.3957 | 384.3273
5.7222 | 20483.3872 | 51.3529 | 384.655
5.7292 | 20446.9276 | 51.0888 | 385.3057
5.7361 | 20417.9679 | 50.6274 | 386.282
5.7431 | 20396.5455 | 49.997 | 387.6582
5.75 | 20382.6834 | 49.3058 | 389.5099
5.7569 | 20376.39 | 48.6868 | 391.6723
5.7639 | 20377.6593 | 48.2347 | 393.8349
5.7708 | 20386.4706 | 47.9806 | 395.8239
5.7778 | 20402.7891 | 47.9004 | 397.6741
5.7847 | 20426.5655 | 47.9735 | 399.4204
5.7917 | 20457.7362 | 48.1995 | 401.1575
5.7986 | 20496.2233 | 48.545 | 402.8881
5.8056 | 20541.9353 | 48.9606 | 404.5227
5.8125 | 20594.7666 | 49.389 | 405.929
5.8194 | 20654.5979 | 49.7718 | 406.8917
5.8264 | 20721.2967 | 50.0977 | 407.2814
5.8333 | 20794.7174 | 50.3757 | 407.0406
5.8403 | 20874.7015 | 50.5586 | 406.1702
5.8472 | 20961.0777 | 50.5853 | 404.7755
5.8542 | 21053.6629 | 50.4214 | 403.0692
5.8611 | 21152.2618 | 50.1031 | 401.204
5.8681 | 21256.6679 | 49.7048 | 399.4068
5.875 | 21366.6632 | 49.2925 | 397.9158
5.8819 | 21482.0194 | 48.9269 | 396.8864
5.8889 | 21602.4977 | 48.6457 | 396.4106
5.8958 | 21727.8498 | 48.4927 | 396.5103
5.9028 | 21857.8176 | 48.4468 | 396.9724
5.9097 | 21992.1348 | 48.4393 | 397.4744
5.9167 | 22130.5262 | 48.4057 | 397.828
5.9236 | 22272.7092 | 48.3435 | 398.0458
5.9306 | 22418.3938 | 48.2802 | 398.1298
5.9375 | 22567.2834 | 48.249 | 398.0483
5.9444 | 22719.0752 | 48.2609 | 397.9093
5.9514 | 22873.4608 | 48.3292 | 397.978
5.9583 | 23030.127 | 48.5058 | 398.4376
5.9653 | 23188.756 | 48.8663 | 399.326
5.9722 | 23349.0267 | 49.4318 | 400.4309
5.9792 | 23510.6143 | 50.2145 | 401.4767
5.9861 | 23673.1919 | 51.255 | 402.264
5.9931 | 23836.4305 | 52.5964 | 402.6622
6 | 24000 | 54.2609 | 402.6138
6.0069 | 24163.5695 | 56.2314 | 402.2111
6.0139 | 24326.8081 | 58.4262 | 401.5103
6.0208 | 24489.3857 | 60.7336 | 400.6231
6.0278 | 24650.9733 | 63.0212 | 399.7919
6.0347 | 24811.244 | 65.1827 | 399.2327
6.0417 | 24969.873 | 67.1148 | 399.0083
6.0486 | 25126.5392 | 68.7751 | 399.2293
6.0556 | 25280.9248 | 70.1973 | 399.9561
6.0625 | 25432.7166 | 71.4361 | 401.0993
6.0694 | 25581.6062 | 72.5261 | 402.5964
6.0764 | 25727.2908 | 73.444 | 404.4515
6.0833 | 25869.4738 | 74.135 | 406.6161
6.0903 | 26007.8652 | 74.4866 | 409.1445
6.0972 | 26142.1824 | 74.3879 | 412.2003
6.1042 | 26272.1502 | 73.7872 | 415.9143
6.1111 | 26397.5023 | 72.7314 | 420.18
6.1181 | 26517.9806 | 71.3443 | 424.8081
6.125 | 26633.3368 | 69.7755 | 429.5737
6.1319 | 26743.3321 | 68.1427 | 434.1285
6.1389 | 26847.7382 | 66.5245 | 438.2413
6.1458 | 26946.3371 | 64.9437 | 441.7339
6.1528 | 27038.9223 | 63.4128 | 444.3645
6.1597 | 27125.2985 | 61.9669 | 446.1427
6.1667 | 27205.2826 | 60.6158 | 447.0952
6.1736 | 27278.7033 | 59.3515 | 447.2099
6.1806 | 27345.4021 | 58.1681 | 446.5272
6.1875 | 27405.2334 | 57.0782 | 445.07
6.1944 | 27458.0647 | 56.1365 | 443.0138
6.2014 | 27503.7767 | 55.3771 | 440.5438
6.2083 | 27542.2638 | 54.7914 | 437.627
6.2153 | 27573.4345 | 54.3594 | 434.2406
6.2222 | 27597.2109 | 54.0536 | 430.5597
6.2292 | 27613.5294 | 53.8432 | 426.7271
6.2361 | 27622.3407 | 53.7105 | 422.701
6.2431 | 27623.61 | 53.6741 | 418.6194
6.25 | 27617.3166 | 53.7705 | 414.7211
6.2569 | 27603.4545 | 53.9913 | 411.1261
6.2639 | 27582.0321 | 54.2784 | 407.9481
6.2708 | 27553.0724 | 54.5693 | 405.4456
6.2778 | 27516.6128 | 54.8224 | 403.7816
6.2847 | 27472.7048 | 54.995 | 402.8165
6.2917 | 27421.4146 | 55.0835 | 402.32
6.2986 | 27362.8223 | 55.1213 | 402.1185
6.3056 | 27297.0219 | 55.1357 | 402.0779
6.3125 | 27224.1214 | 55.1493 | 402.088
6.3194 | 27144.2424 | 55.1365 | 402.1205
6.3264 | 27057.5198 | 55.0481 | 402.2842
6.3333 | 26964.1016 | 54.8461 | 402.831
6.3403 | 26864.1489 | 54.5343 | 404.0008
6.3472 | 26757.8349 | 54.106 | 405.9743
6.3542 | 26645.3455 | 53.6057 | 408.6795
6.3611 | 26526.8782 | 53.1169 | 411.8301
6.3681 | 26402.6419 | 52.7384 | 415.0904
6.375 | 26272.8569 | 52.5345 | 418.126
6.3819 | 26137.7539 | 52.5564 | 420.658
6.3889 | 25997.574 | 52.7832 | 422.4578
6.3958 | 25852.568 | 53.138 | 423.5412
6.4028 | 25702.9961 | 53.4876 | 424.0535
6.4097 | 25549.1272 | 53.6977 | 424.172
6.4167 | 25391.2386 | 53.6921 | 424.183
6.4236 | 25229.6153 | 53.5001 | 424.3959
6.4306 | 25064.5496 | 53.2054 | 425.0858
6.4375 | 24896.3404 | 52.8801 | 426.4612
6.4444 | 24725.293 | 52.6232 | 428.5038
6.4514 | 24551.7177 | 52.5199 | 431.2214
6.4583 | 24375.9304 | 52.5656 | 434.5224
6.4653 | 24198.2507 | 52.7124 | 438.2925
6.4722 | 24019.0025 | 52.913 | 442.4258
6.4792 | 23838.5125 | 53.1472 | 446.6984
6.4861 | 23657.1099 | 53.4515 | 450.8219
6.4931 | 23475.126 | 53.8493 | 454.4273
6.5 | 23292.8932 | 54.3413 | 457.0717
6.5069 | 23110.7445 | 54.8834 | 458.5105
6.5139 | 22929.0131 | 55.4568 | 458.6792
6.5208 | 22748.0312 | 56.0589 | 457.6433
6.5278 | 22568.1299 | 56.6614 | 455.4964
6.5347 | 22389.6387 | 57.246 | 452.3799
6.5417 | 22212.884 | 57.8608 | 448.5815
6.5486 | 22038.1895 | 58.5811 | 444.4361
6.5556 | 21865.875 | 59.4578 | 440.1642
6.5625 | 21696.2558 | 60.4907 | 435.8371
6.5694 | 21529.6425 | 61.6465 | 431.5504
6.5764 | 21366.3398 | 62.809 | 427.4802
6.5833 | 21206.6467 | 63.8139 | 423.687
6.5903 | 21050.855 | 64.5055 | 420.1911
6.5972 | 20899.2497 | 64.8211 | 417.0384
6.6042 | 20752.1076 | 64.7914 | 414.2656
6.6111 | 20609.6975 | 64.4583 | 411.8908
6.6181 | 20472.2792 | 63.8618 | 409.9398
6.625 | 20340.1033 | 63.068 | 408.5225
6.6319 | 20213.4103 | 62.1359 | 407.717
6.6389 | 20092.4308 | 61.052 | 407.5392
6.6458 | 19977.3845 | 59.7758 | 407.999
6.6528 | 19868.48 | 58.3077 | 409.1378
6.6597 | 19765.9144 | 56.7225 | 410.9026
6.6667 | 19669.873 | 55.1446 | 413.1276
6.6736 | 19580.5287 | 53.7028 | 415.5384
6.6806 | 19498.0421 | 52.4877 | 417.928
6.6875 | 19422.5606 | 51.5775 | 420.0626
6.6944 | 19354.2187 | 51.0181 | 421.8497
6.7014 | 19293.1373 | 50.7814 | 423.2589
6.7083 | 19239.424 | 50.8339 | 424.1581
6.7153 | 19193.1721 | 51.132 | 424.5504
6.7222 | 19154.4612 | 51.6125 | 424.619
6.7292 | 19123.3567 | 52.2292 | 424.565
6.7361 | 19099.9097 | 52.9228 | 424.4471
6.7431 | 19084.1569 | 53.6809 | 424.3251
6.75 | 19076.1205 | 54.4918 | 424.2656
6.7569 | 19075.8082 | 55.329 | 424.2177
6.7639 | 19083.2133 | 56.1435 | 424.1653
6.7708 | 19098.3146 | 56.8782 | 424.0266
6.7778 | 19121.0764 | 57.5157 | 423.7819
6.7847 | 19151.4485 | 58.0542 | 423.582
6.7917 | 19189.3666 | 58.5067 | 423.4997
6.7986 | 19234.7521 | 58.9165 | 423.6843
6.8056 | 19287.5126 | 59.3089 | 424.2962
6.8125 | 19347.5415 | 59.6743 | 425.3491
6.8194 | 19414.719 | 60.0158 | 426.8452
6.8264 | 19488.9115 | 60.311 | 428.707
6.8333 | 19569.9726 | 60.6328 | 430.3576
6.8403 | 19657.7426 | 61.2833 | 432.0387
6.8472 | 19752.0497 | 62.0439 | 433.5586
6.8542 | 19852.7097 | 62.775 | 434.8725
6.8611 | 19959.5262 | 63.4183 | 435.9794
6.8681 | 20072.2918 | 63.9553 | 436.88
6.875 | 20190.7876 | 64.3843 | 437.5736
6.8819 | 20314.7842 | 64.7119 | 438.053
6.8889 | 20444.0418 | 64.9492 | 438.3095
6.8958 | 20578.3109 | 65.1082 | 438.3409
6.9028 | 20717.3327 | 65.2001 | 438.1505
6.9097 | 20860.8395 | 65.2342 | 437.741
6.9167 | 21008.5551 | 65.2185 | 437.1151
6.9236 | 21160.1959 | 65.1586 | 436.2773
6.9306 | 21315.4706 | 65.0584 | 435.2323
6.9375 | 21474.0815 | 64.9201 | 433.9846
6.9444 | 21635.7247 | 64.7442 | 432.5364
6.9514 | 21800.0907 | 64.5296 | 430.8876
6.9583 | 21966.8649 | 64.2749 | 429.0378
6.9653 | 22135.7286 | 63.9777 | 426.9851
6.9722 | 22306.3591 | 63.6355 | 424.7271
6.9792 | 22478.4306 | 63.2448 | 422.2635
6.9861 | 22651.615 | 62.8009 | 419.5926
6.9931 | 22825.5819 | 62.2987 | 416.7134
7 | 23000 | 61.7323 | 413.6249
Temp_sine | Disabled
No interpolation | Repeated every 168 hours
Time | T
d | °C
0 | 20
0.0069444 | 20.0545
0.013889 | 20.1091
0.020833 | 20.1636
0.027778 | 20.2181
0.034722 | 20.2727
0.041667 | 20.3272
0.048611 | 20.3817
0.055556 | 20.4362
0.0625 | 20.4907
0.069444 | 20.5451
0.076389 | 20.5996
0.083333 | 20.654
0.090278 | 20.7084
0.097222 | 20.7628
0.10417 | 20.8172
0.11111 | 20.8716
0.11806 | 20.9259
0.125 | 20.9802
0.13194 | 21.0344
0.13889 | 21.0887
0.14583 | 21.1429
0.15278 | 21.197
0.15972 | 21.2512
0.16667 | 21.3053
0.17361 | 21.3593
0.18056 | 21.4133
0.1875 | 21.4673
0.19444 | 21.5212
0.20139 | 21.5751
0.20833 | 21.629
0.21528 | 21.6827
0.22222 | 21.7365
0.22917 | 21.7902
0.23611 | 21.8438
0.24306 | 21.8974
0.25 | 21.9509
0.25694 | 22.0044
0.26389 | 22.0578
0.27083 | 22.1111
0.27778 | 22.1644
0.28472 | 22.2176
0.29167 | 22.2708
0.29861 | 22.3238
0.30556 | 22.3769
0.3125 | 22.4298
0.31944 | 22.4827
0.32639 | 22.5355
0.33333 | 22.5882
0.34028 | 22.6408
0.34722 | 22.6934
0.35417 | 22.7459
0.36111 | 22.7983
0.36806 | 22.8506
0.375 | 22.9028
0.38194 | 22.955
0.38889 | 23.0071
0.39583 | 23.059
0.40278 | 23.1109
0.40972 | 23.1627
0.41667 | 23.2144
0.42361 | 23.266
0.43056 | 23.3175
0.4375 | 23.3689
0.44444 | 23.4202
0.45139 | 23.4714
0.45833 | 23.5225
0.46528 | 23.5735
0.47222 | 23.6244
0.47917 | 23.6752
0.48611 | 23.7258
0.49306 | 23.7764
0.5 | 23.8268
0.50694 | 23.8772
0.51389 | 23.9274
0.52083 | 23.9775
0.52778 | 24.0275
0.53472 | 24.0773
0.54167 | 24.1271
0.54861 | 24.1767
0.55556 | 24.2262
0.5625 | 24.2756
0.56944 | 24.3248
0.57639 | 24.3739
0.58333 | 24.4229
0.59028 | 24.4717
0.59722 | 24.5205
0.60417 | 24.569
0.61111 | 24.6175
0.61806 | 24.6658
0.625 | 24.714
0.63194 | 24.762
0.63889 | 24.8099
0.64583 | 24.8576
0.65278 | 24.9052
0.65972 | 24.9527
0.66667 | 25
0.67361 | 25.0472
0.68056 | 25.0942
0.6875 | 25.141
0.69444 | 25.1877
0.70139 | 25.2343
0.70833 | 25.2807
0.71528 | 25.3269
0.72222 | 25.373
0.72917 | 25.4189
0.73611 | 25.4647
0.74306 | 25.5103
0.75 | 25.5557
0.75694 | 25.601
0.76389 | 25.6461
0.77083 | 25.691
0.77778 | 25.7358
0.78472 | 25.7804
0.79167 | 25.8248
0.79861 | 25.869
0.80556 | 25.9131
0.8125 | 25.957
0.81944 | 26.0007
0.82639 | 26.0443
0.83333 | 26.0876
0.84028 | 26.1308
0.84722 | 26.1738
0.85417 | 26.2166
0.86111 | 26.2592
0.86806 | 26.3017
0.875 | 26.3439
0.88194 | 26.386
0.88889 | 26.4279
0.89583 | 26.4696
0.90278 | 26.5111
0.90972 | 26.5524
0.91667 | 26.5935
0.92361 | 26.6344
0.93056 | 26.6751
0.9375 | 26.7156
0.94444 | 26.7559
0.95139 | 26.796
0.95833 | 26.8359
0.96528 | 26.8756
0.97222 | 26.9151
0.97917 | 26.9544
0.98611 | 26.9935
0.99306 | 27.0324
1 | 27.0711
1.0069 | 27.1095
1.0139 | 27.1478
1.0208 | 27.1858
1.0278 | 27.2236
1.0347 | 27.2612
1.0417 | 27.2986
1.0486 | 27.3358
1.0556 | 27.3728
1.0625 | 27.4095
1.0694 | 27.446
1.0764 | 27.4823
1.0833 | 27.5184
1.0903 | 27.5542
1.0972 | 27.5899
1.1042 | 27.6253
1.1111 | 27.6604
1.1181 | 27.6954
1.125 | 27.7301
1.1319 | 27.7646
1.1389 | 27.7988
1.1458 | 27.8329
1.1528 | 27.8667
1.1597 | 27.9002
1.1667 | 27.9335
1.1736 | 27.9666
1.1806 | 27.9995
1.1875 | 28.0321
1.1944 | 28.0644
1.2014 | 28.0966
1.2083 | 28.1285
1.2153 | 28.1601
1.2222 | 28.1915
1.2292 | 28.2227
1.2361 | 28.2536
1.2431 | 28.2843
1.25 | 28.3147
1.2569 | 28.3449
1.2639 | 28.3748
1.2708 | 28.4045
1.2778 | 28.4339
1.2847 | 28.4631
1.2917 | 28.492
1.2986 | 28.5207
1.3056 | 28.5491
1.3125 | 28.5773
1.3194 | 28.6052
1.3264 | 28.6329
1.3333 | 28.6603
1.3403 | 28.6874
1.3472 | 28.7143
1.3542 | 28.7409
1.3611 | 28.7673
1.3681 | 28.7934
1.375 | 28.8192
1.3819 | 28.8448
1.3889 | 28.8701
1.3958 | 28.8952
1.4028 | 28.9199
1.4097 | 28.9445
1.4167 | 28.9687
1.4236 | 28.9927
1.4306 | 29.0164
1.4375 | 29.0399
1.4444 | 29.0631
1.4514 | 29.086
1.4583 | 29.1086
1.4653 | 29.131
1.4722 | 29.1531
1.4792 | 29.1749
1.4861 | 29.1965
1.4931 | 29.2178
1.5 | 29.2388
1.5069 | 29.2595
1.5139 | 29.28
1.5208 | 29.3002
1.5278 | 29.3201
1.5347 | 29.3397
1.5417 | 29.3591
1.5486 | 29.3781
1.5556 | 29.3969
1.5625 | 29.4154
1.5694 | 29.4337
1.5764 | 29.4516
1.5833 | 29.4693
1.5903 | 29.4867
1.5972 | 29.5038
1.6042 | 29.5206
1.6111 | 29.5372
1.6181 | 29.5534
1.625 | 29.5694
1.6319 | 29.5851
1.6389 | 29.6005
1.6458 | 29.6156
1.6528 | 29.6305
1.6597 | 29.645
1.6667 | 29.6593
1.6736 | 29.6732
1.6806 | 29.6869
1.6875 | 29.7003
1.6944 | 29.7134
1.7014 | 29.7262
1.7083 | 29.7388
1.7153 | 29.751
1.7222 | 29.763
1.7292 | 29.7746
1.7361 | 29.786
1.7431 | 29.7971
1.75 | 29.8079
1.7569 | 29.8183
1.7639 | 29.8285
1.7708 | 29.8385
1.7778 | 29.8481
1.7847 | 29.8574
1.7917 | 29.8664
1.7986 | 29.8752
1.8056 | 29.8836
1.8125 | 29.8918
1.8194 | 29.8996
1.8264 | 29.9072
1.8333 | 29.9144
1.8403 | 29.9214
1.8472 | 29.9281
1.8542 | 29.9345
1.8611 | 29.9406
1.8681 | 29.9464
1.875 | 29.9518
1.8819 | 29.957
1.8889 | 29.9619
1.8958 | 29.9666
1.9028 | 29.9709
1.9097 | 29.9749
1.9167 | 29.9786
1.9236 | 29.982
1.9306 | 29.9851
1.9375 | 29.988
1.9444 | 29.9905
1.9514 | 29.9927
1.9583 | 29.9946
1.9653 | 29.9963
1.9722 | 29.9976
1.9792 | 29.9987
1.9861 | 29.9994
1.9931 | 29.9999
2 | 30
2.0069 | 29.9999
2.0139 | 29.9994
2.0208 | 29.9987
2.0278 | 29.9976
2.0347 | 29.9963
2.0417 | 29.9946
2.0486 | 29.9927
2.0556 | 29.9905
2.0625 | 29.988
2.0694 | 29.9851
2.0764 | 29.982
2.0833 | 29.9786
2.0903 | 29.9749
2.0972 | 29.9709
2.1042 | 29.9666
2.1111 | 29.9619
2.1181 | 29.957
2.125 | 29.9518
2.1319 | 29.9464
2.1389 | 29.9406
2.1458 | 29.9345
2.1528 | 29.9281
2.1597 | 29.9214
2.1667 | 29.9144
2.1736 | 29.9072
2.1806 | 29.8996
2.1875 | 29.8918
2.1944 | 29.8836
2.2014 | 29.8752
2.2083 | 29.8664
2.2153 | 29.8574
2.2222 | 29.8481
2.2292 | 29.8385
2.2361 | 29.8285
2.2431 | 29.8183
2.25 | 29.8079
2.2569 | 29.7971
2.2639 | 29.786
2.2708 | 29.7746
2.2778 | 29.763
2.2847 | 29.751
2.2917 | 29.7388
2.2986 | 29.7262
2.3056 | 29.7134
2.3125 | 29.7003
2.3194 | 29.6869
2.3264 | 29.6732
2.3333 | 29.6593
2.3403 | 29.645
2.3472 | 29.6305
2.3542 | 29.6156
2.3611 | 29.6005
2.3681 | 29.5851
2.375 | 29.5694
2.3819 | 29.5534
2.3889 | 29.5372
2.3958 | 29.5206
2.4028 | 29.5038
2.4097 | 29.4867
2.4167 | 29.4693
2.4236 | 29.4516
2.4306 | 29.4337
2.4375 | 29.4154
2.4444 | 29.3969
2.4514 | 29.3781
2.4583 | 29.3591
2.4653 | 29.3397
2.4722 | 29.3201
2.4792 | 29.3002
2.4861 | 29.28
2.4931 | 29.2595
2.5 | 29.2388
2.5069 | 29.2178
2.5139 | 29.1965
2.5208 | 29.1749
2.5278 | 29.1531
2.5347 | 29.131
2.5417 | 29.1086
2.5486 | 29.086
2.5556 | 29.0631
2.5625 | 29.0399
2.5694 | 29.0164
2.5764 | 28.9927
2.5833 | 28.9687
2.5903 | 28.9445
2.5972 | 28.9199
2.6042 | 28.8952
2.6111 | 28.8701
2.6181 | 28.8448
2.625 | 28.8192
2.6319 | 28.7934
2.6389 | 28.7673
2.6458 | 28.7409
2.6528 | 28.7143
2.6597 | 28.6874
2.6667 | 28.6603
2.6736 | 28.6329
2.6806 | 28.6052
2.6875 | 28.5773
2.6944 | 28.5491
2.7014 | 28.5207
2.7083 | 28.492
2.7153 | 28.4631
2.7222 | 28.4339
2.7292 | 28.4045
2.7361 | 28.3748
2.7431 | 28.3449
2.75 | 28.3147
2.7569 | 28.2843
2.7639 | 28.2536
2.7708 | 28.2227
2.7778 | 28.1915
2.7847 | 28.1601
2.7917 | 28.1285
2.7986 | 28.0966
2.8056 | 28.0644
2.8125 | 28.0321
2.8194 | 27.9995
2.8264 | 27.9666
2.8333 | 27.9335
2.8403 | 27.9002
2.8472 | 27.8667
2.8542 | 27.8329
2.8611 | 27.7988
2.8681 | 27.7646
2.875 | 27.7301
2.8819 | 27.6954
2.8889 | 27.6604
2.8958 | 27.6253
2.9028 | 27.5899
2.9097 | 27.5542
2.9167 | 27.5184
2.9236 | 27.4823
2.9306 | 27.446
2.9375 | 27.4095
2.9444 | 27.3728
2.9514 | 27.3358
2.9583 | 27.2986
2.9653 | 27.2612
2.9722 | 27.2236
2.9792 | 27.1858
2.9861 | 27.1478
2.9931 | 27.1095
3 | 27.0711
3.0069 | 27.0324
3.0139 | 26.9935
3.0208 | 26.9544
3.0278 | 26.9151
3.0347 | 26.8756
3.0417 | 26.8359
3.0486 | 26.796
3.0556 | 26.7559
3.0625 | 26.7156
3.0694 | 26.6751
3.0764 | 26.6344
3.0833 | 26.5935
3.0903 | 26.5524
3.0972 | 26.5111
3.1042 | 26.4696
3.1111 | 26.4279
3.1181 | 26.386
3.125 | 26.3439
3.1319 | 26.3017
3.1389 | 26.2592
3.1458 | 26.2166
3.1528 | 26.1738
3.1597 | 26.1308
3.1667 | 26.0876
3.1736 | 26.0443
3.1806 | 26.0007
3.1875 | 25.957
3.1944 | 25.9131
3.2014 | 25.869
3.2083 | 25.8248
3.2153 | 25.7804
3.2222 | 25.7358
3.2292 | 25.691
3.2361 | 25.6461
3.2431 | 25.601
3.25 | 25.5557
3.2569 | 25.5103
3.2639 | 25.4647
3.2708 | 25.4189
3.2778 | 25.373
3.2847 | 25.3269
3.2917 | 25.2807
3.2986 | 25.2343
3.3056 | 25.1877
3.3125 | 25.141
3.3194 | 25.0942
3.3264 | 25.0472
3.3333 | 25
3.3403 | 24.9527
3.3472 | 24.9052
3.3542 | 24.8576
3.3611 | 24.8099
3.3681 | 24.762
3.375 | 24.714
3.3819 | 24.6658
3.3889 | 24.6175
3.3958 | 24.569
3.4028 | 24.5205
3.4097 | 24.4717
3.4167 | 24.4229
3.4236 | 24.3739
3.4306 | 24.3248
3.4375 | 24.2756
3.4444 | 24.2262
3.4514 | 24.1767
3.4583 | 24.1271
3.4653 | 24.0773
3.4722 | 24.0275
3.4792 | 23.9775
3.4861 | 23.9274
3.4931 | 23.8772
3.5 | 23.8268
3.5069 | 23.7764
3.5139 | 23.7258
3.5208 | 23.6752
3.5278 | 23.6244
3.5347 | 23.5735
3.5417 | 23.5225
3.5486 | 23.4714
3.5556 | 23.4202
3.5625 | 23.3689
3.5694 | 23.3175
3.5764 | 23.266
3.5833 | 23.2144
3.5903 | 23.1627
3.5972 | 23.1109
3.6042 | 23.059
3.6111 | 23.0071
3.6181 | 22.955
3.625 | 22.9028
3.6319 | 22.8506
3.6389 | 22.7983
3.6458 | 22.7459
3.6528 | 22.6934
3.6597 | 22.6408
3.6667 | 22.5882
3.6736 | 22.5355
3.6806 | 22.4827
3.6875 | 22.4298
3.6944 | 22.3769
3.7014 | 22.3238
3.7083 | 22.2708
3.7153 | 22.2176
3.7222 | 22.1644
3.7292 | 22.1111
3.7361 | 22.0578
3.7431 | 22.0044
3.75 | 21.9509
3.7569 | 21.8974
3.7639 | 21.8438
3.7708 | 21.7902
3.7778 | 21.7365
3.7847 | 21.6827
3.7917 | 21.629
3.7986 | 21.5751
3.8056 | 21.5212
3.8125 | 21.4673
3.8194 | 21.4133
3.8264 | 21.3593
3.8333 | 21.3053
3.8403 | 21.2512
3.8472 | 21.197
3.8542 | 21.1429
3.8611 | 21.0887
3.8681 | 21.0344
3.875 | 20.9802
3.8819 | 20.9259
3.8889 | 20.8716
3.8958 | 20.8172
3.9028 | 20.7628
3.9097 | 20.7084
3.9167 | 20.654
3.9236 | 20.5996
3.9306 | 20.5451
3.9375 | 20.4907
3.9444 | 20.4362
3.9514 | 20.3817
3.9583 | 20.3272
3.9653 | 20.2727
3.9722 | 20.2181
3.9792 | 20.1636
3.9861 | 20.1091
3.9931 | 20.0545
4 | 20
4.0069 | 19.9455
4.0139 | 19.8909
4.0208 | 19.8364
4.0278 | 19.7819
4.0347 | 19.7273
4.0417 | 19.6728
4.0486 | 19.6183
4.0556 | 19.5638
4.0625 | 19.5093
4.0694 | 19.4549
4.0764 | 19.4004
4.0833 | 19.346
4.0903 | 19.2916
4.0972 | 19.2372
4.1042 | 19.1828
4.1111 | 19.1284
4.1181 | 19.0741
4.125 | 19.0198
4.1319 | 18.9656
4.1389 | 18.9113
4.1458 | 18.8571
4.1528 | 18.803
4.1597 | 18.7488
4.1667 | 18.6947
4.1736 | 18.6407
4.1806 | 18.5867
4.1875 | 18.5327
4.1944 | 18.4788
4.2014 | 18.4249
4.2083 | 18.371
4.2153 | 18.3173
4.2222 | 18.2635
4.2292 | 18.2098
4.2361 | 18.1562
4.2431 | 18.1026
4.25 | 18.0491
4.2569 | 17.9956
4.2639 | 17.9422
4.2708 | 17.8889
4.2778 | 17.8356
4.2847 | 17.7824
4.2917 | 17.7292
4.2986 | 17.6762
4.3056 | 17.6231
4.3125 | 17.5702
4.3194 | 17.5173
4.3264 | 17.4645
4.3333 | 17.4118
4.3403 | 17.3592
4.3472 | 17.3066
4.3542 | 17.2541
4.3611 | 17.2017
4.3681 | 17.1494
4.375 | 17.0972
4.3819 | 17.045
4.3889 | 16.9929
4.3958 | 16.941
4.4028 | 16.8891
4.4097 | 16.8373
4.4167 | 16.7856
4.4236 | 16.734
4.4306 | 16.6825
4.4375 | 16.6311
4.4444 | 16.5798
4.4514 | 16.5286
4.4583 | 16.4775
4.4653 | 16.4265
4.4722 | 16.3756
4.4792 | 16.3248
4.4861 | 16.2742
4.4931 | 16.2236
4.5 | 16.1732
4.5069 | 16.1228
4.5139 | 16.0726
4.5208 | 16.0225
4.5278 | 15.9725
4.5347 | 15.9227
4.5417 | 15.8729
4.5486 | 15.8233
4.5556 | 15.7738
4.5625 | 15.7244
4.5694 | 15.6752
4.5764 | 15.6261
4.5833 | 15.5771
4.5903 | 15.5283
4.5972 | 15.4795
4.6042 | 15.431
4.6111 | 15.3825
4.6181 | 15.3342
4.625 | 15.286
4.6319 | 15.238
4.6389 | 15.1901
4.6458 | 15.1424
4.6528 | 15.0948
4.6597 | 15.0473
4.6667 | 15
4.6736 | 14.9528
4.6806 | 14.9058
4.6875 | 14.859
4.6944 | 14.8123
4.7014 | 14.7657
4.7083 | 14.7193
4.7153 | 14.6731
4.7222 | 14.627
4.7292 | 14.5811
4.7361 | 14.5353
4.7431 | 14.4897
4.75 | 14.4443
4.7569 | 14.399
4.7639 | 14.3539
4.7708 | 14.309
4.7778 | 14.2642
4.7847 | 14.2196
4.7917 | 14.1752
4.7986 | 14.131
4.8056 | 14.0869
4.8125 | 14.043
4.8194 | 13.9993
4.8264 | 13.9557
4.8333 | 13.9124
4.8403 | 13.8692
4.8472 | 13.8262
4.8542 | 13.7834
4.8611 | 13.7408
4.8681 | 13.6983
4.875 | 13.6561
4.8819 | 13.614
4.8889 | 13.5721
4.8958 | 13.5304
4.9028 | 13.4889
4.9097 | 13.4476
4.9167 | 13.4065
4.9236 | 13.3656
4.9306 | 13.3249
4.9375 | 13.2844
4.9444 | 13.2441
4.9514 | 13.204
4.9583 | 13.1641
4.9653 | 13.1244
4.9722 | 13.0849
4.9792 | 13.0456
4.9861 | 13.0065
4.9931 | 12.9676
5 | 12.9289
5.0069 | 12.8905
5.0139 | 12.8522
5.0208 | 12.8142
5.0278 | 12.7764
5.0347 | 12.7388
5.0417 | 12.7014
5.0486 | 12.6642
5.0556 | 12.6272
5.0625 | 12.5905
5.0694 | 12.554
5.0764 | 12.5177
5.0833 | 12.4816
5.0903 | 12.4458
5.0972 | 12.4101
5.1042 | 12.3747
5.1111 | 12.3396
5.1181 | 12.3046
5.125 | 12.2699
5.1319 | 12.2354
5.1389 | 12.2012
5.1458 | 12.1671
5.1528 | 12.1333
5.1597 | 12.0998
5.1667 | 12.0665
5.1736 | 12.0334
5.1806 | 12.0005
5.1875 | 11.9679
5.1944 | 11.9356
5.2014 | 11.9034
5.2083 | 11.8715
5.2153 | 11.8399
5.2222 | 11.8085
5.2292 | 11.7773
5.2361 | 11.7464
5.2431 | 11.7157
5.25 | 11.6853
5.2569 | 11.6551
5.2639 | 11.6252
5.2708 | 11.5955
5.2778 | 11.5661
5.2847 | 11.5369
5.2917 | 11.508
5.2986 | 11.4793
5.3056 | 11.4509
5.3125 | 11.4227
5.3194 | 11.3948
5.3264 | 11.3671
5.3333 | 11.3397
5.3403 | 11.3126
5.3472 | 11.2857
5.3542 | 11.2591
5.3611 | 11.2327
5.3681 | 11.2066
5.375 | 11.1808
5.3819 | 11.1552
5.3889 | 11.1299
5.3958 | 11.1048
5.4028 | 11.0801
5.4097 | 11.0555
5.4167 | 11.0313
5.4236 | 11.0073
5.4306 | 10.9836
5.4375 | 10.9601
5.4444 | 10.9369
5.4514 | 10.914
5.4583 | 10.8914
5.4653 | 10.869
5.4722 | 10.8469
5.4792 | 10.8251
5.4861 | 10.8035
5.4931 | 10.7822
5.5 | 10.7612
5.5069 | 10.7405
5.5139 | 10.72
5.5208 | 10.6998
5.5278 | 10.6799
5.5347 | 10.6603
5.5417 | 10.6409
5.5486 | 10.6219
5.5556 | 10.6031
5.5625 | 10.5846
5.5694 | 10.5663
5.5764 | 10.5484
5.5833 | 10.5307
5.5903 | 10.5133
5.5972 | 10.4962
5.6042 | 10.4794
5.6111 | 10.4628
5.6181 | 10.4466
5.625 | 10.4306
5.6319 | 10.4149
5.6389 | 10.3995
5.6458 | 10.3844
5.6528 | 10.3695
5.6597 | 10.355
5.6667 | 10.3407
5.6736 | 10.3268
5.6806 | 10.3131
5.6875 | 10.2997
5.6944 | 10.2866
5.7014 | 10.2738
5.7083 | 10.2612
5.7153 | 10.249
5.7222 | 10.237
5.7292 | 10.2254
5.7361 | 10.214
5.7431 | 10.2029
5.75 | 10.1921
5.7569 | 10.1817
5.7639 | 10.1715
5.7708 | 10.1615
5.7778 | 10.1519
5.7847 | 10.1426
5.7917 | 10.1336
5.7986 | 10.1248
5.8056 | 10.1164
5.8125 | 10.1082
5.8194 | 10.1004
5.8264 | 10.0928
5.8333 | 10.0856
5.8403 | 10.0786
5.8472 | 10.0719
5.8542 | 10.0655
5.8611 | 10.0594
5.8681 | 10.0536
5.875 | 10.0482
5.8819 | 10.043
5.8889 | 10.0381
5.8958 | 10.0334
5.9028 | 10.0291
5.9097 | 10.0251
5.9167 | 10.0214
5.9236 | 10.018
5.9306 | 10.0149
5.9375 | 10.012
5.9444 | 10.0095
5.9514 | 10.0073
5.9583 | 10.0054
5.9653 | 10.0037
5.9722 | 10.0024
5.9792 | 10.0013
5.9861 | 10.0006
5.9931 | 10.0001
6 | 10
6.0069 | 10.0001
6.0139 | 10.0006
6.0208 | 10.0013
6.0278 | 10.0024
6.0347 | 10.0037
6.0417 | 10.0054
6.0486 | 10.0073
6.0556 | 10.0095
6.0625 | 10.012
6.0694 | 10.0149
6.0764 | 10.018
6.0833 | 10.0214
6.0903 | 10.0251
6.0972 | 10.0291
6.1042 | 10.0334
6.1111 | 10.0381
6.1181 | 10.043
6.125 | 10.0482
6.1319 | 10.0536
6.1389 | 10.0594
6.1458 | 10.0655
6.1528 | 10.0719
6.1597 | 10.0786
6.1667 | 10.0856
6.1736 | 10.0928
6.1806 | 10.1004
6.1875 | 10.1082
6.1944 | 10.1164
6.2014 | 10.1248
6.2083 | 10.1336
6.2153 | 10.1426
6.2222 | 10.1519
6.2292 | 10.1615
6.2361 | 10.1715
6.2431 | 10.1817
6.25 | 10.1921
6.2569 | 10.2029
6.2639 | 10.214
6.2708 | 10.2254
6.2778 | 10.237
6.2847 | 10.249
6.2917 | 10.2612
6.2986 | 10.2738
6.3056 | 10.2866
6.3125 | 10.2997
6.3194 | 10.3131
6.3264 | 10.3268
6.3333 | 10.3407
6.3403 | 10.355
6.3472 | 10.3695
6.3542 | 10.3844
6.3611 | 10.3995
6.3681 | 10.4149
6.375 | 10.4306
6.3819 | 10.4466
6.3889 | 10.4628
6.3958 | 10.4794
6.4028 | 10.4962
6.4097 | 10.5133
6.4167 | 10.5307
6.4236 | 10.5484
6.4306 | 10.5663
6.4375 | 10.5846
6.4444 | 10.6031
6.4514 | 10.6219
6.4583 | 10.6409
6.4653 | 10.6603
6.4722 | 10.6799
6.4792 | 10.6998
6.4861 | 10.72
6.4931 | 10.7405
6.5 | 10.7612
6.5069 | 10.7822
6.5139 | 10.8035
6.5208 | 10.8251
6.5278 | 10.8469
6.5347 | 10.869
6.5417 | 10.8914
6.5486 | 10.914
6.5556 | 10.9369
6.5625 | 10.9601
6.5694 | 10.9836
6.5764 | 11.0073
6.5833 | 11.0313
6.5903 | 11.0555
6.5972 | 11.0801
6.6042 | 11.1048
6.6111 | 11.1299
6.6181 | 11.1552
6.625 | 11.1808
6.6319 | 11.2066
6.6389 | 11.2327
6.6458 | 11.2591
6.6528 | 11.2857
6.6597 | 11.3126
6.6667 | 11.3397
6.6736 | 11.3671
6.6806 | 11.3948
6.6875 | 11.4227
6.6944 | 11.4509
6.7014 | 11.4793
6.7083 | 11.508
6.7153 | 11.5369
6.7222 | 11.5661
6.7292 | 11.5955
6.7361 | 11.6252
6.7431 | 11.6551
6.75 | 11.6853
6.7569 | 11.7157
6.7639 | 11.7464
6.7708 | 11.7773
6.7778 | 11.8085
6.7847 | 11.8399
6.7917 | 11.8715
6.7986 | 11.9034
6.8056 | 11.9356
6.8125 | 11.9679
6.8194 | 12.0005
6.8264 | 12.0334
6.8333 | 12.0665
6.8403 | 12.0998
6.8472 | 12.1333
6.8542 | 12.1671
6.8611 | 12.2012
6.8681 | 12.2354
6.875 | 12.2699
6.8819 | 12.3046
6.8889 | 12.3396
6.8958 | 12.3747
6.9028 | 12.4101
6.9097 | 12.4458
6.9167 | 12.4816
6.9236 | 12.5177
6.9306 | 12.554
6.9375 | 12.5905
6.9444 | 12.6272
6.9514 | 12.6642
6.9583 | 12.7014
6.9653 | 12.7388
6.9722 | 12.7764
6.9792 | 12.8142
6.9861 | 12.8522
6.9931 | 12.8905
7 | 12.9289
Table2 | Disabled
No interpolation
Time | T
d | °C
0 | 20
3.5 | 10
Table3 | Disabled
No interpolation
Time | Q | TKN
d | m3/d | g N/m3
0 | 24000 | 43.3218
0.0069444 | 24185.3856 | 42.2981
0.013889 | 24370.4379 | 41.3464
0.020833 | 24554.8239 | 40.4653
0.027778 | 24738.2121 | 39.6523
0.034722 | 24920.273 | 38.9053
0.041667 | 25100.6793 | 38.2222
0.048611 | 25279.1072 | 37.6015
0.055556 | 25455.2363 | 37.0411
0.0625 | 25628.7509 | 36.5384
0.069444 | 25799.3399 | 36.0913
0.076389 | 25966.6981 | 35.698
0.083333 | 26130.5262 | 35.3566
0.090278 | 26290.5316 | 35.0655
0.097222 | 26446.4291 | 34.8235
0.10417 | 26597.9412 | 34.6299
0.11111 | 26744.7986 | 34.4847
0.11806 | 26886.7411 | 34.389
0.125 | 27023.5174 | 34.3457
0.13194 | 27154.8866 | 34.3605
0.13889 | 27280.6174 | 34.4425
0.14583 | 27400.4896 | 34.6048
0.15278 | 27514.2941 | 34.8662
0.15972 | 27621.833 | 35.25
0.16667 | 27722.9207 | 35.7641
0.17361 | 27817.3834 | 36.3406
0.18056 | 27905.0602 | 36.7747
0.1875 | 27985.8028 | 37.1278
0.19444 | 28059.4763 | 37.3677
0.20139 | 28125.9589 | 37.4431
0.20833 | 28185.1428 | 37.3201
0.21528 | 28236.9336 | 37.0232
0.22222 | 28281.2512 | 36.615
0.22917 | 28318.0295 | 36.1481
0.23611 | 28347.2168 | 35.6529
0.24306 | 28368.7758 | 35.161
0.25 | 28382.6834 | 34.6947
0.25694 | 28388.9313 | 34.2381
0.26389 | 28387.5255 | 33.7857
0.27083 | 28378.4865 | 33.3517
0.27778 | 28361.8493 | 32.955
0.28472 | 28337.6632 | 32.602
0.29167 | 28305.992 | 32.2744
0.29861 | 28266.9133 | 31.9664
0.30556 | 28220.5191 | 31.7094
0.3125 | 28166.9149 | 31.532
0.31944 | 28106.2199 | 31.4514
0.32639 | 28038.5669 | 31.4879
0.33333 | 27964.1016 | 31.6526
0.34028 | 27882.9827 | 31.9402
0.34722 | 27795.3814 | 32.3297
0.35417 | 27701.4812 | 32.8093
0.36111 | 27601.4774 | 33.3602
0.36806 | 27495.5768 | 33.9627
0.375 | 27383.9974 | 34.6052
0.38194 | 27266.9678 | 35.2777
0.38889 | 27144.7269 | 35.9827
0.39583 | 27017.5234 | 36.7297
0.40278 | 26885.6154 | 37.5163
0.40972 | 26749.2697 | 38.307
0.41667 | 26608.7614 | 39.0385
0.42361 | 26464.3736 | 39.6508
0.43056 | 26316.3965 | 40.1065
0.4375 | 26165.127 | 40.3948
0.44444 | 26010.8682 | 40.5377
0.45139 | 25853.9287 | 40.5856
0.45833 | 25694.622 | 40.5872
0.46528 | 25533.2662 | 40.5601
0.47222 | 25370.1829 | 40.5157
0.47917 | 25205.6971 | 40.4888
0.48611 | 25040.136 | 40.4907
0.49306 | 24873.8291 | 40.4855
0.5 | 24707.1068 | 40.4295
0.50694 | 24540.3004 | 40.2797
0.51389 | 24373.741 | 39.9902
0.52083 | 24207.7593 | 39.5265
0.52778 | 24042.6846 | 38.8894
0.53472 | 23878.8444 | 38.1231
0.54167 | 23716.5636 | 37.3108
0.54861 | 23556.1641 | 36.5472
0.55556 | 23397.9639 | 35.8832
0.5625 | 23242.2767 | 35.3493
0.56944 | 23089.4114 | 34.9769
0.57639 | 22939.6713 | 34.7788
0.58333 | 22793.3533 | 34.7405
0.59028 | 22650.7481 | 34.8472
0.59722 | 22512.1389 | 35.1053
0.60417 | 22377.801 | 35.5069
0.61111 | 22248.0016 | 36.0065
0.61806 | 22122.9991 | 36.5746
0.625 | 22003.0425 | 37.202
0.63194 | 21888.371 | 37.8654
0.63889 | 21779.2137 | 38.5433
0.64583 | 21675.7888 | 39.1982
0.65278 | 21578.3037 | 39.7967
0.65972 | 21486.9541 | 40.3305
0.66667 | 21401.9238 | 40.7877
0.67361 | 21323.3846 | 41.1676
0.68056 | 21251.4956 | 41.4833
0.6875 | 21186.4031 | 41.7561
0.69444 | 21128.2404 | 42.0062
0.70139 | 21077.127 | 42.2439
0.70833 | 21033.1694 | 42.4434
0.71528 | 20996.4599 | 42.559
0.72222 | 20967.0768 | 42.5393
0.72917 | 20945.0844 | 42.322
0.73611 | 20930.5327 | 41.8605
0.74306 | 20923.4573 | 41.1338
0.75 | 20923.8795 | 40.1724
0.75694 | 20931.806 | 39.0227
0.76389 | 20947.2291 | 37.7426
0.77083 | 20970.1265 | 36.3774
0.77778 | 21000.4616 | 34.9718
0.78472 | 21038.1835 | 33.5999
0.79167 | 21083.2268 | 32.3375
0.79861 | 21135.5123 | 31.2382
0.80556 | 21194.9465 | 30.3266
0.8125 | 21261.4222 | 29.6047
0.81944 | 21334.8187 | 29.0456
0.82639 | 21415.0018 | 28.6186
0.83333 | 21501.8242 | 28.3141
0.84028 | 21595.1258 | 28.1144
0.84722 | 21694.7339 | 27.9802
0.85417 | 21800.4636 | 27.9138
0.86111 | 21912.1182 | 27.9328
0.86806 | 22029.4895 | 28.0624
0.875 | 22152.3582 | 28.3099
0.88194 | 22280.4942 | 28.683
0.88889 | 22413.6573 | 29.1768
0.89583 | 22551.5976 | 29.7739
0.90278 | 22694.0558 | 30.4647
0.90972 | 22840.7637 | 31.2232
0.91667 | 22991.4449 | 32.0097
0.92361 | 23145.8152 | 32.7828
0.93056 | 23303.5833 | 33.4912
0.9375 | 23464.451 | 34.072
0.94444 | 23628.1141 | 34.4676
0.95139 | 23794.2629 | 34.6325
0.95833 | 23962.5827 | 34.5291
0.96528 | 24132.7545 | 34.1365
0.97222 | 24304.4555 | 33.4906
0.97917 | 24477.3598 | 32.6442
0.98611 | 24651.1391 | 31.6803
0.99306 | 24825.463 | 30.6935
1 | 25000 | 29.7307
1.0069 | 25174.4181 | 28.8152
1.0139 | 25348.385 | 27.9942
1.0208 | 25521.5694 | 27.2963
1.0278 | 25693.6409 | 26.7291
1.0347 | 25864.2714 | 26.3003
1.0417 | 26033.1351 | 26.0143
1.0486 | 26199.9093 | 25.8657
1.0556 | 26364.2753 | 25.8442
1.0625 | 26525.9185 | 25.9651
1.0694 | 26684.5294 | 26.2198
1.0764 | 26839.8041 | 26.5924
1.0833 | 26991.4449 | 27.088
1.0903 | 27139.1605 | 27.6896
1.0972 | 27282.6673 | 28.3798
1.1042 | 27421.6891 | 29.1464
1.1111 | 27555.9582 | 29.9899
1.1181 | 27685.2158 | 30.8969
1.125 | 27809.2124 | 31.826
1.1319 | 27927.7082 | 32.7382
1.1389 | 28040.4738 | 33.613
1.1458 | 28147.2903 | 34.4493
1.1528 | 28247.9503 | 35.2613
1.1597 | 28342.2574 | 36.0507
1.1667 | 28430.0274 | 36.8176
1.1736 | 28511.0885 | 37.5447
1.1806 | 28585.281 | 38.2152
1.1875 | 28652.4585 | 38.8399
1.1944 | 28712.4874 | 39.4274
1.2014 | 28765.2479 | 39.9967
1.2083 | 28810.6334 | 40.5518
1.2153 | 28848.5515 | 41.0905
1.2222 | 28878.9236 | 41.6088
1.2292 | 28901.6854 | 42.0989
1.2361 | 28916.7867 | 42.5302
1.2431 | 28924.1918 | 42.8335
1.25 | 28923.8795 | 42.9459
1.2569 | 28915.8431 | 42.8378
1.2639 | 28900.0903 | 42.4981
1.2708 | 28876.6433 | 41.9318
1.2778 | 28845.5388 | 41.1732
1.2847 | 28806.8279 | 40.2707
1.2917 | 28760.576 | 39.2855
1.2986 | 28706.8627 | 38.2773
1.3056 | 28645.7813 | 37.3335
1.3125 | 28577.4394 | 36.4995
1.3194 | 28501.9579 | 35.7857
1.3264 | 28419.4713 | 35.1913
1.3333 | 28330.127 | 34.7296
1.3403 | 28234.0856 | 34.4095
1.3472 | 28131.52 | 34.229
1.3542 | 28022.6155 | 34.1708
1.3611 | 27907.5692 | 34.217
1.3681 | 27786.5897 | 34.3636
1.375 | 27659.8967 | 34.6072
1.3819 | 27527.7208 | 34.9634
1.3889 | 27390.3025 | 35.4863
1.3958 | 27247.8924 | 36.2338
1.4028 | 27100.7503 | 37.2087
1.4097 | 26949.145 | 38.3992
1.4167 | 26793.3533 | 39.7429
1.4236 | 26633.6602 | 41.1349
1.4306 | 26470.3575 | 42.4781
1.4375 | 26303.7442 | 43.6912
1.4444 | 26134.125 | 44.7191
1.4514 | 25961.8105 | 45.5286
1.4583 | 25787.116 | 46.1118
1.4653 | 25610.3613 | 46.4596
1.4722 | 25431.8701 | 46.5567
1.4792 | 25251.9688 | 46.3765
1.4861 | 25070.9869 | 45.9167
1.4931 | 24889.2555 | 45.2149
1.5 | 24707.1068 | 44.3375
1.5069 | 24524.874 | 43.3313
1.5139 | 24342.8901 | 42.2448
1.5208 | 24161.4875 | 41.1237
1.5278 | 23980.9975 | 40.0091
1.5347 | 23801.7493 | 38.9368
1.5417 | 23624.0696 | 37.9526
1.5486 | 23448.2823 | 37.1116
1.5556 | 23274.707 | 36.449
1.5625 | 23103.6596 | 35.9396
1.5694 | 22935.4504 | 35.5391
1.5764 | 22770.3847 | 35.2384
1.5833 | 22608.7614 | 35.055
1.5903 | 22450.8728 | 35.0047
1.5972 | 22297.0039 | 35.0954
1.6042 | 22147.432 | 35.327
1.6111 | 22002.426 | 35.6873
1.6181 | 21862.2461 | 36.1694
1.625 | 21727.1431 | 36.7726
1.6319 | 21597.3581 | 37.5056
1.6389 | 21473.1218 | 38.3564
1.6458 | 21354.6545 | 39.2741
1.6528 | 21242.1651 | 40.2372
1.6597 | 21135.8511 | 41.2085
1.6667 | 21035.8984 | 42.1209
1.6736 | 20942.4802 | 42.8951
1.6806 | 20855.7576 | 43.4984
1.6875 | 20775.8786 | 43.9377
1.6944 | 20702.9781 | 44.2192
1.7014 | 20637.1777 | 44.3668
1.7083 | 20578.5854 | 44.436
1.7153 | 20527.2952 | 44.463
1.7222 | 20483.3872 | 44.4446
1.7292 | 20446.9276 | 44.3365
1.7361 | 20417.9679 | 44.1179
1.7431 | 20396.5455 | 43.8037
1.75 | 20382.6834 | 43.3942
1.7569 | 20376.39 | 42.8799
1.7639 | 20377.6593 | 42.2575
1.7708 | 20386.4706 | 41.5364
1.7778 | 20402.7891 | 40.7429
1.7847 | 20426.5655 | 39.9024
1.7917 | 20457.7362 | 39.033
1.7986 | 20496.2233 | 38.1675
1.8056 | 20541.9353 | 37.3486
1.8125 | 20594.7666 | 36.6123
1.8194 | 20654.5979 | 35.9804
1.8264 | 20721.2967 | 35.4261
1.8333 | 20794.7174 | 34.903
1.8403 | 20874.7015 | 34.3967
1.8472 | 20961.0777 | 33.91
1.8542 | 21053.6629 | 33.444
1.8611 | 21152.2618 | 32.9977
1.8681 | 21256.6679 | 32.5833
1.875 | 21366.6632 | 32.2237
1.8819 | 21482.0194 | 31.9298
1.8889 | 21602.4977 | 31.6945
1.8958 | 21727.8498 | 31.5
1.9028 | 21857.8176 | 31.3559
1.9097 | 21992.1348 | 31.2708
1.9167 | 22130.5262 | 31.2414
1.9236 | 22272.7092 | 31.2782
1.9306 | 22418.3938 | 31.4016
1.9375 | 22567.2834 | 31.6222
1.9444 | 22719.0752 | 31.9554
1.9514 | 22873.4608 | 32.385
1.9583 | 23030.127 | 32.879
1.9653 | 23188.756 | 33.3978
1.9722 | 23349.0267 | 33.8821
1.9792 | 23510.6143 | 34.2729
1.9861 | 23673.1919 | 34.5307
1.9931 | 23836.4305 | 34.6359
2 | 24000 | 34.5875
2.0069 | 24163.5695 | 34.4104
2.0139 | 24326.8081 | 34.1611
2.0208 | 24489.3857 | 33.8808
2.0278 | 24650.9733 | 33.6064
2.0347 | 24811.244 | 33.367
2.0417 | 24969.873 | 33.184
2.0486 | 25126.5392 | 33.0594
2.0556 | 25280.9248 | 32.9888
2.0625 | 25432.7166 | 32.9781
2.0694 | 25581.6062 | 33.0315
2.0764 | 25727.2908 | 33.1488
2.0833 | 25869.4738 | 33.3148
2.0903 | 26007.8652 | 33.4968
2.0972 | 26142.1824 | 33.6703
2.1042 | 26272.1502 | 33.8356
2.1111 | 26397.5023 | 34.0081
2.1181 | 26517.9806 | 34.1917
2.125 | 26633.3368 | 34.3805
2.1319 | 26743.3321 | 34.5802
2.1389 | 26847.7382 | 34.7646
2.1458 | 26946.3371 | 34.9049
2.1528 | 27038.9223 | 34.9924
2.1597 | 27125.2985 | 35.0408
2.1667 | 27205.2826 | 35.0916
2.1736 | 27278.7033 | 35.1553
2.1806 | 27345.4021 | 35.2254
2.1875 | 27405.2334 | 35.302
2.1944 | 27458.0647 | 35.3864
2.2014 | 27503.7767 | 35.488
2.2083 | 27542.2638 | 35.5954
2.2153 | 27573.4345 | 35.699
2.2222 | 27597.2109 | 35.7972
2.2292 | 27613.5294 | 35.8735
2.2361 | 27622.3407 | 35.921
2.2431 | 27623.61 | 35.9368
2.25 | 27617.3166 | 35.9616
2.2569 | 27603.4545 | 36.0659
2.2639 | 27582.0321 | 36.2848
2.2708 | 27553.0724 | 36.6079
2.2778 | 27516.6128 | 37.0287
2.2847 | 27472.7048 | 37.5431
2.2917 | 27421.4146 | 38.1427
2.2986 | 27362.8223 | 38.7816
2.3056 | 27297.0219 | 39.4088
2.3125 | 27224.1214 | 39.9682
2.3194 | 27144.2424 | 40.4235
2.3264 | 27057.5198 | 40.74
2.3333 | 26964.1016 | 40.8779
2.3403 | 26864.1489 | 40.8483
2.3472 | 26757.8349 | 40.684
2.3542 | 26645.3455 | 40.3921
2.3611 | 26526.8782 | 39.9896
2.3681 | 26402.6419 | 39.4896
2.375 | 26272.8569 | 38.9186
2.3819 | 26137.7539 | 38.3032
2.3889 | 25997.574 | 37.6811
2.3958 | 25852.568 | 37.1188
2.4028 | 25702.9961 | 36.7016
2.4097 | 25549.1272 | 36.4968
2.4167 | 25391.2386 | 36.4873
2.4236 | 25229.6153 | 36.6266
2.4306 | 25064.5496 | 36.9059
2.4375 | 24896.3404 | 37.3227
2.4444 | 24725.293 | 37.8539
2.4514 | 24551.7177 | 38.4536
2.4583 | 24375.9304 | 39.0588
2.4653 | 24198.2507 | 39.6235
2.4722 | 24019.0025 | 40.1104
2.4792 | 23838.5125 | 40.5156
2.4861 | 23657.1099 | 40.8419
2.4931 | 23475.126 | 41.0951
2.5 | 23292.8932 | 41.2597
2.5069 | 23110.7445 | 41.3049
2.5139 | 22929.0131 | 41.2181
2.5208 | 22748.0312 | 40.9712
2.5278 | 22568.1299 | 40.5614
2.5347 | 22389.6387 | 40.0227
2.5417 | 22212.884 | 39.3839
2.5486 | 22038.1895 | 38.6724
2.5556 | 21865.875 | 37.8774
2.5625 | 21696.2558 | 36.9628
2.5694 | 21529.6425 | 35.9387
2.5764 | 21366.3398 | 34.8436
2.5833 | 21206.6467 | 33.7236
2.5903 | 21050.855 | 32.5979
2.5972 | 20899.2497 | 31.4455
2.6042 | 20752.1076 | 30.2715
2.6111 | 20609.6975 | 29.1405
2.6181 | 20472.2792 | 28.1144
2.625 | 20340.1033 | 27.2182
2.6319 | 20213.4103 | 26.4535
2.6389 | 20092.4308 | 25.813
2.6458 | 19977.3845 | 25.2791
2.6528 | 19868.48 | 24.8552
2.6597 | 19765.9144 | 24.5561
2.6667 | 19669.873 | 24.4132
2.6736 | 19580.5287 | 24.4352
2.6806 | 19498.0421 | 24.5944
2.6875 | 19422.5606 | 24.866
2.6944 | 19354.2187 | 25.2474
2.7014 | 19293.1373 | 25.7139
2.7083 | 19239.424 | 26.234
2.7153 | 19193.1721 | 26.7951
2.7222 | 19154.4612 | 27.3883
2.7292 | 19123.3567 | 27.9915
2.7361 | 19099.9097 | 28.5803
2.7431 | 19084.1569 | 29.1184
2.75 | 19076.1205 | 29.6032
2.7569 | 19075.8082 | 30.07
2.7639 | 19083.2133 | 30.5511
2.7708 | 19098.3146 | 31.0471
2.7778 | 19121.0764 | 31.5752
2.7847 | 19151.4485 | 32.1584
2.7917 | 19189.3666 | 32.8056
2.7986 | 19234.7521 | 33.5236
2.8056 | 19287.5126 | 34.2977
2.8125 | 19347.5415 | 35.1011
2.8194 | 19414.719 | 35.8862
2.8264 | 19488.9115 | 36.6148
2.8333 | 19569.9726 | 37.2798
2.8403 | 19657.7426 | 37.8887
2.8472 | 19752.0497 | 38.445
2.8542 | 19852.7097 | 38.9613
2.8611 | 19959.5262 | 39.4619
2.8681 | 20072.2918 | 39.9767
2.875 | 20190.7876 | 40.5299
2.8819 | 20314.7842 | 41.1268
2.8889 | 20444.0418 | 41.7537
2.8958 | 20578.3109 | 42.4039
2.9028 | 20717.3327 | 43.0724
2.9097 | 20860.8395 | 43.716
2.9167 | 21008.5551 | 44.2791
2.9236 | 21160.1959 | 44.6931
2.9306 | 21315.4706 | 44.9169
2.9375 | 21474.0815 | 44.97
2.9444 | 21635.7247 | 44.8715
2.9514 | 21800.0907 | 44.5876
2.9583 | 21966.8649 | 44.074
2.9653 | 22135.7286 | 43.3281
2.9722 | 22306.3591 | 42.3715
2.9792 | 22478.4306 | 41.2359
2.9861 | 22651.615 | 39.9632
2.9931 | 22825.5819 | 38.5998
3 | 23000 | 37.1824
3.0069 | 23174.537 | 35.7493
3.0139 | 23348.8609 | 34.3471
3.0208 | 23522.6402 | 33.0033
3.0278 | 23695.5445 | 31.734
3.0347 | 23867.2455 | 30.5339
3.0417 | 24037.4173 | 29.4096
3.0486 | 24205.7371 | 28.3705
3.0556 | 24371.8859 | 27.4405
3.0625 | 24535.549 | 26.651
3.0694 | 24696.4167 | 26.0207
3.0764 | 24854.1848 | 25.56
3.0833 | 25008.5551 | 25.2879
3.0903 | 25159.2363 | 25.2076
3.0972 | 25305.9442 | 25.3326
3.1042 | 25448.4024 | 25.665
3.1111 | 25586.3427 | 26.1681
3.1181 | 25719.5058 | 26.7706
3.125 | 25847.6418 | 27.4017
3.1319 | 25970.5105 | 28.0254
3.1389 | 26087.8818 | 28.6176
3.1458 | 26199.5364 | 29.1454
3.1528 | 26305.2661 | 29.5998
3.1597 | 26404.8742 | 30.0043
3.1667 | 26498.1758 | 30.3613
3.1736 | 26584.9982 | 30.6438
3.1806 | 26665.1813 | 30.8609
3.1875 | 26738.5778 | 31.0642
3.1944 | 26805.0535 | 31.3117
3.2014 | 26864.4877 | 31.6523
3.2083 | 26916.7732 | 32.072
3.2153 | 26961.8165 | 32.5283
3.2222 | 26999.5384 | 32.987
3.2292 | 27029.8735 | 33.4431
3.2361 | 27052.7709 | 33.8829
3.2431 | 27068.194 | 34.3027
3.25 | 27076.1205 | 34.6975
3.2569 | 27076.5427 | 35.0488
3.2639 | 27069.4673 | 35.3586
3.2708 | 27054.9156 | 35.633
3.2778 | 27032.9232 | 35.8696
3.2847 | 27003.5401 | 36.0761
3.2917 | 26966.8306 | 36.2829
3.2986 | 26922.873 | 36.5015
3.3056 | 26871.7596 | 36.7126
3.3125 | 26813.5969 | 36.8825
3.3194 | 26748.5044 | 36.9899
3.3264 | 26676.6154 | 37.0143
3.3333 | 26598.0762 | 36.9331
3.3403 | 26513.0459 | 36.747
3.3472 | 26421.6963 | 36.4801
3.3542 | 26324.2112 | 36.1765
3.3611 | 26220.7863 | 35.8912
3.3681 | 26111.629 | 35.6482
3.375 | 25996.9575 | 35.4601
3.3819 | 25877.0009 | 35.3329
3.3889 | 25751.9984 | 35.2706
3.3958 | 25622.199 | 35.2418
3.4028 | 25487.8611 | 35.2294
3.4097 | 25349.2519 | 35.2227
3.4167 | 25206.6467 | 35.2183
3.4236 | 25060.3287 | 35.2235
3.4306 | 24910.5886 | 35.2497
3.4375 | 24757.7233 | 35.2738
3.4444 | 24602.0361 | 35.284
3.4514 | 24443.8359 | 35.2913
3.4583 | 24283.4364 | 35.2951
3.4653 | 24121.1556 | 35.2862
3.4722 | 23957.3154 | 35.257
3.4792 | 23792.2407 | 35.1801
3.4861 | 23626.259 | 35.0378
3.4931 | 23459.6996 | 34.8133
3.5 | 23292.8932 | 34.5092
3.5069 | 23126.1709 | 34.1493
3.5139 | 22959.864 | 33.7783
3.5208 | 22794.3029 | 33.4056
3.5278 | 22629.8171 | 33.0115
3.5347 | 22466.7338 | 32.5819
3.5417 | 22305.378 | 32.1269
3.5486 | 22146.0713 | 31.7078
3.5556 | 21989.1318 | 31.3784
3.5625 | 21834.873 | 31.1669
3.5694 | 21683.6035 | 31.0733
3.5764 | 21535.6264 | 31.106
3.5833 | 21391.2386 | 31.26
3.5903 | 21250.7303 | 31.5353
3.5972 | 21114.3846 | 31.9275
3.6042 | 20982.4766 | 32.425
3.6111 | 20855.2731 | 32.9904
3.6181 | 20733.0322 | 33.5904
3.625 | 20616.0026 | 34.1722
3.6319 | 20504.4232 | 34.6827
3.6389 | 20398.5226 | 35.0704
3.6458 | 20298.5188 | 35.3028
3.6528 | 20204.6186 | 35.4069
3.6597 | 20117.0173 | 35.4299
3.6667 | 20035.8984 | 35.4213
3.6736 | 19961.4331 | 35.4284
3.6806 | 19893.7801 | 35.4863
3.6875 | 19833.0851 | 35.5888
3.6944 | 19779.4809 | 35.7022
3.7014 | 19733.0867 | 35.7804
3.7083 | 19694.008 | 35.798
3.7153 | 19662.3368 | 35.764
3.7222 | 19638.1507 | 35.6916
3.7292 | 19621.5135 | 35.6166
3.7361 | 19612.4745 | 35.6002
3.7431 | 19611.0687 | 35.6926
3.75 | 19617.3166 | 35.9493
3.7569 | 19631.2242 | 36.3926
3.7639 | 19652.7832 | 36.9859
3.7708 | 19681.9705 | 37.6675
3.7778 | 19718.7488 | 38.3906
3.7847 | 19763.0664 | 39.1209
3.7917 | 19814.8572 | 39.8217
3.7986 | 19874.0411 | 40.4794
3.8056 | 19940.5237 | 41.0843
3.8125 | 20014.1972 | 41.6045
3.8194 | 20094.9398 | 42.0574
3.8264 | 20182.6166 | 42.4669
3.8333 | 20277.0793 | 42.825
3.8403 | 20378.167 | 43.0921
3.8472 | 20485.7059 | 43.2256
3.8542 | 20599.5104 | 43.1736
3.8611 | 20719.3826 | 42.919
3.8681 | 20845.1134 | 42.4683
3.875 | 20976.4826 | 41.8487
3.8819 | 21113.2589 | 41.1121
3.8889 | 21255.2014 | 40.2894
3.8958 | 21402.0588 | 39.4359
3.9028 | 21553.5709 | 38.6077
3.9097 | 21709.4684 | 37.8511
3.9167 | 21869.4738 | 37.2019
3.9236 | 22033.3019 | 36.6814
3.9306 | 22200.6601 | 36.2957
3.9375 | 22371.2491 | 36.0476
3.9444 | 22544.7637 | 35.9048
3.9514 | 22720.8928 | 35.8396
3.9583 | 22899.3207 | 35.8155
3.9653 | 23079.727 | 35.809
3.9722 | 23261.7879 | 35.7985
3.9792 | 23445.1761 | 35.7923
3.9861 | 23629.5621 | 35.7973
3.9931 | 23814.6144 | 35.8026
4 | 24000 | 35.8185
4.0069 | 24185.3856 | 35.8545
4.0139 | 24370.4379 | 35.9019
4.0208 | 24554.8239 | 35.9409
4.0278 | 24738.2121 | 35.9837
4.0347 | 24920.273 | 36.0742
4.0417 | 25100.6793 | 36.2666
4.0486 | 25279.1072 | 36.5993
4.0556 | 25455.2363 | 37.0867
4.0625 | 25628.7509 | 37.7147
4.0694 | 25799.3399 | 38.4239
4.0764 | 25966.6981 | 39.1451
4.0833 | 26130.5262 | 39.8187
4.0903 | 26290.5316 | 40.3935
4.0972 | 26446.4291 | 40.8375
4.1042 | 26597.9412 | 41.1721
4.1111 | 26744.7986 | 41.4665
4.1181 | 26886.7411 | 41.7882
4.125 | 27023.5174 | 42.1877
4.1319 | 27154.8866 | 42.7056
4.1389 | 27280.6174 | 43.3601
4.1458 | 27400.4896 | 44.1319
4.1528 | 27514.2941 | 44.9716
4.1597 | 27621.833 | 45.8068
4.1667 | 27722.9207 | 46.5592
4.1736 | 27817.3834 | 47.1508
4.1806 | 27905.0602 | 47.4944
4.1875 | 27985.8028 | 47.5426
4.1944 | 28059.4763 | 47.3064
4.2014 | 28125.9589 | 46.8185
4.2083 | 28185.1428 | 46.1064
4.2153 | 28236.9336 | 45.2052
4.2222 | 28281.2512 | 44.1569
4.2292 | 28318.0295 | 43.0292
4.2361 | 28347.2168 | 41.8892
4.2431 | 28368.7758 | 40.7912
4.25 | 28382.6834 | 39.7748
4.2569 | 28388.9313 | 38.8513
4.2639 | 28387.5255 | 37.9874
4.2708 | 28378.4865 | 37.1319
4.2778 | 28361.8493 | 36.2568
4.2847 | 28337.6632 | 35.3745
4.2917 | 28305.992 | 34.5124
4.2986 | 28266.9133 | 33.7005
4.3056 | 28220.5191 | 32.9671
4.3125 | 28166.9149 | 32.335
4.3194 | 28106.2199 | 31.8078
4.3264 | 28038.5669 | 31.3472
4.3333 | 27964.1016 | 30.9021
4.3403 | 27882.9827 | 30.4303
4.3472 | 27795.3814 | 29.9443
4.3542 | 27701.4812 | 29.4921
4.3611 | 27601.4774 | 29.1126
4.3681 | 27495.5768 | 28.8506
4.375 | 27383.9974 | 28.7347
4.3819 | 27266.9678 | 28.7597
4.3889 | 27144.7269 | 28.8802
4.3958 | 27017.5234 | 29.034
4.4028 | 26885.6154 | 29.1701
4.4097 | 26749.2697 | 29.2761
4.4167 | 26608.7614 | 29.3623
4.4236 | 26464.3736 | 29.4632
4.4306 | 26316.3965 | 29.6161
4.4375 | 26165.127 | 29.8679
4.4444 | 26010.8682 | 30.2321
4.4514 | 25853.9287 | 30.6867
4.4583 | 25694.622 | 31.2229
4.4653 | 25533.2662 | 31.8487
4.4722 | 25370.1829 | 32.5849
4.4792 | 25205.6971 | 33.4278
4.4861 | 25040.136 | 34.3687
4.4931 | 24873.8291 | 35.4157
4.5 | 24707.1068 | 36.533
4.5069 | 24540.3004 | 37.6457
4.5139 | 24373.741 | 38.7016
4.5208 | 24207.7593 | 39.6642
4.5278 | 24042.6846 | 40.4834
4.5347 | 23878.8444 | 41.1138
4.5417 | 23716.5636 | 41.5488
4.5486 | 23556.1641 | 41.8198
4.5556 | 23397.9639 | 41.9372
4.5625 | 23242.2767 | 41.9212
4.5694 | 23089.4114 | 41.7753
4.5764 | 22939.6713 | 41.4742
4.5833 | 22793.3533 | 41.0228
4.5903 | 22650.7481 | 40.4188
4.5972 | 22512.1389 | 39.6672
4.6042 | 22377.801 | 38.8233
4.6111 | 22248.0016 | 37.9916
4.6181 | 22122.9991 | 37.2549
4.625 | 22003.0425 | 36.6357
4.6319 | 21888.371 | 36.1121
4.6389 | 21779.2137 | 35.6491
4.6458 | 21675.7888 | 35.217
4.6528 | 21578.3037 | 34.8046
4.6597 | 21486.9541 | 34.4186
4.6667 | 21401.9238 | 34.0976
4.6736 | 21323.3846 | 33.902
4.6806 | 21251.4956 | 33.8902
4.6875 | 21186.4031 | 34.0877
4.6944 | 21128.2404 | 34.473
4.7014 | 21077.127 | 35.0146
4.7083 | 21033.1694 | 35.6251
4.7153 | 20996.4599 | 36.1936
4.7222 | 20967.0768 | 36.6358
4.7292 | 20945.0844 | 36.91
4.7361 | 20930.5327 | 37.0158
4.7431 | 20923.4573 | 36.9835
4.75 | 20923.8795 | 36.8405
4.7569 | 20931.806 | 36.6059
4.7639 | 20947.2291 | 36.2929
4.7708 | 20970.1265 | 35.928
4.7778 | 21000.4616 | 35.5332
4.7847 | 21038.1835 | 35.1366
4.7917 | 21083.2268 | 34.7746
4.7986 | 21135.5123 | 34.4685
4.8056 | 21194.9465 | 34.2283
4.8125 | 21261.4222 | 34.0443
4.8194 | 21334.8187 | 33.9268
4.8264 | 21415.0018 | 33.8893
4.8333 | 21501.8242 | 33.8982
4.8403 | 21595.1258 | 33.9169
4.8472 | 21694.7339 | 33.9553
4.8542 | 21800.4636 | 34.0296
4.8611 | 21912.1182 | 34.1787
4.8681 | 22029.4895 | 34.4296
4.875 | 22152.3582 | 34.7801
4.8819 | 22280.4942 | 35.2087
4.8889 | 22413.6573 | 35.695
4.8958 | 22551.5976 | 36.2048
4.9028 | 22694.0558 | 36.6891
4.9097 | 22840.7637 | 37.1225
4.9167 | 22991.4449 | 37.511
4.9236 | 23145.8152 | 37.8454
4.9306 | 23303.5833 | 38.1003
4.9375 | 23464.451 | 38.2563
4.9444 | 23628.1141 | 38.2934
4.9514 | 23794.2629 | 38.1598
4.9583 | 23962.5827 | 37.8314
4.9653 | 24132.7545 | 37.3165
4.9722 | 24304.4555 | 36.6605
4.9792 | 24477.3598 | 35.932
4.9861 | 24651.1391 | 35.1928
4.9931 | 24825.463 | 34.4887
5 | 25000 | 33.836
5.0069 | 25174.4181 | 33.2502
5.0139 | 25348.385 | 32.7332
5.0208 | 25521.5694 | 32.2567
5.0278 | 25693.6409 | 31.7988
5.0347 | 25864.2714 | 31.3718
5.0417 | 26033.1351 | 30.9763
5.0486 | 26199.9093 | 30.6175
5.0556 | 26364.2753 | 30.327
5.0625 | 26525.9185 | 30.1563
5.0694 | 26684.5294 | 30.1365
5.0764 | 26839.8041 | 30.2839
5.0833 | 26991.4449 | 30.5862
5.0903 | 27139.1605 | 30.9988
5.0972 | 27282.6673 | 31.4804
5.1042 | 27421.6891 | 31.9919
5.1111 | 27555.9582 | 32.5074
5.1181 | 27685.2158 | 33.0095
5.125 | 27809.2124 | 33.4717
5.1319 | 27927.7082 | 33.8619
5.1389 | 28040.4738 | 34.1613
5.1458 | 28147.2903 | 34.361
5.1528 | 28247.9503 | 34.468
5.1597 | 28342.2574 | 34.4896
5.1667 | 28430.0274 | 34.4484
5.1736 | 28511.0885 | 34.4058
5.1806 | 28585.281 | 34.4107
5.1875 | 28652.4585 | 34.4676
5.1944 | 28712.4874 | 34.5467
5.2014 | 28765.2479 | 34.6194
5.2083 | 28810.6334 | 34.6657
5.2153 | 28848.5515 | 34.6641
5.2222 | 28878.9236 | 34.5958
5.2292 | 28901.6854 | 34.4515
5.2361 | 28916.7867 | 34.2687
5.2431 | 28924.1918 | 34.0866
5.25 | 28923.8795 | 33.9574
5.2569 | 28915.8431 | 33.91
5.2639 | 28900.0903 | 33.968
5.2708 | 28876.6433 | 34.1682
5.2778 | 28845.5388 | 34.5212
5.2847 | 28806.8279 | 35.03
5.2917 | 28760.576 | 35.7002
5.2986 | 28706.8627 | 36.5071
5.3056 | 28645.7813 | 37.3943
5.3125 | 28577.4394 | 38.2682
5.3194 | 28501.9579 | 39.0232
5.3264 | 28419.4713 | 39.5622
5.3333 | 28330.127 | 39.8255
5.3403 | 28234.0856 | 39.8325
5.3472 | 28131.52 | 39.6097
5.3542 | 28022.6155 | 39.2019
5.3611 | 27907.5692 | 38.6948
5.3681 | 27786.5897 | 38.1569
5.375 | 27659.8967 | 37.6431
5.3819 | 27527.7208 | 37.2056
5.3889 | 27390.3025 | 36.8665
5.3958 | 27247.8924 | 36.6213
5.4028 | 27100.7503 | 36.4466
5.4097 | 26949.145 | 36.3286
5.4167 | 26793.3533 | 36.2363
5.4236 | 26633.6602 | 36.147
5.4306 | 26470.3575 | 36.0513
5.4375 | 26303.7442 | 35.9302
5.4444 | 26134.125 | 35.7544
5.4514 | 25961.8105 | 35.4695
5.4583 | 25787.116 | 35.0362
5.4653 | 25610.3613 | 34.4849
5.4722 | 25431.8701 | 33.8815
5.4792 | 25251.9688 | 33.3034
5.4861 | 25070.9869 | 32.8113
5.4931 | 24889.2555 | 32.4727
5.5 | 24707.1068 | 32.3197
5.5069 | 24524.874 | 32.3695
5.5139 | 24342.8901 | 32.6048
5.5208 | 24161.4875 | 32.9767
5.5278 | 23980.9975 | 33.4146
5.5347 | 23801.7493 | 33.8449
5.5417 | 23624.0696 | 34.1767
5.5486 | 23448.2823 | 34.3458
5.5556 | 23274.707 | 34.3278
5.5625 | 23103.6596 | 34.1551
5.5694 | 22935.4504 | 33.9052
5.5764 | 22770.3847 | 33.6581
5.5833 | 22608.7614 | 33.4808
5.5903 | 22450.8728 | 33.4153
5.5972 | 22297.0039 | 33.483
5.6042 | 22147.432 | 33.7005
5.6111 | 22002.426 | 34.0495
5.6181 | 21862.2461 | 34.4952
5.625 | 21727.1431 | 34.9702
5.6319 | 21597.3581 | 35.3761
5.6389 | 21473.1218 | 35.6374
5.6458 | 21354.6545 | 35.7253
5.6528 | 21242.1651 | 35.6486
5.6597 | 21135.8511 | 35.4238
5.6667 | 21035.8984 | 35.094
5.6736 | 20942.4802 | 34.6888
5.6806 | 20855.7576 | 34.2184
5.6875 | 20775.8786 | 33.7162
5.6944 | 20702.9781 | 33.2202
5.7014 | 20637.1777 | 32.7464
5.7083 | 20578.5854 | 32.325
5.7153 | 20527.2952 | 31.9577
5.7222 | 20483.3872 | 31.629
5.7292 | 20446.9276 | 31.355
5.7361 | 20417.9679 | 31.138
5.7431 | 20396.5455 | 30.9793
5.75 | 20382.6834 | 30.8817
5.7569 | 20376.39 | 30.8544
5.7639 | 20377.6593 | 30.9059
5.7708 | 20386.4706 | 31.0346
5.7778 | 20402.7891 | 31.227
5.7847 | 20426.5655 | 31.459
5.7917 | 20457.7362 | 31.7288
5.7986 | 20496.2233 | 32.0594
5.8056 | 20541.9353 | 32.4611
5.8125 | 20594.7666 | 32.925
5.8194 | 20654.5979 | 33.4425
5.8264 | 20721.2967 | 34.0173
5.8333 | 20794.7174 | 34.6392
5.8403 | 20874.7015 | 35.2935
5.8472 | 20961.0777 | 35.938
5.8542 | 21053.6629 | 36.5318
5.8611 | 21152.2618 | 37.065
5.8681 | 21256.6679 | 37.5255
5.875 | 21366.6632 | 37.9152
5.8819 | 21482.0194 | 38.2535
5.8889 | 21602.4977 | 38.579
5.8958 | 21727.8498 | 38.9417
5.9028 | 21857.8176 | 39.3511
5.9097 | 21992.1348 | 39.7855
5.9167 | 22130.5262 | 40.203
5.9236 | 22272.7092 | 40.5528
5.9306 | 22418.3938 | 40.781
5.9375 | 22567.2834 | 40.8618
5.9444 | 22719.0752 | 40.7685
5.9514 | 22873.4608 | 40.4894
5.9583 | 23030.127 | 40.0312
5.9653 | 23188.756 | 39.4267
5.9722 | 23349.0267 | 38.7458
5.9792 | 23510.6143 | 38.049
5.9861 | 23673.1919 | 37.3516
5.9931 | 23836.4305 | 36.6365
6 | 24000 | 35.9078
6.0069 | 24163.5695 | 35.1701
6.0139 | 24326.8081 | 34.4446
6.0208 | 24489.3857 | 33.7647
6.0278 | 24650.9733 | 33.1478
6.0347 | 24811.244 | 32.5994
6.0417 | 24969.873 | 32.1399
6.0486 | 25126.5392 | 31.7812
6.0556 | 25280.9248 | 31.5233
6.0625 | 25432.7166 | 31.3744
6.0694 | 25581.6062 | 31.3297
6.0764 | 25727.2908 | 31.4019
6.0833 | 25869.4738 | 31.6071
6.0903 | 26007.8652 | 31.9416
6.0972 | 26142.1824 | 32.386
6.1042 | 26272.1502 | 32.9036
6.1111 | 26397.5023 | 33.457
6.1181 | 26517.9806 | 34.0076
6.125 | 26633.3368 | 34.5307
6.1319 | 26743.3321 | 34.9798
6.1389 | 26847.7382 | 35.3017
6.1458 | 26946.3371 | 35.4643
6.1528 | 27038.9223 | 35.4484
6.1597 | 27125.2985 | 35.2347
6.1667 | 27205.2826 | 34.8297
6.1736 | 27278.7033 | 34.2586
6.1806 | 27345.4021 | 33.544
6.1875 | 27405.2334 | 32.705
6.1944 | 27458.0647 | 31.7524
6.2014 | 27503.7767 | 30.7039
6.2083 | 27542.2638 | 29.6181
6.2153 | 27573.4345 | 28.5757
6.2222 | 27597.2109 | 27.6492
6.2292 | 27613.5294 | 26.8714
6.2361 | 27622.3407 | 26.2439
6.2431 | 27623.61 | 25.7811
6.25 | 27617.3166 | 25.489
6.2569 | 27603.4545 | 25.3808
6.2639 | 27582.0321 | 25.4849
6.2708 | 27553.0724 | 25.8453
6.2778 | 27516.6128 | 26.4893
6.2847 | 27472.7048 | 27.4141
6.2917 | 27421.4146 | 28.5939
6.2986 | 27362.8223 | 29.9827
6.3056 | 27297.0219 | 31.5099
6.3125 | 27224.1214 | 33.1113
6.3194 | 27144.2424 | 34.7325
6.3264 | 27057.5198 | 36.3431
6.3333 | 26964.1016 | 37.9362
6.3403 | 26864.1489 | 39.4803
6.3472 | 26757.8349 | 40.9152
6.3542 | 26645.3455 | 42.1749
6.3611 | 26526.8782 | 43.2118
6.3681 | 26402.6419 | 44.0026
6.375 | 26272.8569 | 44.5384
6.3819 | 26137.7539 | 44.817
6.3889 | 25997.574 | 44.8495
6.3958 | 25852.568 | 44.6745
6.4028 | 25702.9961 | 44.3259
6.4097 | 25549.1272 | 43.8417
6.4167 | 25391.2386 | 43.2504
6.4236 | 25229.6153 | 42.5753
6.4306 | 25064.5496 | 41.8489
6.4375 | 24896.3404 | 41.0849
6.4444 | 24725.293 | 40.3005
6.4514 | 24551.7177 | 39.5163
6.4583 | 24375.9304 | 38.7445
6.4653 | 24198.2507 | 37.973
6.4722 | 24019.0025 | 37.2081
6.4792 | 23838.5125 | 36.4767
6.4861 | 23657.1099 | 35.8072
6.4931 | 23475.126 | 35.2467
6.5 | 23292.8932 | 34.8116
6.5069 | 23110.7445 | 34.487
6.5139 | 22929.0131 | 34.2641
6.5208 | 22748.0312 | 34.1331
6.5278 | 22568.1299 | 34.076
6.5347 | 22389.6387 | 34.0943
6.5417 | 22212.884 | 34.1738
6.5486 | 22038.1895 | 34.3115
6.5556 | 21865.875 | 34.4873
6.5625 | 21696.2558 | 34.6609
6.5694 | 21529.6425 | 34.8128
6.5764 | 21366.3398 | 34.9498
6.5833 | 21206.6467 | 35.0684
6.5903 | 21050.855 | 35.1688
6.5972 | 20899.2497 | 35.2615
6.6042 | 20752.1076 | 35.3562
6.6111 | 20609.6975 | 35.438
6.6181 | 20472.2792 | 35.5141
6.625 | 20340.1033 | 35.6124
6.6319 | 20213.4103 | 35.7492
6.6389 | 20092.4308 | 35.9047
6.6458 | 19977.3845 | 36.0514
6.6528 | 19868.48 | 36.1405
6.6597 | 19765.9144 | 36.143
6.6667 | 19669.873 | 36.0507
6.6736 | 19580.5287 | 35.8303
6.6806 | 19498.0421 | 35.4703
6.6875 | 19422.5606 | 35.0108
6.6944 | 19354.2187 | 34.512
6.7014 | 19293.1373 | 34.021
6.7083 | 19239.424 | 33.6036
6.7153 | 19193.1721 | 33.2903
6.7222 | 19154.4612 | 33.0991
6.7292 | 19123.3567 | 33.063
6.7361 | 19099.9097 | 33.1869
6.7431 | 19084.1569 | 33.4547
6.75 | 19076.1205 | 33.8439
6.7569 | 19075.8082 | 34.337
6.7639 | 19083.2133 | 34.895
6.7708 | 19098.3146 | 35.4744
6.7778 | 19121.0764 | 36.0512
6.7847 | 19151.4485 | 36.6076
6.7917 | 19189.3666 | 37.1396
6.7986 | 19234.7521 | 37.6513
6.8056 | 19287.5126 | 38.1555
6.8125 | 19347.5415 | 38.6695
6.8194 | 19414.719 | 39.1794
6.8264 | 19488.9115 | 39.6788
6.8333 | 19569.9726 | 39.9785
6.8403 | 19657.7426 | 40.2106
6.8472 | 19752.0497 | 40.3906
6.8542 | 19852.7097 | 40.5257
6.8611 | 19959.5262 | 40.6173
6.8681 | 20072.2918 | 40.6645
6.875 | 20190.7876 | 40.6653
6.8819 | 20314.7842 | 40.6187
6.8889 | 20444.0418 | 40.5235
6.8958 | 20578.3109 | 40.3789
6.9028 | 20717.3327 | 40.1851
6.9097 | 20860.8395 | 39.9423
6.9167 | 21008.5551 | 39.6503
6.9236 | 21160.1959 | 39.3089
6.9306 | 21315.4706 | 38.9185
6.9375 | 21474.0815 | 38.4789
6.9444 | 21635.7247 | 37.9901
6.9514 | 21800.0907 | 37.4526
6.9583 | 21966.8649 | 36.8672
6.9653 | 22135.7286 | 36.2349
6.9722 | 22306.3591 | 35.5569
6.9792 | 22478.4306 | 34.8338
6.9861 | 22651.615 | 34.0662
6.9931 | 22825.5819 | 33.2546
7 | 23000 | 32.3996

## Primary
Unit overview
Name: | Primary
Sumo name: | Primary1
Category: | Separators
Unit: | Primary
Type: | Volumeless primary with specified primary sludge concentration
Settings
Process settings
Symbol | Name | Value | Unit | Comment
fXTSS,sludge | Solids percent removal | 60 | %
XTSS,sludge,target | Sludge solids concentration | 5000 | g/m3
Cost settings
Symbol | Name | Value | Unit | Comment
eTSS,polymer | Polymer dosage rate based on TSS load | 3 | g polymer/kg TSS

## Side flow divider
Unit overview
Name: | Side flow divider
Sumo name: | Sideflowdivider1
Category: | Flow elements
Unit: | Side flow divider
Type: | Side pump
Settings
Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 600 | m3/d
IncreaseSRT | Disabled
No interpolation
Time | Qpumped,target
d | m3/d
0 | 600
3.5 | 400
Decrease SRT | Disabled
No interpolation | Repeated every 168 hours
Time | Qpumped,target
d | m3/d
0 | 600
3.5 | 1000

## Side flow divider2
Unit overview
Name: | Side flow divider2
Sumo name: | Sideflowdivider1_1
Category: | Flow elements
Unit: | Side flow divider
Type: | Side pump
Settings
Pump parameters
Symbol | Name | Value | Unit | Comment
Qpumped,target | Pumped flow | 36000 | m3/d

## CSTR
Unit overview
Name: | CSTR
Sumo name: | CSTR1
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and input DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
Ntrain | Number of trains | 1
htank | Tank depth | 5 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 0 | g O2/m3 | List of Set SVs will appear here.
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XCASTO_0 | Carbon storing organisms (CASTO) initial concentration | 700 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 140 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XHAO,H_0 | Active hydrous aluminium oxide, high surface (HAO,H) initial concentration | 1e-40 | g Al/m3
XHAO,L_0 | Active hydrous aluminium oxide, low surface (HAO,L) initial concentration | 1e-40 | g Al/m3
XHAO,old_0 | Aged unused hydrous aluminium oxide (HAO,old) initial concentration | 1e-40 | g Al/m3
XHAO,H,P_0 | P-bound hydrous aluminium oxide, high surface (HAO,H,P) initial concentration | 1e-40 | g Al/m3
XHAO,L,P_0 | P-bound hydrous aluminium oxide, low surface (HAO,L,P) initial concentration | 1e-40 | g Al/m3
XHAO,H,P,old_0 | Aged P-bound hydrous aluminium oxide, high surface (HAO,H,P,old) initial concentration | 1e-40 | g Al/m3
XHAO,L,P,old_0 | Aged P-bound hydrous aluminium oxide, low surface (HAO,L,P,old) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XBSH_0 | Brushite (BSH) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
SALPHA_0 | Alpha indicator initial concentration | 0.5
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration under aerated conditions | 1.54 | %v/v
GCH4,aer | Methane gas (CH4) off-gas concentration under aerated conditions | 1e-40 | %v/v
GH2,aer | Hydrogen gas (H2) off-gas concentration under aerated conditions | 1e-40 | %v/v
GO2,aer | Oxygen gas (O2) off-gas concentration under aerated conditions | 18.84 | %v/v
GNH3,aer | Ammonia gas (NH3) off-gas concentration under aerated conditions | 1e-40 | %v/v
GN2,aer | Nitrogen gas (N2) off-gas concentration under aerated conditions | 79.62 | %v/v
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 2.3 | %v/v
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 0.04 | %v/v
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 3.16 | %v/v
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 94.5 | %v/v
Aeration gas composition
Symbol | Name | Value | Unit | Comment
GCO2,air,inp | Carbon dioxide gas (CO2) in air input | 0.04 | %v/v
GCH4,air,inp | Methane gas (CH4) in air input | 1e-40 | %v/v
GH2,air,inp | Hydrogen gas (H2) in air input | 1e-40 | %v/v
GO2,air,inp | Oxygen gas (O2) in air input | 20.95 | %v/v
GNH3,air,inp | Ammonia gas (NH3) in air input | 1e-40 | %v/v
GN2,air,inp | Nitrogen gas (N2) in air input | 79.01 | %v/v
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble,aer | Bubble Sauter mean diameter under aerated conditions | 0.003 | m
dbubble,nonaer | Bubble Sauter mean diameter under non-aerated conditions | 0.01 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the graphics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.

## CSTR2
Unit overview
Name: | CSTR2
Sumo name: | CSTR2
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and input DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
Ntrain | Number of trains | 1
htank | Tank depth | 5 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 3 | g O2/m3 | List of Set SVs will appear here.
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XCASTO_0 | Carbon storing organisms (CASTO) initial concentration | 700 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 140 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XHAO,H_0 | Active hydrous aluminium oxide, high surface (HAO,H) initial concentration | 1e-40 | g Al/m3
XHAO,L_0 | Active hydrous aluminium oxide, low surface (HAO,L) initial concentration | 1e-40 | g Al/m3
XHAO,old_0 | Aged unused hydrous aluminium oxide (HAO,old) initial concentration | 1e-40 | g Al/m3
XHAO,H,P_0 | P-bound hydrous aluminium oxide, high surface (HAO,H,P) initial concentration | 1e-40 | g Al/m3
XHAO,L,P_0 | P-bound hydrous aluminium oxide, low surface (HAO,L,P) initial concentration | 1e-40 | g Al/m3
XHAO,H,P,old_0 | Aged P-bound hydrous aluminium oxide, high surface (HAO,H,P,old) initial concentration | 1e-40 | g Al/m3
XHAO,L,P,old_0 | Aged P-bound hydrous aluminium oxide, low surface (HAO,L,P,old) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XBSH_0 | Brushite (BSH) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
SALPHA_0 | Alpha indicator initial concentration | 0.5
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration under aerated conditions | 1.54 | %v/v
GCH4,aer | Methane gas (CH4) off-gas concentration under aerated conditions | 1e-40 | %v/v
GH2,aer | Hydrogen gas (H2) off-gas concentration under aerated conditions | 1e-40 | %v/v
GO2,aer | Oxygen gas (O2) off-gas concentration under aerated conditions | 18.84 | %v/v
GNH3,aer | Ammonia gas (NH3) off-gas concentration under aerated conditions | 1e-40 | %v/v
GN2,aer | Nitrogen gas (N2) off-gas concentration under aerated conditions | 79.62 | %v/v
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 2.3 | %v/v
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 0.04 | %v/v
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 3.16 | %v/v
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 94.5 | %v/v
Aeration gas composition
Symbol | Name | Value | Unit | Comment
GCO2,air,inp | Carbon dioxide gas (CO2) in air input | 0.04 | %v/v
GCH4,air,inp | Methane gas (CH4) in air input | 1e-40 | %v/v
GH2,air,inp | Hydrogen gas (H2) in air input | 1e-40 | %v/v
GO2,air,inp | Oxygen gas (O2) in air input | 20.95 | %v/v
GNH3,air,inp | Ammonia gas (NH3) in air input | 1e-40 | %v/v
GN2,air,inp | Nitrogen gas (N2) in air input | 79.01 | %v/v
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble,aer | Bubble Sauter mean diameter under aerated conditions | 0.003 | m
dbubble,nonaer | Bubble Sauter mean diameter under non-aerated conditions | 0.01 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the graphics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.
Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.6 | g O2/m3
Table1 | Enabled
No interpolation | Repeated every 168 hours
Time | SO2
d | g O2/m3
0 | 2
0.0069444 | 0.5
0.013889 | 0.5
0.020833 | 0.5
0.027778 | 0.5
0.034722 | 0.5
0.041667 | 0.5
0.048611 | 0.5
0.055556 | 0.64037
0.0625 | 1.3016
0.069444 | 1.5848
0.076389 | 1.7194
0.083333 | 1.4001
0.090278 | 1.0763
0.097222 | 1.1126
0.10417 | 1.2801
0.11111 | 0.7673
0.11806 | 0.5
0.125 | 0.5
0.13194 | 0.98167
0.13889 | 2.0382
0.14583 | 2.9797
0.15278 | 3
0.15972 | 3
0.16667 | 3
0.17361 | 2.0903
0.18056 | 0.5
0.1875 | 0.5
0.19444 | 0.5
0.20139 | 0.5
0.20833 | 1.3723
0.21528 | 2.2029
0.22222 | 2.5724
0.22917 | 2.8011
0.23611 | 2.8086
0.24306 | 2.3535
0.25 | 1.7106
0.25694 | 1.6012
0.26389 | 2.4223
0.27083 | 3
0.27778 | 3
0.28472 | 3
0.29167 | 2.3633
0.29861 | 0.80073
0.30556 | 1.0144
0.3125 | 1.6084
0.31944 | 1.591
0.32639 | 0.83807
0.33333 | 0.5
0.34028 | 0.5
0.34722 | 0.5
0.35417 | 0.5
0.36111 | 0.5
0.36806 | 0.5
0.375 | 0.5
0.38194 | 0.5
0.38889 | 0.5
0.39583 | 0.70736
0.40278 | 0.99094
0.40972 | 0.87737
0.41667 | 1.1439
0.42361 | 1.0177
0.43056 | 0.5
0.4375 | 0.5
0.44444 | 0.5
0.45139 | 0.61556
0.45833 | 1.9256
0.46528 | 3
0.47222 | 3
0.47917 | 3
0.48611 | 2.0514
0.49306 | 1.0226
0.5 | 0.5
0.50694 | 0.5
0.51389 | 1.0485
0.52083 | 1.5924
0.52778 | 1.6114
0.53472 | 2.493
0.54167 | 3
0.54861 | 3
0.55556 | 3
0.5625 | 3
0.56944 | 2.2239
0.57639 | 1.4233
0.58333 | 1.3367
0.59028 | 2.1655
0.59722 | 3
0.60417 | 3
0.61111 | 2.9472
0.61806 | 2.3117
0.625 | 1.919
0.63194 | 1.9152
0.63889 | 1.9711
0.64583 | 1.5279
0.65278 | 1.3876
0.65972 | 1.6052
0.66667 | 1.5516
0.67361 | 1.3072
0.68056 | 0.67418
0.6875 | 0.5
0.69444 | 0.90652
0.70139 | 2.0725
0.70833 | 3
0.71528 | 3
0.72222 | 2.5162
0.72917 | 1.7403
0.73611 | 2.1377
0.74306 | 3
0.75 | 3
0.75694 | 2.6839
0.76389 | 1.8434
0.77083 | 1.3208
0.77778 | 1.1188
0.78472 | 1.652
0.79167 | 2.2633
0.79861 | 2.7662
0.80556 | 3
0.8125 | 3
0.81944 | 2.3924
0.82639 | 0.5
0.83333 | 0.5
0.84028 | 0.5
0.84722 | 0.5
0.85417 | 0.5
0.86111 | 1.8689
0.86806 | 3
0.875 | 2.9208
0.88194 | 1.3033
0.88889 | 0.55139
0.89583 | 1.2033
0.90278 | 1.9357
0.90972 | 2.4693
0.91667 | 2.2864
0.92361 | 1.2567
0.93056 | 0.66051
0.9375 | 1.1759
0.94444 | 2.3087
0.95139 | 3
0.95833 | 3
0.96528 | 3
0.97222 | 1.4217
0.97917 | 0.5
0.98611 | 0.5
0.99306 | 0.5
1 | 0.5
1.0069 | 0.5
1.0139 | 0.5
1.0208 | 0.60978
1.0278 | 0.5
1.0347 | 0.5
1.0417 | 0.5
1.0486 | 0.86484
1.0556 | 1.4488
1.0625 | 1.2931
1.0694 | 0.5
1.0764 | 0.5
1.0833 | 1.7622
1.0903 | 3
1.0972 | 3
1.1042 | 3
1.1111 | 2.5154
1.1181 | 2.096
1.125 | 1.989
1.1319 | 1.3283
1.1389 | 0.5
1.1458 | 0.5
1.1528 | 0.5
1.1597 | 0.5
1.1667 | 1.2944
1.1736 | 2.4222
1.1806 | 2.839
1.1875 | 2.5865
1.1944 | 2.4129
1.2014 | 2.4848
1.2083 | 2.5011
1.2153 | 2.3551
1.2222 | 1.5442
1.2292 | 0.5
1.2361 | 0.5
1.2431 | 0.5
1.25 | 0.70681
1.2569 | 1.0023
1.2639 | 0.5
1.2708 | 0.5
1.2778 | 0.5
1.2847 | 0.50152
1.2917 | 1.4482
1.2986 | 2.544
1.3056 | 2.4335
1.3125 | 1.6924
1.3194 | 0.93592
1.3264 | 0.71334
1.3333 | 2.0245
1.3403 | 3
1.3472 | 3
1.3542 | 2.5889
1.3611 | 0.67837
1.3681 | 0.5
1.375 | 1.9106
1.3819 | 3
1.3889 | 3
1.3958 | 3
1.4028 | 3
1.4097 | 2.5296
1.4167 | 1.8157
1.4236 | 1.3343
1.4306 | 2.1025
1.4375 | 3
1.4444 | 3
1.4514 | 3
1.4583 | 3
1.4653 | 1.8275
1.4722 | 0.5
1.4792 | 0.5
1.4861 | 0.5
1.4931 | 0.5
1.5 | 1.5822
1.5069 | 2.2391
1.5139 | 1.7123
1.5208 | 0.5
1.5278 | 0.5
1.5347 | 0.5
1.5417 | 0.5
1.5486 | 1.5036
1.5556 | 2.6148
1.5625 | 3
1.5694 | 3
1.5764 | 3
1.5833 | 3
1.5903 | 3
1.5972 | 3
1.6042 | 2.3444
1.6111 | 1.8768
1.6181 | 1.7106
1.625 | 0.92885
1.6319 | 0.5
1.6389 | 0.5
1.6458 | 0.80305
1.6528 | 1.3846
1.6597 | 2.5879
1.6667 | 2.9436
1.6736 | 2.3231
1.6806 | 2.1938
1.6875 | 2.1833
1.6944 | 1.3243
1.7014 | 0.55955
1.7083 | 0.9111
1.7153 | 1.1916
1.7222 | 1.5826
1.7292 | 2.37
1.7361 | 2.4567
1.7431 | 2.3247
1.75 | 2.9224
1.7569 | 3
1.7639 | 3
1.7708 | 3
1.7778 | 2.6689
1.7847 | 1.6786
1.7917 | 1.5431
1.7986 | 2.233
1.8056 | 3
1.8125 | 3
1.8194 | 3
1.8264 | 3
1.8333 | 3
1.8403 | 2.4488
1.8472 | 1.6656
1.8542 | 1.083
1.8611 | 0.73658
1.8681 | 0.5
1.875 | 0.5
1.8819 | 0.6573
1.8889 | 1.8266
1.8958 | 3
1.9028 | 3
1.9097 | 2.3102
1.9167 | 0.99996
1.9236 | 0.5
1.9306 | 1.3525
1.9375 | 3
1.9444 | 3
1.9514 | 3
1.9583 | 2.5716
1.9653 | 1.21
1.9722 | 0.98287
1.9792 | 1.8364
1.9861 | 3
1.9931 | 3
2 | 3
2.0069 | 3
2.0139 | 3
2.0208 | 2.9197
2.0278 | 2.2401
2.0347 | 1.0359
2.0417 | 0.5
2.0486 | 0.5
2.0556 | 0.5
2.0625 | 0.5
2.0694 | 1.2771
2.0764 | 2.7043
2.0833 | 3
2.0903 | 3
2.0972 | 3
2.1042 | 1.9438
2.1111 | 0.5
2.1181 | 0.5
2.125 | 0.5
2.1319 | 0.5
2.1389 | 1.019
2.1458 | 2.6957
2.1528 | 3
2.1597 | 2.6729
2.1667 | 0.84422
2.1736 | 0.5
2.1806 | 0.5
2.1875 | 0.5
2.1944 | 0.84416
2.2014 | 1.1468
2.2083 | 1.24
2.2153 | 1.6376
2.2222 | 1.8831
2.2292 | 1.0287
2.2361 | 0.5
2.2431 | 0.5
2.25 | 0.5
2.2569 | 0.5
2.2639 | 1.0268
2.2708 | 1.3599
2.2778 | 1.5316
2.2847 | 1.7578
2.2917 | 1.1628
2.2986 | 0.87294
2.3056 | 1.3771
2.3125 | 1.2016
2.3194 | 0.5
2.3264 | 0.66446
2.3333 | 1.4263
2.3403 | 2.2638
2.3472 | 3
2.3542 | 3
2.3611 | 3
2.3681 | 3
2.375 | 3
2.3819 | 3
2.3889 | 1.9124
2.3958 | 1.9201
2.4028 | 2.5215
2.4097 | 2.6137
2.4167 | 2.2617
2.4236 | 2.0485
2.4306 | 1.7027
2.4375 | 1.3305
2.4444 | 1.1306
2.4514 | 0.61415
2.4583 | 0.67189
2.4653 | 1.5076
2.4722 | 2.5256
2.4792 | 3
2.4861 | 3
2.4931 | 2.6494
2.5 | 1.8224
2.5069 | 1.4113
2.5139 | 1.853
2.5208 | 3
2.5278 | 3
2.5347 | 3
2.5417 | 3
2.5486 | 2.8545
2.5556 | 1.1915
2.5625 | 0.5
2.5694 | 0.5
2.5764 | 0.5
2.5833 | 0.5
2.5903 | 0.5
2.5972 | 0.5
2.6042 | 1.6767
2.6111 | 2.6134
2.6181 | 3
2.625 | 2.1799
2.6319 | 1.2105
2.6389 | 1.5513
2.6458 | 2.1735
2.6528 | 2.0209
2.6597 | 1.0953
2.6667 | 0.5
2.6736 | 0.5
2.6806 | 0.62088
2.6875 | 0.65646
2.6944 | 0.5
2.7014 | 0.5
2.7083 | 0.56241
2.7153 | 0.5
2.7222 | 0.5
2.7292 | 0.52097
2.7361 | 1.0245
2.7431 | 2.1469
2.75 | 2.8568
2.7569 | 2.4459
2.7639 | 2.768
2.7708 | 3
2.7778 | 3
2.7847 | 2.5079
2.7917 | 1.9523
2.7986 | 1.8073
2.8056 | 2.1749
2.8125 | 2.1366
2.8194 | 0.90618
2.8264 | 0.5
2.8333 | 0.5
2.8403 | 0.5
2.8472 | 0.5
2.8542 | 2.0259
2.8611 | 3
2.8681 | 3
2.875 | 3
2.8819 | 2.5914
2.8889 | 2.6923
2.8958 | 3
2.9028 | 2.8641
2.9097 | 1.4276
2.9167 | 0.5
2.9236 | 0.5
2.9306 | 0.5
2.9375 | 0.5
2.9444 | 0.5
2.9514 | 0.5
2.9583 | 0.5
2.9653 | 0.76557
2.9722 | 1.9683
2.9792 | 2.3911
2.9861 | 1.7346
2.9931 | 1.3384
3 | 1.4112
3.0069 | 1.9958
3.0139 | 2.6417
3.0208 | 2.583
3.0278 | 2.0571
3.0347 | 1.3658
3.0417 | 0.77028
3.0486 | 0.5
3.0556 | 0.5
3.0625 | 0.5
3.0694 | 0.5
3.0764 | 1.0394
3.0833 | 3
3.0903 | 3
3.0972 | 3
3.1042 | 2.8525
3.1111 | 0.5
3.1181 | 0.5
3.125 | 0.5
3.1319 | 2.1186
3.1389 | 3
3.1458 | 3
3.1528 | 3
3.1597 | 3
3.1667 | 3
3.1736 | 1.2278
3.1806 | 0.5
3.1875 | 0.5
3.1944 | 0.5
3.2014 | 0.5
3.2083 | 0.52774
3.2153 | 1.0078
3.2222 | 1.6422
3.2292 | 2.4819
3.2361 | 2.4064
3.2431 | 1.6608
3.25 | 1.5964
3.2569 | 1.6219
3.2639 | 1.5976
3.2708 | 1.9513
3.2778 | 2.0979
3.2847 | 1.5637
3.2917 | 1.8202
3.2986 | 2.4597
3.3056 | 2.0164
3.3125 | 1.2777
3.3194 | 1.0095
3.3264 | 0.83495
3.3333 | 1.2629
3.3403 | 2.514
3.3472 | 3
3.3542 | 3
3.3611 | 2.0809
3.3681 | 0.73202
3.375 | 0.5
3.3819 | 0.5
3.3889 | 0.5
3.3958 | 1.1657
3.4028 | 2.4561
3.4097 | 2.1329
3.4167 | 1.3234
3.4236 | 1.0926
3.4306 | 1.724
3.4375 | 3
3.4444 | 3
3.4514 | 3
3.4583 | 3
3.4653 | 0.65803
3.4722 | 0.5
3.4792 | 0.5
3.4861 | 0.5
3.4931 | 0.5
3.5 | 1.0946
3.5069 | 1.7431
3.5139 | 1.9785
3.5208 | 1.5988
3.5278 | 1.2642
3.5347 | 0.98328
3.5417 | 0.5
3.5486 | 0.5
3.5556 | 0.5
3.5625 | 0.5
3.5694 | 0.77658
3.5764 | 1.1651
3.5833 | 0.97605
3.5903 | 1.3148
3.5972 | 2.3622
3.6042 | 3
3.6111 | 3
3.6181 | 3
3.625 | 3
3.6319 | 3
3.6389 | 1.6838
3.6458 | 0.5
3.6528 | 0.5
3.6597 | 0.5
3.6667 | 0.5
3.6736 | 1.3338
3.6806 | 2.385
3.6875 | 3
3.6944 | 3
3.7014 | 3
3.7083 | 3
3.7153 | 3
3.7222 | 1.9227
3.7292 | 0.5
3.7361 | 0.5
3.7431 | 0.5
3.75 | 1.1179
3.7569 | 2.2468
3.7639 | 1.6477
3.7708 | 0.5
3.7778 | 0.5
3.7847 | 0.5
3.7917 | 0.80459
3.7986 | 2.0627
3.8056 | 2.0537
3.8125 | 1.3767
3.8194 | 1.3374
3.8264 | 1.5373
3.8333 | 1.4969
3.8403 | 0.92101
3.8472 | 0.5
3.8542 | 0.5
3.8611 | 1.5092
3.8681 | 2.259
3.875 | 1.2771
3.8819 | 0.5
3.8889 | 0.5
3.8958 | 0.5
3.9028 | 0.77873
3.9097 | 1.6169
3.9167 | 1.6031
3.9236 | 2.4132
3.9306 | 3
3.9375 | 2.6879
3.9444 | 1.3546
3.9514 | 1.093
3.9583 | 1.5335
3.9653 | 2.7957
3.9722 | 3
3.9792 | 3
3.9861 | 2.6566
3.9931 | 1.695
4 | 1.3471
4.0069 | 1.4056
4.0139 | 1.8655
4.0208 | 2.1896
4.0278 | 1.9573
4.0347 | 1.6158
4.0417 | 1.567
4.0486 | 1.7299
4.0556 | 2.3863
4.0625 | 2.4067
4.0694 | 1.8353
4.0764 | 1.319
4.0833 | 0.84091
4.0903 | 1.1847
4.0972 | 2.2732
4.1042 | 2.6552
4.1111 | 1.7862
4.1181 | 0.5
4.125 | 0.5
4.1319 | 0.5
4.1389 | 0.5
4.1458 | 0.5
4.1528 | 0.5
4.1597 | 0.5
4.1667 | 0.98578
4.1736 | 0.98841
4.1806 | 0.5
4.1875 | 0.5
4.1944 | 0.64228
4.2014 | 2.217
4.2083 | 2.9847
4.2153 | 2.699
4.2222 | 1.9797
4.2292 | 2.239
4.2361 | 3
4.2431 | 3
4.25 | 2.7086
4.2569 | 2.2055
4.2639 | 1.3942
4.2708 | 0.515
4.2778 | 0.5
4.2847 | 0.5
4.2917 | 0.5
4.2986 | 0.5
4.3056 | 0.5
4.3125 | 0.67298
4.3194 | 1.4625
4.3264 | 1.7197
4.3333 | 1.6242
4.3403 | 1.9634
4.3472 | 2.3609
4.3542 | 2.5381
4.3611 | 2.4909
4.3681 | 2.2719
4.375 | 2.3133
4.3819 | 2.902
4.3889 | 3
4.3958 | 3
4.4028 | 2.1306
4.4097 | 1.1881
4.4167 | 0.80516
4.4236 | 0.5
4.4306 | 0.5
4.4375 | 0.5
4.4444 | 0.5
4.4514 | 1.3541
4.4583 | 1.9841
4.4653 | 1.6589
4.4722 | 0.5
4.4792 | 0.5
4.4861 | 0.5
4.4931 | 0.5
4.5 | 0.5
4.5069 | 0.5
4.5139 | 0.5
4.5208 | 0.5
4.5278 | 0.81442
4.5347 | 1.6981
4.5417 | 1.6873
4.5486 | 1.0373
4.5556 | 0.64737
4.5625 | 0.5
4.5694 | 0.5
4.5764 | 1.2499
4.5833 | 1.4797
4.5903 | 1.1282
4.5972 | 0.66723
4.6042 | 0.77742
4.6111 | 1.1477
4.6181 | 1.8952
4.625 | 2.2194
4.6319 | 1.7147
4.6389 | 1.302
4.6458 | 1.3696
4.6528 | 1.6927
4.6597 | 1.9333
4.6667 | 2.7427
4.6736 | 3
4.6806 | 3
4.6875 | 2.5004
4.6944 | 1.4341
4.7014 | 1.3937
4.7083 | 2.248
4.7153 | 3
4.7222 | 3
4.7292 | 3
4.7361 | 2.7081
4.7431 | 2.7056
4.75 | 3
4.7569 | 3
4.7639 | 3
4.7708 | 2.7947
4.7778 | 1.4972
4.7847 | 0.87871
4.7917 | 1.6648
4.7986 | 2.1796
4.8056 | 1.7948
4.8125 | 0.63894
4.8194 | 0.5
4.8264 | 0.5
4.8333 | 0.80334
4.8403 | 1.9904
4.8472 | 1.5757
4.8542 | 0.5
4.8611 | 0.5
4.8681 | 0.5
4.875 | 0.5
4.8819 | 0.90689
4.8889 | 1.5595
4.8958 | 1.7952
4.9028 | 1.9985
4.9097 | 2.0349
4.9167 | 1.4525
4.9236 | 0.69041
4.9306 | 0.5
4.9375 | 0.5313
4.9444 | 1.2203
4.9514 | 2.262
4.9583 | 3
4.9653 | 3
4.9722 | 2.9768
4.9792 | 1.7488
4.9861 | 0.90818
4.9931 | 0.88463
5 | 1.5814
5.0069 | 2.7556
5.0139 | 3
5.0208 | 3
5.0278 | 2.812
5.0347 | 1.8646
5.0417 | 1.3206
5.0486 | 1.8333
5.0556 | 2.1573
5.0625 | 2.1516
5.0694 | 2.4076
5.0764 | 1.8618
5.0833 | 1.0909
5.0903 | 1.5458
5.0972 | 2.5046
5.1042 | 3
5.1111 | 3
5.1181 | 3
5.125 | 2.8568
5.1319 | 1.5554
5.1389 | 0.68229
5.1458 | 0.8079
5.1528 | 0.77065
5.1597 | 1.0083
5.1667 | 2.267
5.1736 | 2.8021
5.1806 | 2.3291
5.1875 | 2.5077
5.1944 | 1.8512
5.2014 | 0.75772
5.2083 | 1.2943
5.2153 | 2.2795
5.2222 | 2.886
5.2292 | 3
5.2361 | 3
5.2431 | 3
5.25 | 2.4342
5.2569 | 1.7956
5.2639 | 1.094
5.2708 | 1.3121
5.2778 | 1.6003
5.2847 | 1.2823
5.2917 | 0.5
5.2986 | 0.5
5.3056 | 0.5
5.3125 | 0.5
5.3194 | 1.0139
5.3264 | 2.5576
5.3333 | 3
5.3403 | 3
5.3472 | 3
5.3542 | 3
5.3611 | 3
5.3681 | 2.2915
5.375 | 0.92955
5.3819 | 0.5
5.3889 | 0.5
5.3958 | 0.5
5.4028 | 0.5
5.4097 | 0.5
5.4167 | 1.4253
5.4236 | 2.7186
5.4306 | 3
5.4375 | 3
5.4444 | 3
5.4514 | 3
5.4583 | 2.4083
5.4653 | 2.2504
5.4722 | 2.2717
5.4792 | 1.481
5.4861 | 1.043
5.4931 | 0.97749
5.5 | 0.77115
5.5069 | 1.1841
5.5139 | 1.7018
5.5208 | 1.5668
5.5278 | 1.2943
5.5347 | 1.9207
5.5417 | 2.8359
5.5486 | 3
5.5556 | 2.9399
5.5625 | 2.591
5.5694 | 2.3525
5.5764 | 2.7767
5.5833 | 3
5.5903 | 2.9132
5.5972 | 2.5252
5.6042 | 1.9277
5.6111 | 0.51182
5.6181 | 0.5
5.625 | 0.5
5.6319 | 0.53963
5.6389 | 2.0888
5.6458 | 2.7876
5.6528 | 1.6356
5.6597 | 0.5
5.6667 | 0.5
5.6736 | 0.5
5.6806 | 1.7454
5.6875 | 2.6704
5.6944 | 2.7147
5.7014 | 1.806
5.7083 | 0.80892
5.7153 | 0.55067
5.7222 | 0.5
5.7292 | 0.5
5.7361 | 0.5
5.7431 | 0.5
5.75 | 1.3894
5.7569 | 2.72
5.7639 | 2.7798
5.7708 | 1.1951
5.7778 | 0.5
5.7847 | 0.5
5.7917 | 0.74021
5.7986 | 1.4021
5.8056 | 1.6631
5.8125 | 1.0724
5.8194 | 0.5
5.8264 | 0.5
5.8333 | 0.5
5.8403 | 0.5
5.8472 | 1.2036
5.8542 | 2.6456
5.8611 | 3
5.8681 | 2.5393
5.875 | 1.0062
5.8819 | 0.5
5.8889 | 0.5
5.8958 | 1.7381
5.9028 | 2.8619
5.9097 | 2.588
5.9167 | 1.5676
5.9236 | 1.2946
5.9306 | 2.3883
5.9375 | 3
5.9444 | 3
5.9514 | 3
5.9583 | 1.7709
5.9653 | 1.0256
5.9722 | 1.1083
5.9792 | 1.5418
5.9861 | 2.0117
5.9931 | 2.6091
6 | 3
6.0069 | 3
6.0139 | 3
6.0208 | 2.9369
6.0278 | 2.0322
6.0347 | 0.88377
6.0417 | 0.5
6.0486 | 0.5
6.0556 | 0.5
6.0625 | 0.5
6.0694 | 0.5
6.0764 | 0.5
6.0833 | 0.5
6.0903 | 0.5
6.0972 | 0.998
6.1042 | 1.5118
6.1111 | 1.4012
6.1181 | 0.92835
6.125 | 1.1136
6.1319 | 2.1772
6.1389 | 2.4768
6.1458 | 1.609
6.1528 | 0.91195
6.1597 | 0.5
6.1667 | 0.5
6.1736 | 0.5
6.1806 | 0.5
6.1875 | 0.5
6.1944 | 1.0372
6.2014 | 2.1592
6.2083 | 2.7329
6.2153 | 3
6.2222 | 3
6.2292 | 2.912
6.2361 | 2.445
6.2431 | 1.9215
6.25 | 1.0976
6.2569 | 1.2086
6.2639 | 1.8525
6.2708 | 2.3883
6.2778 | 2.7096
6.2847 | 2.7245
6.2917 | 1.7833
6.2986 | 0.64447
6.3056 | 0.5
6.3125 | 0.5
6.3194 | 0.5
6.3264 | 1.1518
6.3333 | 2.9496
6.3403 | 3
6.3472 | 3
6.3542 | 3
6.3611 | 3
6.3681 | 2.7684
6.375 | 2.1608
6.3819 | 0.78454
6.3889 | 0.5
6.3958 | 0.5
6.4028 | 0.5
6.4097 | 0.92639
6.4167 | 2.1256
6.4236 | 2.8768
6.4306 | 2.8099
6.4375 | 2.0611
6.4444 | 0.8208
6.4514 | 0.5
6.4583 | 0.5
6.4653 | 0.5
6.4722 | 0.5
6.4792 | 0.5
6.4861 | 1.2338
6.4931 | 1.909
6.5 | 2.2921
6.5069 | 2.2572
6.5139 | 1.7814
6.5208 | 0.9153
6.5278 | 0.5
6.5347 | 0.5
6.5417 | 0.5
6.5486 | 1.262
6.5556 | 2.1096
6.5625 | 1.2805
6.5694 | 0.5
6.5764 | 0.5
6.5833 | 0.5
6.5903 | 0.5
6.5972 | 0.5
6.6042 | 0.5
6.6111 | 0.5
6.6181 | 0.5
6.625 | 0.5
6.6319 | 0.5
6.6389 | 0.5
6.6458 | 0.69717
6.6528 | 1.7745
6.6597 | 2.756
6.6667 | 3
6.6736 | 3
6.6806 | 3
6.6875 | 1.9372
6.6944 | 0.5
6.7014 | 0.5
6.7083 | 0.5
6.7153 | 1.3487
6.7222 | 2.6682
6.7292 | 3
6.7361 | 3
6.7431 | 3
6.75 | 3
6.7569 | 2.1161
6.7639 | 0.83514
6.7708 | 0.5
6.7778 | 0.5
6.7847 | 0.5
6.7917 | 0.6071
6.7986 | 0.5
6.8056 | 0.5
6.8125 | 0.5
6.8194 | 0.5
6.8264 | 1.0908
6.8333 | 1.2953
6.8403 | 0.5
6.8472 | 0.66835
6.8542 | 2.05
6.8611 | 3
6.8681 | 3
6.875 | 3
6.8819 | 2.0023
6.8889 | 0.78112
6.8958 | 1.2884
6.9028 | 2.2737
6.9097 | 2.6623
6.9167 | 2.5209
6.9236 | 1.959
6.9306 | 1.3868
6.9375 | 1.8588
6.9444 | 2.8384
6.9514 | 3
6.9583 | 3
6.9653 | 3
6.9722 | 1.4684
6.9792 | 0.5
6.9861 | 0.5
6.9931 | 0.5
7 | 0.5
DOsmallrange | Disabled
No interpolation
Time | SO2
d | g O2/m3
0 | 1.4351
0.0069444 | 1.6181
0.013889 | 1.4242
0.020833 | 1.389
0.027778 | 1.4154
0.034722 | 1.4427
0.041667 | 1.4441
0.048611 | 1.5178
0.055556 | 1.4803
0.0625 | 1.5586
0.069444 | 1.4148
0.076389 | 1.58
0.083333 | 1.3491
0.090278 | 1.5876
0.097222 | 1.4757
0.10417 | 1.5167
0.11111 | 1.3035
0.11806 | 1.373
0.125 | 1.6175
0.13194 | 1.7029
0.13889 | 1.4725
0.14583 | 1.5604
0.15278 | 1.6781
0.15972 | 1.6774
0.16667 | 1.3135
0.17361 | 1.3949
0.18056 | 1.4583
0.1875 | 1.6402
0.19444 | 1.3632
0.20139 | 1.4707
0.20833 | 1.6271
0.21528 | 1.5066
0.22222 | 1.5451
0.22917 | 1.4678
0.23611 | 1.5788
0.24306 | 1.5929
0.25 | 1.4509
0.25694 | 1.6797
0.26389 | 1.5591
0.27083 | 1.4364
0.27778 | 1.5603
0.28472 | 1.4465
0.29167 | 1.4845
0.29861 | 1.5612
0.30556 | 1.3956
0.3125 | 1.4654
0.31944 | 1.3829
0.32639 | 1.4314
0.33333 | 1.5926
0.34028 | 1.3518
0.34722 | 1.4442
0.35417 | 1.4972
0.36111 | 1.3524
0.36806 | 1.5259
0.375 | 1.2981
0.38194 | 1.52
0.38889 | 1.5426
0.39583 | 1.373
0.40278 | 1.4515
0.40972 | 1.5594
0.41667 | 1.4724
0.42361 | 1.3142
0.43056 | 1.5041
0.4375 | 1.5283
0.44444 | 1.5064
0.45139 | 1.5433
0.45833 | 1.5423
0.46528 | 1.63
0.47222 | 1.395
0.47917 | 1.3214
0.48611 | 1.5816
0.49306 | 1.4672
0.5 | 1.3785
0.50694 | 1.6112
0.51389 | 1.4493
0.52083 | 1.5899
0.52778 | 1.5377
0.53472 | 1.6452
0.54167 | 1.5447
0.54861 | 1.5646
0.55556 | 1.4376
0.5625 | 1.4405
0.56944 | 1.6611
0.57639 | 1.4651
0.58333 | 1.5164
0.59028 | 1.3363
0.59722 | 1.5581
0.60417 | 1.4871
0.61111 | 1.5433
0.61806 | 1.4755
0.625 | 1.3915
0.63194 | 1.6681
0.63889 | 1.5176
0.64583 | 1.2929
0.65278 | 1.5211
0.65972 | 1.4417
0.66667 | 1.5018
0.67361 | 1.6495
0.68056 | 1.4575
0.6875 | 1.6686
0.69444 | 1.5365
0.70139 | 1.3903
0.70833 | 1.693
0.71528 | 1.5623
0.72222 | 1.5657
0.72917 | 1.3537
0.73611 | 1.5854
0.74306 | 1.558
0.75 | 1.4081
0.75694 | 1.5795
0.76389 | 1.5518
0.77083 | 1.5495
0.77778 | 1.5664
0.78472 | 1.429
0.79167 | 1.3693
0.79861 | 1.4258
0.80556 | 1.3532
0.8125 | 1.4608
0.81944 | 1.5842
0.82639 | 1.5083
0.83333 | 1.5315
0.84028 | 1.579
0.84722 | 1.4199
0.85417 | 1.4674
0.86111 | 1.5285
0.86806 | 1.631
0.875 | 1.516
0.88194 | 1.2882
0.88889 | 1.5707
0.89583 | 1.3957
0.90278 | 1.6068
0.90972 | 1.4683
0.91667 | 1.648
0.92361 | 1.5699
0.93056 | 1.5159
0.9375 | 1.4055
0.94444 | 1.4207
0.95139 | 1.2951
0.95833 | 1.2641
0.96528 | 1.3341
0.97222 | 1.4042
0.97917 | 1.5226
0.98611 | 1.5218
0.99306 | 1.4177
1 | 1.3987
1.0069 | 1.6215
1.0139 | 1.5156
1.0208 | 1.46
1.0278 | 1.4558
1.0347 | 1.5448
1.0417 | 1.3335
1.0486 | 1.5215
1.0556 | 1.555
1.0625 | 1.6392
1.0694 | 1.4381
1.0764 | 1.4987
1.0833 | 1.5774
1.0903 | 1.6629
1.0972 | 1.359
1.1042 | 1.3253
1.1111 | 1.4528
1.1181 | 1.494
1.125 | 1.5439
1.1319 | 1.5201
1.1389 | 1.4417
1.1458 | 1.5765
1.1528 | 1.5141
1.1597 | 1.4627
1.1667 | 1.5105
1.1736 | 1.6271
1.1806 | 1.5499
1.1875 | 1.4603
1.1944 | 1.321
1.2014 | 1.4733
1.2083 | 1.5178
1.2153 | 1.4566
1.2222 | 1.5465
1.2292 | 1.3879
1.2361 | 1.4641
1.2431 | 1.5532
1.25 | 1.3356
1.2569 | 1.5467
1.2639 | 1.5112
1.2708 | 1.6497
1.2778 | 1.4413
1.2847 | 1.3281
1.2917 | 1.5741
1.2986 | 1.6088
1.3056 | 1.5757
1.3125 | 1.663
1.3194 | 1.3625
1.3264 | 1.3948
1.3333 | 1.5478
1.3403 | 1.6222
1.3472 | 1.7371
1.3542 | 1.5115
1.3611 | 1.5279
1.3681 | 1.5752
1.375 | 1.474
1.3819 | 1.4974
1.3889 | 1.5097
1.3958 | 1.5144
1.4028 | 1.6856
1.4097 | 1.61
1.4167 | 1.4636
1.4236 | 1.5472
1.4306 | 1.4161
1.4375 | 1.4476
1.4444 | 1.3611
1.4514 | 1.5004
1.4583 | 1.3595
1.4653 | 1.7629
1.4722 | 1.582
1.4792 | 1.3557
1.4861 | 1.45
1.4931 | 1.4482
1.5 | 1.3197
1.5069 | 1.5988
1.5139 | 1.4639
1.5208 | 1.6133
1.5278 | 1.5409
1.5347 | 1.5819
1.5417 | 1.532
1.5486 | 1.7415
1.5556 | 1.4886
1.5625 | 1.5118
1.5694 | 1.6
1.5764 | 1.4642
1.5833 | 1.4945
1.5903 | 1.5241
1.5972 | 1.2265
1.6042 | 1.5194
1.6111 | 1.4855
1.6181 | 1.6455
1.625 | 1.4603
1.6319 | 1.6729
1.6389 | 1.5252
1.6458 | 1.4381
1.6528 | 1.5976
1.6597 | 1.5131
1.6667 | 1.4636
1.6736 | 1.4907
1.6806 | 1.549
1.6875 | 1.6401
1.6944 | 1.4726
1.7014 | 1.5676
1.7083 | 1.5191
1.7153 | 1.567
1.7222 | 1.5208
1.7292 | 1.5328
1.7361 | 1.4177
1.7431 | 1.5332
1.75 | 1.5344
1.7569 | 1.538
1.7639 | 1.6089
1.7708 | 1.5995
1.7778 | 1.5209
1.7847 | 1.4601
1.7917 | 1.5506
1.7986 | 1.4872
1.8056 | 1.4745
1.8125 | 1.4922
1.8194 | 1.4685
1.8264 | 1.4692
1.8333 | 1.5401
1.8403 | 1.4871
1.8472 | 1.6328
1.8542 | 1.5671
1.8611 | 1.4308
1.8681 | 1.4951
1.875 | 1.4673
1.8819 | 1.5303
1.8889 | 1.7057
1.8958 | 1.6707
1.9028 | 1.5511
1.9097 | 1.4812
1.9167 | 1.4411
1.9236 | 1.6143
1.9306 | 1.513
1.9375 | 1.5586
1.9444 | 1.5103
1.9514 | 1.5265
1.9583 | 1.5055
1.9653 | 1.5221
1.9722 | 1.5091
1.9792 | 1.485
1.9861 | 1.4439
1.9931 | 1.3201
2 | 1.4529
2.0069 | 1.4097
2.0139 | 1.5548
2.0208 | 1.4265
2.0278 | 1.6476
2.0347 | 1.5506
2.0417 | 1.5693
2.0486 | 1.5135
2.0556 | 1.3931
2.0625 | 1.4832
2.0694 | 1.4537
2.0764 | 1.3736
2.0833 | 1.542
2.0903 | 1.4676
2.0972 | 1.6341
2.1042 | 1.6214
2.1111 | 1.4497
2.1181 | 1.3884
2.125 | 1.4078
2.1319 | 1.4999
2.1389 | 1.5153
2.1458 | 1.4096
2.1528 | 1.4062
2.1597 | 1.5434
2.1667 | 1.4847
2.1736 | 1.5402
2.1806 | 1.4347
2.1875 | 1.3042
2.1944 | 1.5068
2.2014 | 1.4953
2.2083 | 1.4303
2.2153 | 1.5458
2.2222 | 1.5079
2.2292 | 1.548
2.2361 | 1.264
2.2431 | 1.5444
2.25 | 1.4675
2.2569 | 1.5097
2.2639 | 1.6115
2.2708 | 1.3843
2.2778 | 1.4524
2.2847 | 1.5523
2.2917 | 1.5887
2.2986 | 1.5017
2.3056 | 1.5903
2.3125 | 1.6155
2.3194 | 1.5873
2.3264 | 1.4531
2.3333 | 1.5597
2.3403 | 1.5836
2.3472 | 1.5304
2.3542 | 1.6155
2.3611 | 1.3428
2.3681 | 1.6636
2.375 | 1.5555
2.3819 | 1.4415
2.3889 | 1.449
2.3958 | 1.5493
2.4028 | 1.4349
2.4097 | 1.5927
2.4167 | 1.4812
2.4236 | 1.5321
2.4306 | 1.642
2.4375 | 1.381
2.4444 | 1.4072
2.4514 | 1.631
2.4583 | 1.5115
2.4653 | 1.7828
2.4722 | 1.5274
2.4792 | 1.5116
2.4861 | 1.393
2.4931 | 1.429
2.5 | 1.3487
2.5069 | 1.3863
2.5139 | 1.6272
2.5208 | 1.3856
2.5278 | 1.4474
2.5347 | 1.6578
2.5417 | 1.5579
2.5486 | 1.5579
2.5556 | 1.3577
2.5625 | 1.481
2.5694 | 1.5186
2.5764 | 1.6484
2.5833 | 1.4321
2.5903 | 1.447
2.5972 | 1.4141
2.6042 | 1.6306
2.6111 | 1.4914
2.6181 | 1.285
2.625 | 1.5025
2.6319 | 1.3864
2.6389 | 1.5715
2.6458 | 1.4383
2.6528 | 1.4045
2.6597 | 1.5136
2.6667 | 1.5638
2.6736 | 1.4633
2.6806 | 1.6061
2.6875 | 1.5056
2.6944 | 1.5085
2.7014 | 1.6836
2.7083 | 1.5675
2.7153 | 1.3454
2.7222 | 1.5354
2.7292 | 1.4908
2.7361 | 1.5638
2.7431 | 1.4137
2.75 | 1.4114
2.7569 | 1.3777
2.7639 | 1.4814
2.7708 | 1.3279
2.7778 | 1.5152
2.7847 | 1.5817
2.7917 | 1.5578
2.7986 | 1.6064
2.8056 | 1.4197
2.8125 | 1.5799
2.8194 | 1.4685
2.8264 | 1.6186
2.8333 | 1.5085
2.8403 | 1.3575
2.8472 | 1.3546
2.8542 | 1.3191
2.8611 | 1.3537
2.8681 | 1.4862
2.875 | 1.3994
2.8819 | 1.2267
2.8889 | 1.6692
2.8958 | 1.4717
2.9028 | 1.6122
2.9097 | 1.4693
2.9167 | 1.4831
2.9236 | 1.4919
2.9306 | 1.4962
2.9375 | 1.7091
2.9444 | 1.4589
2.9514 | 1.7958
2.9583 | 1.3313
2.9653 | 1.529
2.9722 | 1.3531
2.9792 | 1.5449
2.9861 | 1.3304
2.9931 | 1.506
3 | 1.3852
3.0069 | 1.6994
3.0139 | 1.5921
3.0208 | 1.6623
3.0278 | 1.4512
3.0347 | 1.3804
3.0417 | 1.3581
3.0486 | 1.5468
3.0556 | 1.633
3.0625 | 1.7305
3.0694 | 1.5851
3.0764 | 1.5522
3.0833 | 1.8201
3.0903 | 1.467
3.0972 | 1.4104
3.1042 | 1.4006
3.1111 | 1.3128
3.1181 | 1.6498
3.125 | 1.3368
3.1319 | 1.4148
3.1389 | 1.6077
3.1458 | 1.456
3.1528 | 1.8328
3.1597 | 1.5104
3.1667 | 1.4227
3.1736 | 1.5677
3.1806 | 1.4303
3.1875 | 1.4925
3.1944 | 1.5026
3.2014 | 1.7006
3.2083 | 1.387
3.2153 | 1.5654
3.2222 | 1.6419
3.2292 | 1.4174
3.2361 | 1.5053
3.2431 | 1.4144
3.25 | 1.6768
3.2569 | 1.5183
3.2639 | 1.5431
3.2708 | 1.4771
3.2778 | 1.5394
3.2847 | 1.4474
3.2917 | 1.2553
3.2986 | 1.5155
3.3056 | 1.4166
3.3125 | 1.5078
3.3194 | 1.6313
3.3264 | 1.4865
3.3333 | 1.359
3.3403 | 1.4837
3.3472 | 1.711
3.3542 | 1.6463
3.3611 | 1.5914
3.3681 | 1.6512
3.375 | 1.4546
3.3819 | 1.3861
3.3889 | 1.4295
3.3958 | 1.4669
3.4028 | 1.3479
3.4097 | 1.5165
3.4167 | 1.4512
3.4236 | 1.5587
3.4306 | 1.4097
3.4375 | 1.5371
3.4444 | 1.374
3.4514 | 1.5223
3.4583 | 1.4587
3.4653 | 1.3983
3.4722 | 1.4674
3.4792 | 1.5284
3.4861 | 1.4988
3.4931 | 1.5036
3.5 | 1.3902
3.5069 | 1.5376
3.5139 | 1.517
3.5208 | 1.614
3.5278 | 1.6657
3.5347 | 1.5338
3.5417 | 1.3181
3.5486 | 1.4198
3.5556 | 1.4426
3.5625 | 1.4766
3.5694 | 1.4695
3.5764 | 1.6639
3.5833 | 1.3103
3.5903 | 1.6319
3.5972 | 1.5532
3.6042 | 1.5602
3.6111 | 1.5467
3.6181 | 1.5208
3.625 | 1.4942
3.6319 | 1.1935
3.6389 | 1.4388
3.6458 | 1.4984
3.6528 | 1.5777
3.6597 | 1.491
3.6667 | 1.4851
3.6736 | 1.4112
3.6806 | 1.4224
3.6875 | 1.5629
3.6944 | 1.3684
3.7014 | 1.5899
3.7083 | 1.4175
3.7153 | 1.4424
3.7222 | 1.5025
3.7292 | 1.5563
3.7361 | 1.4828
3.7431 | 1.4352
3.75 | 1.4847
3.7569 | 1.5017
3.7639 | 1.5828
3.7708 | 1.5699
3.7778 | 1.3994
3.7847 | 1.2756
3.7917 | 1.5102
3.7986 | 1.5902
3.8056 | 1.1994
3.8125 | 1.5659
3.8194 | 1.576
3.8264 | 1.483
3.8333 | 1.5709
3.8403 | 1.5629
3.8472 | 1.4236
3.8542 | 1.6188
3.8611 | 1.6164
3.8681 | 1.5438
3.875 | 1.5764
3.8819 | 1.5172
3.8889 | 1.4364
3.8958 | 1.5264
3.9028 | 1.5558
3.9097 | 1.4676
3.9167 | 1.5239
3.9236 | 1.4331
3.9306 | 1.5542
3.9375 | 1.4265
3.9444 | 1.5616
3.9514 | 1.4771
3.9583 | 1.5821
3.9653 | 1.4845
3.9722 | 1.3692
3.9792 | 1.5778
3.9861 | 1.382
3.9931 | 1.5288
4 | 1.5449
4.0069 | 1.4464
4.0139 | 1.4079
4.0208 | 1.4314
4.0278 | 1.3907
4.0347 | 1.4511
4.0417 | 1.4081
4.0486 | 1.2968
4.0556 | 1.5639
4.0625 | 1.6136
4.0694 | 1.4214
4.0764 | 1.3988
4.0833 | 1.3992
4.0903 | 1.6521
4.0972 | 1.5663
4.1042 | 1.5071
4.1111 | 1.4416
4.1181 | 1.6015
4.125 | 1.4773
4.1319 | 1.5644
4.1389 | 1.5201
4.1458 | 1.4971
4.1528 | 1.4008
4.1597 | 1.6984
4.1667 | 1.406
4.1736 | 1.3391
4.1806 | 1.478
4.1875 | 1.4723
4.1944 | 1.412
4.2014 | 1.5584
4.2083 | 1.4636
4.2153 | 1.5417
4.2222 | 1.6287
4.2292 | 1.3596
4.2361 | 1.5444
4.2431 | 1.6441
4.25 | 1.5333
4.2569 | 1.5516
4.2639 | 1.4768
4.2708 | 1.5602
4.2778 | 1.5613
4.2847 | 1.4608
4.2917 | 1.5711
4.2986 | 1.3105
4.3056 | 1.6358
4.3125 | 1.4088
4.3194 | 1.485
4.3264 | 1.4599
4.3333 | 1.4422
4.3403 | 1.7004
4.3472 | 1.449
4.3542 | 1.5089
4.3611 | 1.498
4.3681 | 1.4262
4.375 | 1.3848
4.3819 | 1.3052
4.3889 | 1.5026
4.3958 | 1.4174
4.4028 | 1.4282
4.4097 | 1.3059
4.4167 | 1.5988
4.4236 | 1.3337
4.4306 | 1.7063
4.4375 | 1.2918
4.4444 | 1.5273
4.4514 | 1.2623
4.4583 | 1.5379
4.4653 | 1.4009
4.4722 | 1.5094
4.4792 | 1.5644
4.4861 | 1.4217
4.4931 | 1.5149
4.5 | 1.4079
4.5069 | 1.6191
4.5139 | 1.5981
4.5208 | 1.4277
4.5278 | 1.7334
4.5347 | 1.2449
4.5417 | 1.5903
4.5486 | 1.5227
4.5556 | 1.4649
4.5625 | 1.5527
4.5694 | 1.5875
4.5764 | 1.8068
4.5833 | 1.4381
4.5903 | 1.5758
4.5972 | 1.6029
4.6042 | 1.5053
4.6111 | 1.5211
4.6181 | 1.6152
4.625 | 1.4648
4.6319 | 1.5516
4.6389 | 1.5962
4.6458 | 1.5387
4.6528 | 1.4775
4.6597 | 1.5249
4.6667 | 1.3084
4.6736 | 1.5711
4.6806 | 1.6563
4.6875 | 1.4175
4.6944 | 1.4432
4.7014 | 1.4276
4.7083 | 1.3991
4.7153 | 1.5731
4.7222 | 1.5085
4.7292 | 1.4572
4.7361 | 1.4404
4.7431 | 1.4254
4.75 | 1.5643
4.7569 | 1.4807
4.7639 | 1.4874
4.7708 | 1.4926
4.7778 | 1.6122
4.7847 | 1.4747
4.7917 | 1.4605
4.7986 | 1.5394
4.8056 | 1.4321
4.8125 | 1.4834
4.8194 | 1.4491
4.8264 | 1.5489
4.8333 | 1.6226
4.8403 | 1.4848
4.8472 | 1.5839
4.8542 | 1.4934
4.8611 | 1.5882
4.8681 | 1.4386
4.875 | 1.4887
4.8819 | 1.5752
4.8889 | 1.5502
4.8958 | 1.6772
4.9028 | 1.5026
4.9097 | 1.4995
4.9167 | 1.6034
4.9236 | 1.3397
4.9306 | 1.5322
4.9375 | 1.7312
4.9444 | 1.5026
4.9514 | 1.449
4.9583 | 1.639
4.9653 | 1.3542
4.9722 | 1.5666
4.9792 | 1.5225
4.9861 | 1.7099
4.9931 | 1.5479
5 | 1.565
5.0069 | 1.3274
5.0139 | 1.6604
5.0208 | 1.4454
5.0278 | 1.449
5.0347 | 1.7099
5.0417 | 1.6022
5.0486 | 1.4796
5.0556 | 1.3851
5.0625 | 1.6057
5.0694 | 1.4929
5.0764 | 1.3338
5.0833 | 1.6725
5.0903 | 1.5981
5.0972 | 1.4982
5.1042 | 1.63
5.1111 | 1.4718
5.1181 | 1.5242
5.125 | 1.4726
5.1319 | 1.5018
5.1389 | 1.3463
5.1458 | 1.7541
5.1528 | 1.4574
5.1597 | 1.3695
5.1667 | 1.4392
5.1736 | 1.3118
5.1806 | 1.5389
5.1875 | 1.5028
5.1944 | 1.5015
5.2014 | 1.6477
5.2083 | 1.5253
5.2153 | 1.5653
5.2222 | 1.4835
5.2292 | 1.5536
5.2361 | 1.4441
5.2431 | 1.4568
5.25 | 1.3129
5.2569 | 1.4527
5.2639 | 1.3805
5.2708 | 1.4705
5.2778 | 1.5712
5.2847 | 1.4683
5.2917 | 1.6346
5.2986 | 1.5432
5.3056 | 1.471
5.3125 | 1.5805
5.3194 | 1.5349
5.3264 | 1.4325
5.3333 | 1.616
5.3403 | 1.4962
5.3472 | 1.4502
5.3542 | 1.4835
5.3611 | 1.5255
5.3681 | 1.4486
5.375 | 1.605
5.3819 | 1.4703
5.3889 | 1.5208
5.3958 | 1.4984
5.4028 | 1.5885
5.4097 | 1.67
5.4167 | 1.3308
5.4236 | 1.5187
5.4306 | 1.6299
5.4375 | 1.4823
5.4444 | 1.6267
5.4514 | 1.4357
5.4583 | 1.5589
5.4653 | 1.5492
5.4722 | 1.4682
5.4792 | 1.392
5.4861 | 1.4763
5.4931 | 1.6038
5.5 | 1.4494
5.5069 | 1.6149
5.5139 | 1.3342
5.5208 | 1.4341
5.5278 | 1.3825
5.5347 | 1.5406
5.5417 | 1.5561
5.5486 | 1.5764
5.5556 | 1.4749
5.5625 | 1.558
5.5694 | 1.414
5.5764 | 1.4758
5.5833 | 1.4765
5.5903 | 1.4482
5.5972 | 1.405
5.6042 | 1.524
5.6111 | 1.5559
5.6181 | 1.535
5.625 | 1.5275
5.6319 | 1.3918
5.6389 | 1.3465
5.6458 | 1.5024
5.6528 | 1.6571
5.6597 | 1.2962
5.6667 | 1.4795
5.6736 | 1.4821
5.6806 | 1.499
5.6875 | 1.3756
5.6944 | 1.4296
5.7014 | 1.3906
5.7083 | 1.6129
5.7153 | 1.6118
5.7222 | 1.4775
5.7292 | 1.5072
5.7361 | 1.3621
5.7431 | 1.503
5.75 | 1.4603
5.7569 | 1.6692
5.7639 | 1.5755
5.7708 | 1.5524
5.7778 | 1.4526
5.7847 | 1.498
5.7917 | 1.8138
5.7986 | 1.6553
5.8056 | 1.5062
5.8125 | 1.5446
5.8194 | 1.5216
5.8264 | 1.4835
5.8333 | 1.4739
5.8403 | 1.5128
5.8472 | 1.5843
5.8542 | 1.5764
5.8611 | 1.522
5.8681 | 1.6041
5.875 | 1.3675
5.8819 | 1.5636
5.8889 | 1.3323
5.8958 | 1.4686
5.9028 | 1.4403
5.9097 | 1.5418
5.9167 | 1.2695
5.9236 | 1.4225
5.9306 | 1.3379
5.9375 | 1.5428
5.9444 | 1.5236
5.9514 | 1.4821
5.9583 | 1.4794
5.9653 | 1.6219
5.9722 | 1.4961
5.9792 | 1.5079
5.9861 | 1.4316
5.9931 | 1.5108
6 | 1.4807
6.0069 | 1.4818
6.0139 | 1.46
6.0208 | 1.479
6.0278 | 1.4896
6.0347 | 1.6331
6.0417 | 1.4458
6.0486 | 1.5979
6.0556 | 1.5276
6.0625 | 1.6449
6.0694 | 1.4693
6.0764 | 1.4273
6.0833 | 1.6279
6.0903 | 1.2236
6.0972 | 1.4432
6.1042 | 1.7763
6.1111 | 1.5061
6.1181 | 1.2937
6.125 | 1.5031
6.1319 | 1.5326
6.1389 | 1.5731
6.1458 | 1.6355
6.1528 | 1.4785
6.1597 | 1.5536
6.1667 | 1.5574
6.1736 | 1.4985
6.1806 | 1.506
6.1875 | 1.4082
6.1944 | 1.4476
6.2014 | 1.395
6.2083 | 1.5306
6.2153 | 1.4942
6.2222 | 1.4822
6.2292 | 1.6482
6.2361 | 1.5132
6.2431 | 1.4948
6.25 | 1.445
6.2569 | 1.3266
6.2639 | 1.4613
6.2708 | 1.2635
6.2778 | 1.4429
6.2847 | 1.501
6.2917 | 1.6256
6.2986 | 1.4179
6.3056 | 1.5305
6.3125 | 1.5
6.3194 | 1.2756
6.3264 | 1.3137
6.3333 | 1.4804
6.3403 | 1.6226
6.3472 | 1.4396
6.3542 | 1.5678
6.3611 | 1.4274
6.3681 | 1.3927
6.375 | 1.3698
6.3819 | 1.477
6.3889 | 1.4343
6.3958 | 1.5382
6.4028 | 1.3551
6.4097 | 1.4022
6.4167 | 1.3776
6.4236 | 1.3923
6.4306 | 1.5624
6.4375 | 1.4542
6.4444 | 1.4438
6.4514 | 1.5136
6.4583 | 1.6022
6.4653 | 1.6936
6.4722 | 1.6561
6.4792 | 1.6359
6.4861 | 1.3135
6.4931 | 1.3283
6.5 | 1.4938
6.5069 | 1.4295
6.5139 | 1.6107
6.5208 | 1.4955
6.5278 | 1.5119
6.5347 | 1.5878
6.5417 | 1.492
6.5486 | 1.559
6.5556 | 1.4445
6.5625 | 1.4384
6.5694 | 1.4311
6.5764 | 1.5117
6.5833 | 1.4144
6.5903 | 1.5797
6.5972 | 1.2536
6.6042 | 1.4525
6.6111 | 1.5563
6.6181 | 1.4447
6.625 | 1.4705
6.6319 | 1.5125
6.6389 | 1.5109
6.6458 | 1.388
6.6528 | 1.5473
6.6597 | 1.6779
6.6667 | 1.58
6.6736 | 1.4342
6.6806 | 1.5108
6.6875 | 1.4483
6.6944 | 1.512
6.7014 | 1.6931
6.7083 | 1.4467
6.7153 | 1.5923
6.7222 | 1.3963
6.7292 | 1.528
6.7361 | 1.4477
6.7431 | 1.5546
6.75 | 1.5705
6.7569 | 1.5468
6.7639 | 1.49
6.7708 | 1.3932
6.7778 | 1.2411
6.7847 | 1.4551
6.7917 | 1.356
6.7986 | 1.5935
6.8056 | 1.5376
6.8125 | 1.4749
6.8194 | 1.5497
6.8264 | 1.5093
6.8333 | 1.3036
6.8403 | 1.4599
6.8472 | 1.3906
6.8542 | 1.4322
6.8611 | 1.303
6.8681 | 1.5307
6.875 | 1.5047
6.8819 | 1.5216
6.8889 | 1.4763
6.8958 | 1.6666
6.9028 | 1.4777
6.9097 | 1.3629
6.9167 | 1.5856
6.9236 | 1.5722
6.9306 | 1.5713
6.9375 | 1.5644
6.9444 | 1.3706
6.9514 | 1.4172
6.9583 | 1.4435
6.9653 | 1.4771
6.9722 | 1.5856
6.9792 | 1.3698
6.9861 | 1.4926
6.9931 | 1.2802
7 | 1.5864
DOsine | Disabled
No interpolation | Repeated every 168 hours
Time | SO2
d | g O2/m3
0 | 1.6851
0.0069444 | 1.8743
0.013889 | 1.6866
0.020833 | 1.6577
0.027778 | 1.6904
0.034722 | 1.7239
0.041667 | 1.7315
0.048611 | 1.8115
0.055556 | 1.7802
0.0625 | 1.8647
0.069444 | 1.7271
0.076389 | 1.8985
0.083333 | 1.6738
0.090278 | 1.9185
0.097222 | 1.8129
0.10417 | 1.86
0.11111 | 1.653
0.11806 | 1.7288
0.125 | 1.9795
0.13194 | 2.0711
0.13889 | 1.8468
0.14583 | 1.9409
0.15278 | 2.0648
0.15972 | 2.0702
0.16667 | 1.7125
0.17361 | 1.8001
0.18056 | 1.8696
0.1875 | 2.0577
0.19444 | 1.7869
0.20139 | 1.9005
0.20833 | 2.063
0.21528 | 1.9486
0.22222 | 1.9933
0.22917 | 1.922
0.23611 | 2.0392
0.24306 | 2.0593
0.25 | 1.9234
0.25694 | 2.1583
0.26389 | 2.0437
0.27083 | 1.9271
0.27778 | 2.0571
0.28472 | 1.9493
0.29167 | 1.9933
0.29861 | 2.076
0.30556 | 1.9164
0.3125 | 1.9923
0.31944 | 1.9157
0.32639 | 1.9702
0.33333 | 2.1374
0.34028 | 1.9025
0.34722 | 2.0008
0.35417 | 2.0597
0.36111 | 1.9209
0.36806 | 2.1003
0.375 | 1.8784
0.38194 | 2.1061
0.38889 | 2.1346
0.39583 | 1.9709
0.40278 | 2.0552
0.40972 | 2.169
0.41667 | 2.0877
0.42361 | 1.9354
0.43056 | 2.131
0.4375 | 2.161
0.44444 | 2.1448
0.45139 | 2.1875
0.45833 | 2.1922
0.46528 | 2.2856
0.47222 | 2.0563
0.47917 | 1.9883
0.48611 | 2.2542
0.49306 | 2.1454
0.5 | 2.0624
0.50694 | 2.3007
0.51389 | 2.1443
0.52083 | 2.2905
0.52778 | 2.2439
0.53472 | 2.357
0.54167 | 2.262
0.54861 | 2.2874
0.55556 | 2.1659
0.5625 | 2.1742
0.56944 | 2.4003
0.57639 | 2.2097
0.58333 | 2.2664
0.59028 | 2.0917
0.59722 | 2.3189
0.60417 | 2.2532
0.61111 | 2.3147
0.61806 | 2.2522
0.625 | 2.1735
0.63194 | 2.4554
0.63889 | 2.3102
0.64583 | 2.0906
0.65278 | 2.3241
0.65972 | 2.2499
0.66667 | 2.3151
0.67361 | 2.4679
0.68056 | 2.2811
0.6875 | 2.4973
0.69444 | 2.3703
0.70139 | 2.2291
0.70833 | 2.5368
0.71528 | 2.4111
0.72222 | 2.4195
0.72917 | 2.2124
0.73611 | 2.4491
0.74306 | 2.4267
0.75 | 2.2816
0.75694 | 2.4578
0.76389 | 2.4349
0.77083 | 2.4375
0.77778 | 2.4592
0.78472 | 2.3265
0.79167 | 2.2716
0.79861 | 2.3328
0.80556 | 2.2649
0.8125 | 2.3772
0.81944 | 2.5051
0.82639 | 2.4339
0.83333 | 2.4616
0.84028 | 2.5137
0.84722 | 2.3591
0.85417 | 2.4112
0.86111 | 2.4767
0.86806 | 2.5836
0.875 | 2.4731
0.88194 | 2.2497
0.88889 | 2.5366
0.89583 | 2.3659
0.90278 | 2.5813
0.90972 | 2.4471
0.91667 | 2.631
0.92361 | 2.5572
0.93056 | 2.5074
0.9375 | 2.4011
0.94444 | 2.4205
0.95139 | 2.299
0.95833 | 2.2721
0.96528 | 2.3461
0.97222 | 2.4202
0.97917 | 2.5426
0.98611 | 2.5458
0.99306 | 2.4456
1 | 2.4306
1.0069 | 2.6572
1.0139 | 2.5552
1.0208 | 2.5033
1.0278 | 2.503
1.0347 | 2.5957
1.0417 | 2.3881
1.0486 | 2.5798
1.0556 | 2.6169
1.0625 | 2.7048
1.0694 | 2.5072
1.0764 | 2.5715
1.0833 | 2.6536
1.0903 | 2.7427
1.0972 | 2.4422
1.1042 | 2.4119
1.1111 | 2.5428
1.1181 | 2.5874
1.125 | 2.6406
1.1319 | 2.6201
1.1389 | 2.545
1.1458 | 2.683
1.1528 | 2.6238
1.1597 | 2.5756
1.1667 | 2.6266
1.1736 | 2.7462
1.1806 | 2.6721
1.1875 | 2.5855
1.1944 | 2.4492
1.2014 | 2.6045
1.2083 | 2.652
1.2153 | 2.5936
1.2222 | 2.6863
1.2292 | 2.5306
1.2361 | 2.6096
1.2431 | 2.7015
1.25 | 2.4866
1.2569 | 2.7003
1.2639 | 2.6675
1.2708 | 2.8086
1.2778 | 2.6029
1.2847 | 2.4922
1.2917 | 2.7407
1.2986 | 2.7778
1.3056 | 2.7471
1.3125 | 2.8368
1.3194 | 2.5387
1.3264 | 2.5734
1.3333 | 2.7286
1.3403 | 2.8054
1.3472 | 2.9224
1.3542 | 2.699
1.3611 | 2.7176
1.3681 | 2.767
1.375 | 2.6679
1.3819 | 2.6933
1.3889 | 2.7076
1.3958 | 2.7143
1.4028 | 2.8874
1.4097 | 2.8138
1.4167 | 2.6692
1.4236 | 2.7546
1.4306 | 2.6253
1.4375 | 2.6586
1.4444 | 2.5737
1.4514 | 2.7147
1.4583 | 2.5754
1.4653 | 2.9804
1.4722 | 2.801
1.4792 | 2.5763
1.4861 | 2.6721
1.4931 | 2.6717
1.5 | 2.5447
1.5069 | 2.8251
1.5139 | 2.6916
1.5208 | 2.8422
1.5278 | 2.7711
1.5347 | 2.8133
1.5417 | 2.7645
1.5486 | 2.9752
1.5556 | 2.7234
1.5625 | 2.7477
1.5694 | 2.8369
1.5764 | 2.7021
1.5833 | 2.7333
1.5903 | 2.7639
1.5972 | 2.4671
1.6042 | 2.7608
1.6111 | 2.7277
1.6181 | 2.8885
1.625 | 2.704
1.6319 | 2.9173
1.6389 | 2.7702
1.6458 | 2.6838
1.6528 | 2.8438
1.6597 | 2.7598
1.6667 | 2.7108
1.6736 | 2.7383
1.6806 | 2.797
1.6875 | 2.8886
1.6944 | 2.7213
1.7014 | 2.8166
1.7083 | 2.7684
1.7153 | 2.8166
1.7222 | 2.7705
1.7292 | 2.7826
1.7361 | 2.6676
1.7431 | 2.7832
1.75 | 2.7844
1.7569 | 2.788
1.7639 | 2.8588
1.7708 | 2.8493
1.7778 | 2.7706
1.7847 | 2.7096
1.7917 | 2.7999
1.7986 | 2.7363
1.8056 | 2.7233
1.8125 | 2.7406
1.8194 | 2.7166
1.8264 | 2.7168
1.8333 | 2.7873
1.8403 | 2.7338
1.8472 | 2.879
1.8542 | 2.8127
1.8611 | 2.6759
1.8681 | 2.7395
1.875 | 2.711
1.8819 | 2.7733
1.8889 | 2.9479
1.8958 | 2.9122
1.9028 | 2.7917
1.9097 | 2.721
1.9167 | 2.6799
1.9236 | 2.8522
1.9306 | 2.7499
1.9375 | 2.7945
1.9444 | 2.7451
1.9514 | 2.7602
1.9583 | 2.738
1.9653 | 2.7535
1.9722 | 2.7393
1.9792 | 2.7139
1.9861 | 2.6715
1.9931 | 2.5464
2 | 2.6779
2.0069 | 2.6333
2.0139 | 2.7769
2.0208 | 2.6471
2.0278 | 2.8667
2.0347 | 2.7681
2.0417 | 2.7852
2.0486 | 2.7278
2.0556 | 2.6057
2.0625 | 2.6942
2.0694 | 2.6629
2.0764 | 2.581
2.0833 | 2.7476
2.0903 | 2.6713
2.0972 | 2.8359
2.1042 | 2.8213
2.1111 | 2.6476
2.1181 | 2.5843
2.125 | 2.6017
2.1319 | 2.6917
2.1389 | 2.705
2.1458 | 2.5971
2.1528 | 2.5915
2.1597 | 2.7265
2.1667 | 2.6656
2.1736 | 2.7188
2.1806 | 2.611
2.1875 | 2.4781
2.1944 | 2.6782
2.2014 | 2.6643
2.2083 | 2.5969
2.2153 | 2.7098
2.2222 | 2.6694
2.2292 | 2.7069
2.2361 | 2.4203
2.2431 | 2.6981
2.25 | 2.6185
2.2569 | 2.658
2.2639 | 2.757
2.2708 | 2.527
2.2778 | 2.5923
2.2847 | 2.6893
2.2917 | 2.7228
2.2986 | 2.6328
2.3056 | 2.7185
2.3125 | 2.7407
2.3194 | 2.7094
2.3264 | 2.5722
2.3333 | 2.6757
2.3403 | 2.6965
2.3472 | 2.6402
2.3542 | 2.7221
2.3611 | 2.4461
2.3681 | 2.7637
2.375 | 2.6522
2.3819 | 2.5348
2.3889 | 2.539
2.3958 | 2.6359
2.4028 | 2.5181
2.4097 | 2.6724
2.4167 | 2.5574
2.4236 | 2.6048
2.4306 | 2.7112
2.4375 | 2.4466
2.4444 | 2.4691
2.4514 | 2.6892
2.4583 | 2.5661
2.4653 | 2.8337
2.4722 | 2.5745
2.4792 | 2.5549
2.4861 | 2.4325
2.4931 | 2.4647
2.5 | 2.3805
2.5069 | 2.4142
2.5139 | 2.6512
2.5208 | 2.4056
2.5278 | 2.4634
2.5347 | 2.6698
2.5417 | 2.5658
2.5486 | 2.5617
2.5556 | 2.3575
2.5625 | 2.4766
2.5694 | 2.5101
2.5764 | 2.6357
2.5833 | 2.4151
2.5903 | 2.4258
2.5972 | 2.3886
2.6042 | 2.6008
2.6111 | 2.4572
2.6181 | 2.2465
2.625 | 2.4596
2.6319 | 2.3391
2.6389 | 2.5197
2.6458 | 2.3821
2.6528 | 2.3437
2.6597 | 2.4483
2.6667 | 2.494
2.6736 | 2.3889
2.6806 | 2.5271
2.6875 | 2.422
2.6944 | 2.4202
2.7014 | 2.5906
2.7083 | 2.4698
2.7153 | 2.243
2.7222 | 2.4282
2.7292 | 2.3788
2.7361 | 2.447
2.7431 | 2.2921
2.75 | 2.2848
2.7569 | 2.2463
2.7639 | 2.3451
2.7708 | 2.1867
2.7778 | 2.369
2.7847 | 2.4305
2.7917 | 2.4016
2.7986 | 2.4452
2.8056 | 2.2534
2.8125 | 2.4085
2.8194 | 2.2921
2.8264 | 2.4371
2.8333 | 2.3218
2.8403 | 2.1657
2.8472 | 2.1576
2.8542 | 2.1168
2.8611 | 2.1463
2.8681 | 2.2735
2.875 | 2.1815
2.8819 | 2.0034
2.8889 | 2.4407
2.8958 | 2.2378
2.9028 | 2.373
2.9097 | 2.2247
2.9167 | 2.2331
2.9236 | 2.2365
2.9306 | 2.2354
2.9375 | 2.4429
2.9444 | 2.1872
2.9514 | 2.5185
2.9583 | 2.0485
2.9653 | 2.2408
2.9722 | 2.0593
2.9792 | 2.2456
2.9861 | 2.0255
2.9931 | 2.1955
3 | 2.0691
3.0069 | 2.3777
3.0139 | 2.2647
3.0208 | 2.3292
3.0278 | 2.1125
3.0347 | 2.036
3.0417 | 2.0079
3.0486 | 2.191
3.0556 | 2.2714
3.0625 | 2.3632
3.0694 | 2.2121
3.0764 | 2.1733
3.0833 | 2.4355
3.0903 | 2.0765
3.0972 | 2.0141
3.1042 | 1.9985
3.1111 | 1.9049
3.1181 | 2.2359
3.125 | 1.917
3.1319 | 1.9892
3.1389 | 2.1762
3.1458 | 2.0186
3.1528 | 2.3894
3.1597 | 2.0611
3.1667 | 1.9674
3.1736 | 2.1065
3.1806 | 1.9631
3.1875 | 2.0193
3.1944 | 2.0234
3.2014 | 2.2154
3.2083 | 1.8959
3.2153 | 2.0682
3.2222 | 2.1387
3.2292 | 1.9082
3.2361 | 1.99
3.2431 | 1.893
3.25 | 2.1493
3.2569 | 1.9847
3.2639 | 2.0035
3.2708 | 1.9314
3.2778 | 1.9875
3.2847 | 1.8894
3.2917 | 1.6912
3.2986 | 1.9453
3.3056 | 1.8402
3.3125 | 1.9254
3.3194 | 2.0426
3.3264 | 1.8917
3.3333 | 1.758
3.3403 | 1.8766
3.3472 | 2.0977
3.3542 | 2.0268
3.3611 | 1.9658
3.3681 | 2.0194
3.375 | 1.8165
3.3819 | 1.7418
3.3889 | 1.779
3.3958 | 1.8103
3.4028 | 1.6851
3.4097 | 1.8475
3.4167 | 1.7759
3.4236 | 1.8772
3.4306 | 1.722
3.4375 | 1.8432
3.4444 | 1.6738
3.4514 | 1.8159
3.4583 | 1.7461
3.4653 | 1.6795
3.4722 | 1.7423
3.4792 | 1.797
3.4861 | 1.7613
3.4931 | 1.7599
3.5 | 1.6402
3.5069 | 1.7813
3.5139 | 1.7545
3.5208 | 1.8453
3.5278 | 1.8908
3.5347 | 1.7527
3.5417 | 1.5307
3.5486 | 1.6262
3.5556 | 1.6427
3.5625 | 1.6705
3.5694 | 1.6572
3.5764 | 1.8454
3.5833 | 1.4855
3.5903 | 1.8009
3.5972 | 1.7161
3.6042 | 1.7168
3.6111 | 1.6972
3.6181 | 1.665
3.625 | 1.6323
3.6319 | 1.3253
3.6389 | 1.5644
3.6458 | 1.6179
3.6528 | 1.691
3.6597 | 1.5981
3.6667 | 1.5861
3.6736 | 1.506
3.6806 | 1.511
3.6875 | 1.6454
3.6944 | 1.4448
3.7014 | 1.6601
3.7083 | 1.4816
3.7153 | 1.5004
3.7222 | 1.5544
3.7292 | 1.602
3.7361 | 1.5224
3.7431 | 1.4687
3.75 | 1.5122
3.7569 | 1.5231
3.7639 | 1.5981
3.7708 | 1.5792
3.7778 | 1.4026
3.7847 | 1.2728
3.7917 | 1.5014
3.7986 | 1.5753
3.8056 | 1.1786
3.8125 | 1.5391
3.8194 | 1.5432
3.8264 | 1.4442
3.8333 | 1.5261
3.8403 | 1.5122
3.8472 | 1.367
3.8542 | 1.5562
3.8611 | 1.5479
3.8681 | 1.4694
3.875 | 1.4962
3.8819 | 1.4311
3.8889 | 1.3444
3.8958 | 1.4285
3.9028 | 1.4521
3.9097 | 1.3581
3.9167 | 1.4086
3.9236 | 1.312
3.9306 | 1.4273
3.9375 | 1.2938
3.9444 | 1.4232
3.9514 | 1.3329
3.9583 | 1.4322
3.9653 | 1.3289
3.9722 | 1.2079
3.9792 | 1.4108
3.9861 | 1.2094
3.9931 | 1.3505
4 | 1.361
4.0069 | 1.2569
4.0139 | 1.2128
4.0208 | 1.2307
4.0278 | 1.1845
4.0347 | 1.2394
4.0417 | 1.1909
4.0486 | 1.0741
4.0556 | 1.3356
4.0625 | 1.3799
4.0694 | 1.1823
4.0764 | 1.1542
4.0833 | 1.1492
4.0903 | 1.3967
4.0972 | 1.3056
4.1042 | 1.241
4.1111 | 1.1701
4.1181 | 1.3247
4.125 | 1.1953
4.1319 | 1.2771
4.1389 | 1.2275
4.1458 | 1.1993
4.1528 | 1.0978
4.1597 | 1.3902
4.1667 | 1.0927
4.1736 | 1.0206
4.1806 | 1.1544
4.1875 | 1.1436
4.1944 | 1.0782
4.2014 | 1.2196
4.2083 | 1.1198
4.2153 | 1.1928
4.2222 | 1.2749
4.2292 | 1.0008
4.2361 | 1.1807
4.2431 | 1.2755
4.25 | 1.1598
4.2569 | 1.1732
4.2639 | 1.0936
4.2708 | 1.1722
4.2778 | 1.1685
4.2847 | 1.0632
4.2917 | 1.1688
4.2986 | 0.90352
4.3056 | 1.2241
4.3125 | 0.99247
4.3194 | 1.0641
4.3264 | 1.0343
4.3333 | 1.0121
4.3403 | 1.2657
4.3472 | 1.0098
4.3542 | 1.0651
4.3611 | 1.0498
4.3681 | 0.97351
4.375 | 0.92768
4.3819 | 0.84374
4.3889 | 1.0368
4.3958 | 0.94721
4.4028 | 0.95369
4.4097 | 0.8271
4.4167 | 1.1157
4.4236 | 0.84641
4.4306 | 1.2149
4.4375 | 0.79615
4.4444 | 1.0275
4.4514 | 0.75844
4.4583 | 1.03
4.4653 | 0.88885
4.4722 | 0.99338
4.4792 | 1.0443
4.4861 | 0.89771
4.4931 | 0.98693
4.5 | 0.87609
4.5069 | 1.0834
4.5139 | 1.0586
4.5208 | 0.8843
4.5278 | 1.1863
4.5347 | 0.694
4.5417 | 1.0357
4.5486 | 0.96443
4.5556 | 0.90294
4.5625 | 0.98719
4.5694 | 1.0183
4.5764 | 1.2341
4.5833 | 0.86187
4.5903 | 0.99602
4.5972 | 1.0197
4.6042 | 0.91866
4.6111 | 0.93106
4.6181 | 1.0219
4.625 | 0.86805
4.6319 | 0.95153
4.6389 | 0.99293
4.6458 | 0.93219
4.6528 | 0.86776
4.6597 | 0.91205
4.6667 | 0.69237
4.6736 | 0.952
4.6806 | 1.0341
4.6875 | 0.79224
4.6944 | 0.81497
4.7014 | 0.79645
4.7083 | 0.76498
4.7153 | 0.93604
4.7222 | 0.86865
4.7292 | 0.81451
4.7361 | 0.79487
4.7431 | 0.77719
4.75 | 0.91332
4.7569 | 0.82703
4.7639 | 0.83112
4.7708 | 0.83369
4.7778 | 0.95071
4.7847 | 0.81065
4.7917 | 0.79394
4.7986 | 0.87035
4.8056 | 0.76067
4.8125 | 0.80955
4.8194 | 0.77284
4.8264 | 0.87034
4.8333 | 0.94174
4.8403 | 0.80165
4.8472 | 0.89854
4.8542 | 0.80582
4.8611 | 0.89851
4.8681 | 0.74674
4.875 | 0.7948
4.8819 | 0.8793
4.8889 | 0.8523
4.8958 | 0.97726
4.9028 | 0.80075
4.9097 | 0.79576
4.9167 | 0.89787
4.9236 | 0.63235
4.9306 | 0.82307
4.9375 | 1.0203
4.9444 | 0.78997
4.9514 | 0.73471
4.9583 | 0.92312
4.9653 | 0.63672
4.9722 | 0.84755
4.9792 | 0.80188
4.9861 | 0.9878
4.9931 | 0.82442
5 | 0.8401
5.0069 | 0.60109
5.0139 | 0.93274
5.0208 | 0.71646
5.0278 | 0.7188
5.0347 | 0.97848
5.0417 | 0.86962
5.0486 | 0.74589
5.0556 | 0.6503
5.0625 | 0.86986
5.0694 | 0.75603
5.0764 | 0.59595
5.0833 | 0.93371
5.0903 | 0.85837
5.0972 | 0.75755
5.1042 | 0.88857
5.1111 | 0.72956
5.1181 | 0.78125
5.125 | 0.72893
5.1319 | 0.75745
5.1389 | 0.60123
5.1458 | 1.0085
5.1528 | 0.71121
5.1597 | 0.62277
5.1667 | 0.69203
5.1736 | 0.56415
5.1806 | 0.79085
5.1875 | 0.75435
5.1944 | 0.75271
5.2014 | 0.89862
5.2083 | 0.77602
5.2153 | 0.81583
5.2222 | 0.7338
5.2292 | 0.80381
5.2361 | 0.69415
5.2431 | 0.70686
5.25 | 0.56292
5.2569 | 0.7027
5.2639 | 0.63057
5.2708 | 0.7207
5.2778 | 0.8215
5.2847 | 0.71877
5.2917 | 0.88526
5.2986 | 0.79411
5.3056 | 0.72222
5.3125 | 0.83205
5.3194 | 0.78689
5.3264 | 0.68486
5.3333 | 0.86878
5.3403 | 0.74944
5.3472 | 0.70403
5.3542 | 0.73782
5.3611 | 0.7805
5.3681 | 0.70421
5.375 | 0.86127
5.3819 | 0.7273
5.3889 | 0.77852
5.3958 | 0.75693
5.4028 | 0.84793
5.4097 | 0.93029
5.4167 | 0.59197
5.4236 | 0.78083
5.4306 | 0.89305
5.4375 | 0.74639
5.4444 | 0.89188
5.4514 | 0.702
5.4583 | 0.82633
5.4653 | 0.81778
5.4722 | 0.73805
5.4792 | 0.66305
5.4861 | 0.7487
5.4931 | 0.87745
5.5 | 0.7245
5.5069 | 0.8914
5.5139 | 0.61209
5.5208 | 0.71355
5.5278 | 0.66345
5.5347 | 0.82308
5.5417 | 0.84019
5.5486 | 0.86207
5.5556 | 0.76225
5.5625 | 0.84711
5.5694 | 0.70486
5.5764 | 0.76844
5.5833 | 0.77089
5.5903 | 0.74444
5.5972 | 0.7032
5.6042 | 0.82407
5.6111 | 0.85795
5.6181 | 0.83911
5.625 | 0.83363
5.6319 | 0.70003
5.6389 | 0.65684
5.6458 | 0.81488
5.6528 | 0.97179
5.6597 | 0.61304
5.6667 | 0.79861
5.6736 | 0.80352
5.6806 | 0.82272
5.6875 | 0.70168
5.6944 | 0.75808
5.7014 | 0.72154
5.7083 | 0.94635
5.7153 | 0.94779
5.7222 | 0.81597
5.7292 | 0.84826
5.7361 | 0.70577
5.7431 | 0.84934
5.75 | 0.80928
5.7569 | 1.0209
5.7639 | 0.93002
5.7708 | 0.90969
5.7778 | 0.81269
5.7847 | 0.86101
5.7917 | 1.1797
5.7986 | 1.0241
5.8056 | 0.87802
5.8125 | 0.9194
5.8194 | 0.89942
5.8264 | 0.86437
5.8333 | 0.85786
5.8403 | 0.89995
5.8472 | 0.97456
5.8542 | 0.96991
5.8611 | 0.91874
5.8681 | 1.004
5.875 | 0.7708
5.8819 | 0.97016
5.8889 | 0.74224
5.8958 | 0.88193
5.9028 | 0.85711
5.9097 | 0.96202
5.9167 | 0.69331
5.9236 | 0.84978
5.9306 | 0.76878
5.9375 | 0.9772
5.9444 | 0.96167
5.9514 | 0.92381
5.9583 | 0.92476
5.9653 | 1.071
5.9722 | 0.94895
5.9792 | 0.96453
5.9861 | 0.89205
5.9931 | 0.97512
6 | 0.94885
6.0069 | 0.95389
6.0139 | 0.93596
6.0208 | 0.959
6.0278 | 0.97358
6.0347 | 1.1211
6.0417 | 0.93783
6.0486 | 1.094
6.0556 | 1.0278
6.0625 | 1.1493
6.0694 | 0.97783
6.0764 | 0.94005
6.0833 | 1.1448
6.0903 | 0.74478
6.0972 | 0.96867
6.1042 | 1.3061
6.1111 | 1.0402
6.1181 | 0.83216
6.125 | 1.046
6.1319 | 1.0799
6.1389 | 1.1249
6.1458 | 1.1917
6.1528 | 1.0392
6.1597 | 1.1189
6.1667 | 1.1273
6.1736 | 1.0729
6.1806 | 1.085
6.1875 | 0.99189
6.1944 | 1.0359
6.2014 | 0.98796
6.2083 | 1.1283
6.2153 | 1.0967
6.2222 | 1.0894
6.2292 | 1.2602
6.2361 | 1.13
6.2431 | 1.1164
6.25 | 1.0715
6.2569 | 0.958
6.2639 | 1.0976
6.2708 | 0.90472
6.2778 | 1.0891
6.2847 | 1.1522
6.2917 | 1.2818
6.2986 | 1.0791
6.3056 | 1.1968
6.3125 | 1.1713
6.3194 | 0.95205
6.3264 | 0.99521
6.3333 | 1.1671
6.3403 | 1.3144
6.3472 | 1.1367
6.3542 | 1.27
6.3611 | 1.1348
6.3681 | 1.1054
6.375 | 1.0877
6.3819 | 1.2003
6.3889 | 1.1629
6.3958 | 1.272
6.4028 | 1.0944
6.4097 | 1.1468
6.4167 | 1.1276
6.4236 | 1.1477
6.4306 | 1.3232
6.4375 | 1.2205
6.4444 | 1.2156
6.4514 | 1.2909
6.4583 | 1.3849
6.4653 | 1.4819
6.4722 | 1.4499
6.4792 | 1.4352
6.4861 | 1.1184
6.4931 | 1.1388
6.5 | 1.3099
6.5069 | 1.2512
6.5139 | 1.4381
6.5208 | 1.3286
6.5278 | 1.3506
6.5347 | 1.4322
6.5417 | 1.3421
6.5486 | 1.4148
6.5556 | 1.3061
6.5625 | 1.3057
6.5694 | 1.3042
6.5764 | 1.3905
6.5833 | 1.2991
6.5903 | 1.4702
6.5972 | 1.1499
6.6042 | 1.3547
6.6111 | 1.4643
6.6181 | 1.3586
6.625 | 1.3902
6.6319 | 1.4381
6.6389 | 1.4424
6.6458 | 1.3254
6.6528 | 1.4907
6.6597 | 1.6272
6.6667 | 1.5352
6.6736 | 1.3954
6.6806 | 1.478
6.6875 | 1.4214
6.6944 | 1.4911
6.7014 | 1.6783
6.7083 | 1.4379
6.7153 | 1.5895
6.7222 | 1.3996
6.7292 | 1.5373
6.7361 | 1.463
6.7431 | 1.576
6.75 | 1.598
6.7569 | 1.5804
6.7639 | 1.5296
6.7708 | 1.439
6.7778 | 1.293
6.7847 | 1.5131
6.7917 | 1.4201
6.7986 | 1.6637
6.8056 | 1.6139
6.8125 | 1.5574
6.8194 | 1.6383
6.8264 | 1.6041
6.8333 | 1.4045
6.8403 | 1.567
6.8472 | 1.5039
6.8542 | 1.5516
6.8611 | 1.4287
6.8681 | 1.6626
6.875 | 1.6427
6.8819 | 1.6658
6.8889 | 1.6267
6.8958 | 1.8232
6.9028 | 1.6405
6.9097 | 1.532
6.9167 | 1.7609
6.9236 | 1.7537
6.9306 | 1.759
6.9375 | 1.7584
6.9444 | 1.5707
6.9514 | 1.6236
6.9583 | 1.6561
6.9653 | 1.6959
6.9722 | 1.8106
6.9792 | 1.6011
6.9861 | 1.7301
6.9931 | 1.524
7 | 1.8364

## CSTR3
Unit overview
Name: | CSTR3
Sumo name: | CSTR3
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and input DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
Ntrain | Number of trains | 1
htank | Tank depth | 5 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 3 | g O2/m3 | List of Set SVs will appear here.
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XCASTO_0 | Carbon storing organisms (CASTO) initial concentration | 700 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 140 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XHAO,H_0 | Active hydrous aluminium oxide, high surface (HAO,H) initial concentration | 1e-40 | g Al/m3
XHAO,L_0 | Active hydrous aluminium oxide, low surface (HAO,L) initial concentration | 1e-40 | g Al/m3
XHAO,old_0 | Aged unused hydrous aluminium oxide (HAO,old) initial concentration | 1e-40 | g Al/m3
XHAO,H,P_0 | P-bound hydrous aluminium oxide, high surface (HAO,H,P) initial concentration | 1e-40 | g Al/m3
XHAO,L,P_0 | P-bound hydrous aluminium oxide, low surface (HAO,L,P) initial concentration | 1e-40 | g Al/m3
XHAO,H,P,old_0 | Aged P-bound hydrous aluminium oxide, high surface (HAO,H,P,old) initial concentration | 1e-40 | g Al/m3
XHAO,L,P,old_0 | Aged P-bound hydrous aluminium oxide, low surface (HAO,L,P,old) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XBSH_0 | Brushite (BSH) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
SALPHA_0 | Alpha indicator initial concentration | 0.5
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration under aerated conditions | 1.54 | %v/v
GCH4,aer | Methane gas (CH4) off-gas concentration under aerated conditions | 1e-40 | %v/v
GH2,aer | Hydrogen gas (H2) off-gas concentration under aerated conditions | 1e-40 | %v/v
GO2,aer | Oxygen gas (O2) off-gas concentration under aerated conditions | 18.84 | %v/v
GNH3,aer | Ammonia gas (NH3) off-gas concentration under aerated conditions | 1e-40 | %v/v
GN2,aer | Nitrogen gas (N2) off-gas concentration under aerated conditions | 79.62 | %v/v
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 2.3 | %v/v
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 0.04 | %v/v
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 3.16 | %v/v
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 94.5 | %v/v
Aeration gas composition
Symbol | Name | Value | Unit | Comment
GCO2,air,inp | Carbon dioxide gas (CO2) in air input | 0.04 | %v/v
GCH4,air,inp | Methane gas (CH4) in air input | 1e-40 | %v/v
GH2,air,inp | Hydrogen gas (H2) in air input | 1e-40 | %v/v
GO2,air,inp | Oxygen gas (O2) in air input | 20.95 | %v/v
GNH3,air,inp | Ammonia gas (NH3) in air input | 1e-40 | %v/v
GN2,air,inp | Nitrogen gas (N2) in air input | 79.01 | %v/v
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble,aer | Bubble Sauter mean diameter under aerated conditions | 0.003 | m
dbubble,nonaer | Bubble Sauter mean diameter under non-aerated conditions | 0.01 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the graphics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.
Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.4 | g O2/m3
Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.4 | g O2/m3
DOrand | Enabled
No interpolation | Repeated every 168 hours
Time | SO2
d | g O2/m3
0 | 0.5
0.0069444 | 0.5
0.013889 | 0.5
0.020833 | 0.5
0.027778 | 0.5
0.034722 | 0.5
0.041667 | 0.5
0.048611 | 0.5
0.055556 | 0.52759
0.0625 | 0.93222
0.069444 | 0.8046
0.076389 | 0.60292
0.083333 | 0.5
0.090278 | 0.5
0.097222 | 1.1128
0.10417 | 2.67
0.11111 | 3
0.11806 | 3
0.125 | 2.0856
0.13194 | 0.5368
0.13889 | 0.5
0.14583 | 0.5
0.15278 | 0.5
0.15972 | 0.5
0.16667 | 0.5
0.17361 | 0.5
0.18056 | 0.5
0.1875 | 0.5
0.19444 | 0.5
0.20139 | 0.5
0.20833 | 0.5
0.21528 | 0.8778
0.22222 | 1.1068
0.22917 | 1.2825
0.23611 | 1.9081
0.24306 | 2.1087
0.25 | 1.6484
0.25694 | 1.6569
0.26389 | 2.0411
0.27083 | 2.5442
0.27778 | 3
0.28472 | 3
0.29167 | 3
0.29861 | 1.878
0.30556 | 1.2641
0.3125 | 1.1749
0.31944 | 1.7604
0.32639 | 2.9874
0.33333 | 3
0.34028 | 2.9095
0.34722 | 1.5402
0.35417 | 1.055
0.36111 | 0.91612
0.36806 | 0.88469
0.375 | 0.5
0.38194 | 0.5
0.38889 | 0.5
0.39583 | 0.5637
0.40278 | 3
0.40972 | 3
0.41667 | 3
0.42361 | 3
0.43056 | 1.6075
0.4375 | 0.73133
0.44444 | 0.5
0.45139 | 0.5
0.45833 | 0.5
0.46528 | 1.1659
0.47222 | 1.6642
0.47917 | 1.9318
0.48611 | 1.2359
0.49306 | 0.5
0.5 | 0.5
0.50694 | 1.6961
0.51389 | 2.4464
0.52083 | 2.1901
0.52778 | 1.3811
0.53472 | 0.57582
0.54167 | 0.5
0.54861 | 0.50245
0.55556 | 0.61685
0.5625 | 0.5
0.56944 | 0.5385
0.57639 | 0.93404
0.58333 | 0.8518
0.59028 | 0.93147
0.59722 | 1.6528
0.60417 | 2.1825
0.61111 | 1.6811
0.61806 | 0.5
0.625 | 0.5
0.63194 | 0.5
0.63889 | 0.69962
0.64583 | 1.2682
0.65278 | 1.5434
0.65972 | 1.3117
0.66667 | 1.0703
0.67361 | 1.9742
0.68056 | 2.5298
0.6875 | 2.1397
0.69444 | 2.2243
0.70139 | 2.8318
0.70833 | 3
0.71528 | 3
0.72222 | 3
0.72917 | 2.6501
0.73611 | 2.2984
0.74306 | 1.9173
0.75 | 1.6678
0.75694 | 1.738
0.76389 | 1.4393
0.77083 | 1.4893
0.77778 | 2.1931
0.78472 | 2.8602
0.79167 | 2.9273
0.79861 | 2.6444
0.80556 | 2.1635
0.8125 | 1.3403
0.81944 | 1.0527
0.82639 | 1.7052
0.83333 | 2.1841
0.84028 | 1.4246
0.84722 | 0.5
0.85417 | 0.5
0.86111 | 0.5
0.86806 | 0.5
0.875 | 0.5
0.88194 | 0.5
0.88889 | 0.5
0.89583 | 0.5
0.90278 | 0.5
0.90972 | 0.5
0.91667 | 0.5
0.92361 | 0.5
0.93056 | 1.3054
0.9375 | 3
0.94444 | 3
0.95139 | 2.6652
0.95833 | 1.227
0.96528 | 0.5
0.97222 | 0.5
0.97917 | 0.90845
0.98611 | 1.5705
0.99306 | 2.2055
1 | 2.9931
1.0069 | 2.5097
1.0139 | 1.5887
1.0208 | 0.86842
1.0278 | 0.5
1.0347 | 0.5
1.0417 | 0.5
1.0486 | 0.5
1.0556 | 0.5
1.0625 | 0.5
1.0694 | 0.5
1.0764 | 0.5
1.0833 | 0.5
1.0903 | 0.5
1.0972 | 1.0567
1.1042 | 2.105
1.1111 | 2.2578
1.1181 | 1.7787
1.125 | 1.688
1.1319 | 2.1248
1.1389 | 2.5747
1.1458 | 2.4995
1.1528 | 1.8293
1.1597 | 0.78494
1.1667 | 0.5
1.1736 | 0.85922
1.1806 | 0.9257
1.1875 | 0.5
1.1944 | 0.5
1.2014 | 0.5
1.2083 | 0.69828
1.2153 | 2.6138
1.2222 | 3
1.2292 | 3
1.2361 | 3
1.2431 | 2.5139
1.25 | 2.2732
1.2569 | 2.4907
1.2639 | 2.7327
1.2708 | 3
1.2778 | 3
1.2847 | 3
1.2917 | 1.8734
1.2986 | 0.5
1.3056 | 0.5
1.3125 | 0.5
1.3194 | 0.5
1.3264 | 1.1009
1.3333 | 0.67837
1.3403 | 0.5
1.3472 | 0.5
1.3542 | 1.2539
1.3611 | 2.8324
1.3681 | 3
1.375 | 3
1.3819 | 3
1.3889 | 2.2012
1.3958 | 0.5
1.4028 | 0.5
1.4097 | 0.5
1.4167 | 0.5
1.4236 | 1.9133
1.4306 | 3
1.4375 | 3
1.4444 | 3
1.4514 | 3
1.4583 | 3
1.4653 | 2.8355
1.4722 | 0.56163
1.4792 | 0.5
1.4861 | 0.83053
1.4931 | 2.1041
1.5 | 2.7084
1.5069 | 3
1.5139 | 2.9505
1.5208 | 2.6232
1.5278 | 3
1.5347 | 3
1.5417 | 2.1138
1.5486 | 0.89961
1.5556 | 0.5
1.5625 | 0.5
1.5694 | 0.5
1.5764 | 1.0809
1.5833 | 2.998
1.5903 | 3
1.5972 | 3
1.6042 | 2.4401
1.6111 | 1.0619
1.6181 | 0.5
1.625 | 1.1571
1.6319 | 2.4103
1.6389 | 3
1.6458 | 3
1.6528 | 2.8282
1.6597 | 1.661
1.6667 | 1.3323
1.6736 | 1.2884
1.6806 | 0.73307
1.6875 | 1.2439
1.6944 | 2.2196
1.7014 | 2.3011
1.7083 | 2.9109
1.7153 | 3
1.7222 | 2.5686
1.7292 | 2.1762
1.7361 | 2.1823
1.7431 | 1.4032
1.75 | 0.84069
1.7569 | 0.68704
1.7639 | 0.5
1.7708 | 0.5
1.7778 | 0.5
1.7847 | 0.5
1.7917 | 0.5
1.7986 | 0.5
1.8056 | 0.94513
1.8125 | 0.76144
1.8194 | 0.5
1.8264 | 0.5
1.8333 | 0.61993
1.8403 | 2.538
1.8472 | 3
1.8542 | 3
1.8611 | 3
1.8681 | 1.3272
1.875 | 0.5
1.8819 | 0.5
1.8889 | 0.5
1.8958 | 1.4295
1.9028 | 2.0039
1.9097 | 2.8428
1.9167 | 3
1.9236 | 3
1.9306 | 3
1.9375 | 3
1.9444 | 3
1.9514 | 3
1.9583 | 3
1.9653 | 3
1.9722 | 3
1.9792 | 2.4783
1.9861 | 0.81478
1.9931 | 0.5
2 | 0.5
2.0069 | 1.7246
2.0139 | 2.7106
2.0208 | 3
2.0278 | 3
2.0347 | 1.626
2.0417 | 0.60882
2.0486 | 0.5
2.0556 | 0.5
2.0625 | 0.5
2.0694 | 0.5
2.0764 | 0.5
2.0833 | 0.5
2.0903 | 0.5
2.0972 | 0.5
2.1042 | 0.5
2.1111 | 1.8828
2.1181 | 2.0756
2.125 | 1.1002
2.1319 | 0.60494
2.1389 | 1.2752
2.1458 | 2.2136
2.1528 | 3
2.1597 | 3
2.1667 | 3
2.1736 | 2.5122
2.1806 | 1.7534
2.1875 | 1.4109
2.1944 | 2.0846
2.2014 | 3
2.2083 | 2.5407
2.2153 | 1.1197
2.2222 | 0.5
2.2292 | 0.78423
2.2361 | 1.7186
2.2431 | 1.7609
2.25 | 0.52563
2.2569 | 0.5
2.2639 | 0.5
2.2708 | 0.5
2.2778 | 0.5
2.2847 | 0.5
2.2917 | 0.5
2.2986 | 0.5
2.3056 | 0.5
2.3125 | 0.5
2.3194 | 0.64768
2.3264 | 1.2131
2.3333 | 1.2445
2.3403 | 0.88684
2.3472 | 0.5
2.3542 | 0.5
2.3611 | 0.5
2.3681 | 0.5
2.375 | 0.5
2.3819 | 0.5
2.3889 | 1.019
2.3958 | 2.0927
2.4028 | 2.5498
2.4097 | 2.3839
2.4167 | 2.0303
2.4236 | 1.6376
2.4306 | 1.6006
2.4375 | 2.4028
2.4444 | 3
2.4514 | 3
2.4583 | 3
2.4653 | 2.9804
2.4722 | 2.072
2.4792 | 1.2777
2.4861 | 0.61864
2.4931 | 0.78976
2.5 | 0.80539
2.5069 | 0.5
2.5139 | 1.0783
2.5208 | 1.4694
2.5278 | 0.86975
2.5347 | 0.66708
2.5417 | 1.0599
2.5486 | 1.6819
2.5556 | 2.0057
2.5625 | 1.9115
2.5694 | 1.9394
2.5764 | 2.5049
2.5833 | 2.8983
2.5903 | 2.4384
2.5972 | 1.0733
2.6042 | 0.5
2.6111 | 0.5
2.6181 | 0.5
2.625 | 1.9511
2.6319 | 2.0601
2.6389 | 1.352
2.6458 | 0.91651
2.6528 | 0.5601
2.6597 | 0.63022
2.6667 | 0.87378
2.6736 | 0.5
2.6806 | 0.5
2.6875 | 0.5
2.6944 | 0.77253
2.7014 | 1.1109
2.7083 | 1.8877
2.7153 | 1.8679
2.7222 | 0.70513
2.7292 | 0.5
2.7361 | 0.5
2.7431 | 0.5
2.75 | 0.5
2.7569 | 0.5
2.7639 | 0.5
2.7708 | 0.5
2.7778 | 0.5
2.7847 | 1.1403
2.7917 | 1.2416
2.7986 | 1.0896
2.8056 | 1.3213
2.8125 | 2.0151
2.8194 | 3
2.8264 | 3
2.8333 | 3
2.8403 | 1.1858
2.8472 | 0.5
2.8542 | 0.5
2.8611 | 0.5
2.8681 | 0.81432
2.875 | 1.1651
2.8819 | 1.2456
2.8889 | 1.841
2.8958 | 2.5795
2.9028 | 3
2.9097 | 3
2.9167 | 3
2.9236 | 3
2.9306 | 3
2.9375 | 2.7093
2.9444 | 1.9463
2.9514 | 1.6705
2.9583 | 1.331
2.9653 | 1.9038
2.9722 | 2.971
2.9792 | 2.851
2.9861 | 2.4244
2.9931 | 2.7559
3 | 2.6092
3.0069 | 2.6031
3.0139 | 3
3.0208 | 3
3.0278 | 3
3.0347 | 2.1877
3.0417 | 1.1134
3.0486 | 0.50383
3.0556 | 0.70164
3.0625 | 1.7574
3.0694 | 2.4965
3.0764 | 1.9854
3.0833 | 1.2871
3.0903 | 0.98191
3.0972 | 0.81011
3.1042 | 1.0024
3.1111 | 0.94219
3.1181 | 0.5
3.125 | 0.5
3.1319 | 0.50528
3.1389 | 2.0493
3.1458 | 3
3.1528 | 3
3.1597 | 1.9542
3.1667 | 0.51642
3.1736 | 0.5
3.1806 | 1.372
3.1875 | 2.6449
3.1944 | 3
3.2014 | 3
3.2083 | 2.9741
3.2153 | 2.661
3.2222 | 3
3.2292 | 2.7622
3.2361 | 1.817
3.2431 | 0.69686
3.25 | 0.5
3.2569 | 0.5
3.2639 | 0.5
3.2708 | 1.9708
3.2778 | 2.7593
3.2847 | 3
3.2917 | 3
3.2986 | 3
3.3056 | 2.6325
3.3125 | 2.9576
3.3194 | 3
3.3264 | 3
3.3333 | 3
3.3403 | 2.7385
3.3472 | 1.4738
3.3542 | 1.4116
3.3611 | 1.5366
3.3681 | 1.881
3.375 | 2.4165
3.3819 | 2.8022
3.3889 | 2.8076
3.3958 | 2.525
3.4028 | 2.3575
3.4097 | 2.2202
3.4167 | 2.2801
3.4236 | 2.2137
3.4306 | 1.6374
3.4375 | 0.68344
3.4444 | 0.5
3.4514 | 0.50139
3.4583 | 0.86692
3.4653 | 0.55003
3.4722 | 0.5
3.4792 | 0.5
3.4861 | 1.1958
3.4931 | 3
3.5 | 3
3.5069 | 3
3.5139 | 3
3.5208 | 1.839
3.5278 | 1.4239
3.5347 | 1.7481
3.5417 | 2.1037
3.5486 | 2.217
3.5556 | 1.7154
3.5625 | 1.4987
3.5694 | 1.5584
3.5764 | 1.0769
3.5833 | 0.5
3.5903 | 0.5
3.5972 | 0.55307
3.6042 | 0.5539
3.6111 | 0.59484
3.6181 | 0.62837
3.625 | 0.59576
3.6319 | 0.90277
3.6389 | 1.6244
3.6458 | 1.5375
3.6528 | 0.5
3.6597 | 0.5
3.6667 | 0.5
3.6736 | 0.5
3.6806 | 1.4872
3.6875 | 3
3.6944 | 3
3.7014 | 2.1867
3.7083 | 0.5
3.7153 | 0.5
3.7222 | 0.5
3.7292 | 0.5
3.7361 | 1.2528
3.7431 | 1.0591
3.75 | 0.67975
3.7569 | 0.5
3.7639 | 0.83203
3.7708 | 2.5847
3.7778 | 3
3.7847 | 3
3.7917 | 2.3283
3.7986 | 0.92005
3.8056 | 0.5
3.8125 | 0.5
3.8194 | 0.5
3.8264 | 0.5
3.8333 | 0.5
3.8403 | 0.5
3.8472 | 0.5
3.8542 | 1.0067
3.8611 | 2.2497
3.8681 | 2.3449
3.875 | 2.1989
3.8819 | 2.1094
3.8889 | 1.4545
3.8958 | 0.71562
3.9028 | 0.5
3.9097 | 0.5
3.9167 | 0.5
3.9236 | 0.5
3.9306 | 0.5
3.9375 | 0.5
3.9444 | 0.69282
3.9514 | 1.5305
3.9583 | 1.6557
3.9653 | 1.3933
3.9722 | 1.4335
3.9792 | 1.4732
3.9861 | 1.8608
3.9931 | 2.8438
4 | 3
4.0069 | 2.3932
4.0139 | 1.1593
4.0208 | 0.5
4.0278 | 0.5
4.0347 | 0.5
4.0417 | 0.5
4.0486 | 1.9226
4.0556 | 3
4.0625 | 3
4.0694 | 3
4.0764 | 3
4.0833 | 1.3262
4.0903 | 1.0264
4.0972 | 2.3032
4.1042 | 3
4.1111 | 3
4.1181 | 3
4.125 | 3
4.1319 | 2.0472
4.1389 | 1.743
4.1458 | 1.595
4.1528 | 0.70556
4.1597 | 0.5
4.1667 | 0.5
4.1736 | 0.5
4.1806 | 0.5
4.1875 | 0.62836
4.1944 | 0.5
4.2014 | 0.5
4.2083 | 0.89292
4.2153 | 1.7098
4.2222 | 2.5863
4.2292 | 3
4.2361 | 3
4.2431 | 3
4.25 | 3
4.2569 | 1.2993
4.2639 | 0.5
4.2708 | 0.5
4.2778 | 0.5
4.2847 | 1.178
4.2917 | 1.6182
4.2986 | 1.8566
4.3056 | 1.7431
4.3125 | 1.2448
4.3194 | 0.5
4.3264 | 0.5
4.3333 | 0.5
4.3403 | 0.59007
4.3472 | 1.4918
4.3542 | 1.9185
4.3611 | 2.1578
4.3681 | 1.5236
4.375 | 0.98834
4.3819 | 0.5
4.3889 | 0.5
4.3958 | 0.5
4.4028 | 0.5
4.4097 | 1.6702
4.4167 | 2.4862
4.4236 | 2.6193
4.4306 | 1.4613
4.4375 | 0.5
4.4444 | 0.5
4.4514 | 1.3962
4.4583 | 2.7515
4.4653 | 2.9541
4.4722 | 1.7393
4.4792 | 0.5
4.4861 | 0.5
4.4931 | 0.77472
4.5 | 1.1974
4.5069 | 1.5342
4.5139 | 1.5095
4.5208 | 1.3285
4.5278 | 1.5158
4.5347 | 1.4906
4.5417 | 0.95998
4.5486 | 0.71834
4.5556 | 0.5
4.5625 | 0.5
4.5694 | 0.5
4.5764 | 0.5
4.5833 | 0.65544
4.5903 | 1.1739
4.5972 | 1.2103
4.6042 | 0.82743
4.6111 | 1.0101
4.6181 | 1.2073
4.625 | 0.80507
4.6319 | 0.61414
4.6389 | 0.83226
4.6458 | 1.343
4.6528 | 2.3103
4.6597 | 3
4.6667 | 2.4891
4.6736 | 1.3584
4.6806 | 1.1343
4.6875 | 2.227
4.6944 | 3
4.7014 | 3
4.7083 | 3
4.7153 | 1.1576
4.7222 | 0.5
4.7292 | 0.74785
4.7361 | 2.4406
4.7431 | 3
4.75 | 2.8553
4.7569 | 1.2379
4.7639 | 0.5
4.7708 | 0.5
4.7778 | 0.6383
4.7847 | 2.4131
4.7917 | 3
4.7986 | 2.527
4.8056 | 1.7515
4.8125 | 0.77223
4.8194 | 0.5
4.8264 | 0.85018
4.8333 | 0.75042
4.8403 | 0.5
4.8472 | 0.5
4.8542 | 0.5
4.8611 | 0.5
4.8681 | 0.5
4.875 | 0.5
4.8819 | 0.5
4.8889 | 0.5
4.8958 | 0.5
4.9028 | 0.5
4.9097 | 0.87713
4.9167 | 1.0357
4.9236 | 2.1375
4.9306 | 3
4.9375 | 3
4.9444 | 3
4.9514 | 2.0413
4.9583 | 1.8593
4.9653 | 2.5479
4.9722 | 3
4.9792 | 3
4.9861 | 2.4314
4.9931 | 1.0284
5 | 0.5
5.0069 | 0.77777
5.0139 | 1.7179
5.0208 | 3
5.0278 | 3
5.0347 | 3
5.0417 | 2.192
5.0486 | 1.1765
5.0556 | 0.6068
5.0625 | 0.71238
5.0694 | 1.4033
5.0764 | 1.7688
5.0833 | 2.231
5.0903 | 2.7617
5.0972 | 2.4486
5.1042 | 1.2136
5.1111 | 0.5
5.1181 | 0.5
5.125 | 0.5
5.1319 | 0.5
5.1389 | 1.3869
5.1458 | 2.5857
5.1528 | 2.9653
5.1597 | 2.4494
5.1667 | 2.1036
5.1736 | 2.6384
5.1806 | 3
5.1875 | 3
5.1944 | 3
5.2014 | 2.7966
5.2083 | 2.1852
5.2153 | 2.8295
5.2222 | 2.8546
5.2292 | 2.0273
5.2361 | 2.0979
5.2431 | 2.0027
5.25 | 1.7366
5.2569 | 2.1195
5.2639 | 2.2339
5.2708 | 1.96
5.2778 | 1.3084
5.2847 | 0.5
5.2917 | 0.5
5.2986 | 0.61695
5.3056 | 0.80096
5.3125 | 1.6202
5.3194 | 2.2537
5.3264 | 2.3836
5.3333 | 2.8501
5.3403 | 2.7012
5.3472 | 1.8463
5.3542 | 1.9485
5.3611 | 3
5.3681 | 3
5.375 | 3
5.3819 | 3
5.3889 | 3
5.3958 | 3
5.4028 | 3
5.4097 | 3
5.4167 | 3
5.4236 | 3
5.4306 | 3
5.4375 | 2.8979
5.4444 | 1.7202
5.4514 | 0.5
5.4583 | 0.5
5.4653 | 0.5
5.4722 | 0.5
5.4792 | 0.5
5.4861 | 1.1976
5.4931 | 1.7291
5.5 | 1.3223
5.5069 | 0.5
5.5139 | 0.5
5.5208 | 0.5
5.5278 | 0.5
5.5347 | 0.74698
5.5417 | 1.6638
5.5486 | 1.7138
5.5556 | 1.5822
5.5625 | 1.9018
5.5694 | 1.985
5.5764 | 1.9639
5.5833 | 2.375
5.5903 | 2.6157
5.5972 | 2.04
5.6042 | 1.3096
5.6111 | 0.5
5.6181 | 0.5
5.625 | 0.5
5.6319 | 0.5
5.6389 | 1.6162
5.6458 | 1.6719
5.6528 | 0.53565
5.6597 | 0.5
5.6667 | 0.90353
5.6736 | 2.3887
5.6806 | 2.9371
5.6875 | 2.1976
5.6944 | 0.5
5.7014 | 0.5
5.7083 | 0.5
5.7153 | 0.5
5.7222 | 1.3089
5.7292 | 2.6788
5.7361 | 3
5.7431 | 3
5.75 | 1.9018
5.7569 | 0.5
5.7639 | 0.5
5.7708 | 0.72072
5.7778 | 2.0962
5.7847 | 3
5.7917 | 2.8306
5.7986 | 1.8322
5.8056 | 1.6117
5.8125 | 1.6819
5.8194 | 0.97434
5.8264 | 0.5
5.8333 | 0.5
5.8403 | 0.5
5.8472 | 0.80307
5.8542 | 1.1431
5.8611 | 0.69783
5.8681 | 0.5
5.875 | 0.5
5.8819 | 0.5
5.8889 | 0.5
5.8958 | 0.5
5.9028 | 2.0593
5.9097 | 3
5.9167 | 3
5.9236 | 2.0927
5.9306 | 0.5
5.9375 | 0.5
5.9444 | 0.5
5.9514 | 0.62521
5.9583 | 0.95043
5.9653 | 0.80183
5.9722 | 0.67112
5.9792 | 0.63525
5.9861 | 1.2969
5.9931 | 2.1986
6 | 2.5651
6.0069 | 2.7802
6.0139 | 2.1818
6.0208 | 0.61059
6.0278 | 0.5
6.0347 | 0.5
6.0417 | 0.5
6.0486 | 0.5
6.0556 | 0.5
6.0625 | 0.5
6.0694 | 0.5
6.0764 | 0.5
6.0833 | 0.5
6.0903 | 0.5
6.0972 | 1.0129
6.1042 | 1.3662
6.1111 | 0.91433
6.1181 | 0.5
6.125 | 0.5
6.1319 | 0.5
6.1389 | 0.5
6.1458 | 0.5
6.1528 | 0.5
6.1597 | 0.5
6.1667 | 0.5
6.1736 | 0.5
6.1806 | 0.5
6.1875 | 0.5
6.1944 | 0.5
6.2014 | 0.5
6.2083 | 0.5
6.2153 | 0.5
6.2222 | 0.5
6.2292 | 0.90959
6.2361 | 1.6021
6.2431 | 2.3202
6.25 | 2.2351
6.2569 | 2.0954
6.2639 | 2.4325
6.2708 | 2.597
6.2778 | 2.3154
6.2847 | 1.9521
6.2917 | 1.5288
6.2986 | 0.86916
6.3056 | 0.64711
6.3125 | 1.236
6.3194 | 2.086
6.3264 | 3
6.3333 | 3
6.3403 | 3
6.3472 | 3
6.3542 | 2.3204
6.3611 | 0.5
6.3681 | 0.5
6.375 | 0.5
6.3819 | 1.2433
6.3889 | 2.6224
6.3958 | 2.9079
6.4028 | 1.8824
6.4097 | 1.3219
6.4167 | 0.92178
6.4236 | 0.5
6.4306 | 0.5
6.4375 | 0.68363
6.4444 | 0.84715
6.4514 | 1.4334
6.4583 | 2.1533
6.4653 | 1.9317
6.4722 | 1.3504
6.4792 | 0.51151
6.4861 | 0.5
6.4931 | 0.5
6.5 | 1.0787
6.5069 | 2.5825
6.5139 | 3
6.5208 | 2.7104
6.5278 | 2.0608
6.5347 | 1.95
6.5417 | 1.9188
6.5486 | 1.4427
6.5556 | 0.5
6.5625 | 0.5
6.5694 | 0.82248
6.5764 | 2.164
6.5833 | 3
6.5903 | 3
6.5972 | 2.2503
6.6042 | 2.5578
6.6111 | 3
6.6181 | 3
6.625 | 2.9772
6.6319 | 2.7188
6.6389 | 2.2406
6.6458 | 1.6229
6.6528 | 1.1976
6.6597 | 0.5
6.6667 | 0.5
6.6736 | 0.5
6.6806 | 0.5
6.6875 | 0.5
6.6944 | 1.4957
6.7014 | 3
6.7083 | 3
6.7153 | 3
6.7222 | 2.4759
6.7292 | 1.4183
6.7361 | 1.0437
6.7431 | 2.2592
6.75 | 3
6.7569 | 3
6.7639 | 2.5013
6.7708 | 1.3444
6.7778 | 0.5
6.7847 | 0.5
6.7917 | 0.5
6.7986 | 0.5
6.8056 | 0.5
6.8125 | 0.5
6.8194 | 0.5
6.8264 | 0.5
6.8333 | 0.5
6.8403 | 0.5
6.8472 | 0.5
6.8542 | 0.5
6.8611 | 1.1025
6.8681 | 2.0935
6.875 | 2.5651
6.8819 | 3
6.8889 | 3
6.8958 | 2.5467
6.9028 | 1.7254
6.9097 | 1.555
6.9167 | 1.941
6.9236 | 2.9515
6.9306 | 3
6.9375 | 3
6.9444 | 2.6337
6.9514 | 1.5888
6.9583 | 1.953
6.9653 | 3
6.9722 | 3
6.9792 | 2.9655
6.9861 | 1.9591
6.9931 | 0.5
7 | 0.5
DOsmallrange | Disabled
No interpolation
Time | SO2
d | g O2/m3
0 | 0.98758
0.0069444 | 0.74585
0.013889 | 1.0277
0.020833 | 0.9804
0.027778 | 0.98038
0.034722 | 0.96943
0.041667 | 0.88711
0.048611 | 1.0194
0.055556 | 0.93929
0.0625 | 0.91716
0.069444 | 1.0536
0.076389 | 1.0109
0.083333 | 0.88779
0.090278 | 1.0046
0.097222 | 0.87614
0.10417 | 1.0638
0.11111 | 1.1145
0.11806 | 0.99841
0.125 | 1.0661
0.13194 | 0.74545
0.13889 | 1.0012
0.14583 | 0.89837
0.15278 | 0.98844
0.15972 | 0.92237
0.16667 | 0.88602
0.17361 | 1.032
0.18056 | 0.94285
0.1875 | 0.837
0.19444 | 0.90636
0.20139 | 0.97214
0.20833 | 0.99154
0.21528 | 0.91163
0.22222 | 1.0512
0.22917 | 0.99274
0.23611 | 1.0019
0.24306 | 0.96066
0.25 | 1.2026
0.25694 | 1.013
0.26389 | 0.93976
0.27083 | 1.0933
0.27778 | 1.1445
0.28472 | 1
0.29167 | 1.2847
0.29861 | 0.96141
0.30556 | 1.015
0.3125 | 0.96828
0.31944 | 0.98372
0.32639 | 1.0819
0.33333 | 1.0082
0.34028 | 1.1956
0.34722 | 1.0195
0.35417 | 0.76673
0.36111 | 0.94056
0.36806 | 1.1096
0.375 | 0.98045
0.38194 | 0.80845
0.38889 | 0.92814
0.39583 | 0.7871
0.40278 | 1.2699
0.40972 | 1.1451
0.41667 | 1.1153
0.42361 | 1.0393
0.43056 | 1.0799
0.4375 | 0.80854
0.44444 | 0.94145
0.45139 | 1.0059
0.45833 | 0.94082
0.46528 | 0.75644
0.47222 | 1.188
0.47917 | 0.98159
0.48611 | 1.002
0.49306 | 0.94242
0.5 | 0.91991
0.50694 | 0.96936
0.51389 | 1.1764
0.52083 | 1.0136
0.52778 | 0.95216
0.53472 | 0.87401
0.54167 | 1.0611
0.54861 | 0.94002
0.55556 | 1.0399
0.5625 | 0.87597
0.56944 | 1.05
0.57639 | 0.95336
0.58333 | 0.99848
0.59028 | 0.96196
0.59722 | 0.95861
0.60417 | 1.0181
0.61111 | 1.1198
0.61806 | 0.89668
0.625 | 0.89041
0.63194 | 0.83441
0.63889 | 1.138
0.64583 | 1.0683
0.65278 | 0.9396
0.65972 | 0.9596
0.66667 | 1.049
0.67361 | 1.0686
0.68056 | 0.89476
0.6875 | 1.2274
0.69444 | 1.0931
0.70139 | 0.89007
0.70833 | 1.1034
0.71528 | 1.0854
0.72222 | 1.0467
0.72917 | 1.0114
0.73611 | 0.94221
0.74306 | 1.1823
0.75 | 1.0397
0.75694 | 0.94982
0.76389 | 0.88219
0.77083 | 1.2199
0.77778 | 0.94947
0.78472 | 1.0208
0.79167 | 1.0119
0.79861 | 1.1298
0.80556 | 1.0616
0.8125 | 0.85309
0.81944 | 1.0293
0.82639 | 0.99736
0.83333 | 1.013
0.84028 | 1.0461
0.84722 | 0.86244
0.85417 | 0.90757
0.86111 | 0.81898
0.86806 | 0.95358
0.875 | 0.96129
0.88194 | 0.90227
0.88889 | 0.80358
0.89583 | 0.90859
0.90278 | 0.90935
0.90972 | 0.9508
0.91667 | 0.99735
0.92361 | 1.0236
0.93056 | 1.0792
0.9375 | 1.0862
0.94444 | 0.86025
0.95139 | 0.93289
0.95833 | 1.0263
0.96528 | 0.92939
0.97222 | 1.1682
0.97917 | 0.88908
0.98611 | 1.0291
0.99306 | 1.0539
1 | 1.0699
1.0069 | 0.79373
1.0139 | 0.91251
1.0208 | 1.0167
1.0278 | 0.96631
1.0347 | 0.74596
1.0417 | 0.9615
1.0486 | 1.0461
1.0556 | 0.80193
1.0625 | 0.93595
1.0694 | 0.8819
1.0764 | 0.99144
1.0833 | 1.049
1.0903 | 0.97056
1.0972 | 1.0858
1.1042 | 0.99709
1.1111 | 0.92894
1.1181 | 1.0795
1.125 | 1.1295
1.1319 | 0.98648
1.1389 | 0.85963
1.1458 | 0.97739
1.1528 | 0.97765
1.1597 | 1.0031
1.1667 | 1.0063
1.1736 | 0.81714
1.1806 | 0.93487
1.1875 | 0.99159
1.1944 | 1.014
1.2014 | 1.0733
1.2083 | 1.0186
1.2153 | 1.0013
1.2222 | 1.0994
1.2292 | 0.93685
1.2361 | 0.99307
1.2431 | 1.1213
1.25 | 1.0645
1.2569 | 0.95225
1.2639 | 1.0825
1.2708 | 0.97785
1.2778 | 1.0645
1.2847 | 0.9088
1.2917 | 0.78774
1.2986 | 1.1419
1.3056 | 0.89761
1.3125 | 1.074
1.3194 | 0.97792
1.3264 | 0.96046
1.3333 | 0.96049
1.3403 | 1.152
1.3472 | 1.0293
1.3542 | 1.1196
1.3611 | 1.0946
1.3681 | 1.0003
1.375 | 1.0036
1.3819 | 0.88171
1.3889 | 0.85987
1.3958 | 0.97908
1.4028 | 1.0204
1.4097 | 1.107
1.4167 | 1.0751
1.4236 | 1.1264
1.4306 | 1.1622
1.4375 | 1.1123
1.4444 | 1.1058
1.4514 | 0.89671
1.4583 | 0.97973
1.4653 | 0.95633
1.4722 | 1.0772
1.4792 | 1.1375
1.4861 | 0.96513
1.4931 | 1.0115
1.5 | 1.042
1.5069 | 1.0826
1.5139 | 0.8797
1.5208 | 1.0637
1.5278 | 1.1241
1.5347 | 0.89582
1.5417 | 0.8141
1.5486 | 0.95997
1.5556 | 0.88587
1.5625 | 1.2125
1.5694 | 1.0423
1.5764 | 1.1414
1.5833 | 1.0296
1.5903 | 0.95393
1.5972 | 0.9068
1.6042 | 1.0225
1.6111 | 0.98384
1.6181 | 1.0779
1.625 | 1.0107
1.6319 | 0.99513
1.6389 | 0.96644
1.6458 | 0.81121
1.6528 | 1.0542
1.6597 | 0.98879
1.6667 | 0.93941
1.6736 | 1.0698
1.6806 | 1.1729
1.6875 | 0.94668
1.6944 | 1.1181
1.7014 | 1.0767
1.7083 | 0.92818
1.7153 | 1.0753
1.7222 | 0.98492
1.7292 | 0.89864
1.7361 | 1.0097
1.7431 | 0.91868
1.75 | 0.80002
1.7569 | 0.90839
1.7639 | 0.9391
1.7708 | 0.98018
1.7778 | 1.0554
1.7847 | 0.80819
1.7917 | 1.0552
1.7986 | 0.89589
1.8056 | 0.91828
1.8125 | 1.0586
1.8194 | 1.0487
1.8264 | 1.0806
1.8333 | 1.048
1.8403 | 0.98912
1.8472 | 0.92424
1.8542 | 1.0233
1.8611 | 0.934
1.8681 | 1.0065
1.875 | 1.0166
1.8819 | 1.0871
1.8889 | 0.94024
1.8958 | 1.1455
1.9028 | 1.1294
1.9097 | 1.1975
1.9167 | 1.062
1.9236 | 1.0642
1.9306 | 1.0412
1.9375 | 1.1043
1.9444 | 1.1301
1.9514 | 1.0115
1.9583 | 0.91306
1.9653 | 1.0108
1.9722 | 0.98235
1.9792 | 0.90472
1.9861 | 1.0919
1.9931 | 1.0698
2 | 1.0105
2.0069 | 0.99261
2.0139 | 0.99785
2.0208 | 0.90933
2.0278 | 0.97866
2.0347 | 0.98894
2.0417 | 0.9181
2.0486 | 1.217
2.0556 | 0.90327
2.0625 | 0.95246
2.0694 | 0.87918
2.0764 | 0.89855
2.0833 | 1.1234
2.0903 | 0.97801
2.0972 | 1.0571
2.1042 | 0.93471
2.1111 | 0.88698
2.1181 | 1.1058
2.125 | 1.0393
2.1319 | 0.90185
2.1389 | 1.0996
2.1458 | 1.0851
2.1528 | 1.0007
2.1597 | 0.96385
2.1667 | 0.90586
2.1736 | 1.2152
2.1806 | 1.0403
2.1875 | 1.0131
2.1944 | 0.8678
2.2014 | 0.96277
2.2083 | 1.1385
2.2153 | 1.0141
2.2222 | 0.93257
2.2292 | 0.80217
2.2361 | 0.93557
2.2431 | 0.90043
2.25 | 0.89798
2.2569 | 0.95801
2.2639 | 0.93437
2.2708 | 0.80865
2.2778 | 0.83248
2.2847 | 0.9986
2.2917 | 0.91793
2.2986 | 1.1501
2.3056 | 0.92597
2.3125 | 0.98131
2.3194 | 0.97839
2.3264 | 0.92427
2.3333 | 0.96459
2.3403 | 0.85617
2.3472 | 0.90331
2.3542 | 0.8279
2.3611 | 1.069
2.3681 | 1.0605
2.375 | 0.92603
2.3819 | 1.1778
2.3889 | 0.92993
2.3958 | 1.034
2.4028 | 1.0057
2.4097 | 0.93651
2.4167 | 1.0654
2.4236 | 1.1656
2.4306 | 0.82621
2.4375 | 0.99747
2.4444 | 1.22
2.4514 | 0.91454
2.4583 | 0.9094
2.4653 | 1.0015
2.4722 | 1.0664
2.4792 | 0.94955
2.4861 | 0.96441
2.4931 | 1.0281
2.5 | 0.74205
2.5069 | 1.1197
2.5139 | 0.96133
2.5208 | 1.0275
2.5278 | 1.0313
2.5347 | 0.8424
2.5417 | 1.1571
2.5486 | 1.0702
2.5556 | 0.95516
2.5625 | 0.93925
2.5694 | 0.91228
2.5764 | 0.90242
2.5833 | 1.0717
2.5903 | 1.0852
2.5972 | 0.92705
2.6042 | 0.9608
2.6111 | 0.94747
2.6181 | 1.1839
2.625 | 0.88141
2.6319 | 0.84109
2.6389 | 1.0417
2.6458 | 0.91425
2.6528 | 0.92547
2.6597 | 1.1288
2.6667 | 0.92855
2.6736 | 1.0402
2.6806 | 1.0329
2.6875 | 0.9134
2.6944 | 0.95756
2.7014 | 0.95679
2.7083 | 1.1008
2.7153 | 0.78009
2.7222 | 0.95672
2.7292 | 0.95167
2.7361 | 0.90147
2.7431 | 1.0143
2.75 | 1.0116
2.7569 | 0.99849
2.7639 | 0.91965
2.7708 | 1.0058
2.7778 | 1.0583
2.7847 | 1.0534
2.7917 | 1.0079
2.7986 | 1.0928
2.8056 | 0.63573
2.8125 | 0.86602
2.8194 | 1.0796
2.8264 | 0.97785
2.8333 | 0.97358
2.8403 | 1.0164
2.8472 | 0.9651
2.8542 | 1.0541
2.8611 | 0.96018
2.8681 | 1.0393
2.875 | 1.0244
2.8819 | 1.0827
2.8889 | 0.98996
2.8958 | 1.1052
2.9028 | 1.0194
2.9097 | 0.83006
2.9167 | 1.0882
2.9236 | 1.159
2.9306 | 0.89614
2.9375 | 1.3625
2.9444 | 1.0187
2.9514 | 1.0837
2.9583 | 0.82979
2.9653 | 1.0892
2.9722 | 1.0266
2.9792 | 1.008
2.9861 | 1.3064
2.9931 | 1.027
3 | 1.0111
3.0069 | 0.75363
3.0139 | 1.0084
3.0208 | 1.0649
3.0278 | 0.95851
3.0347 | 1.0288
3.0417 | 1.03
3.0486 | 0.94381
3.0556 | 1.0128
3.0625 | 0.99382
3.0694 | 0.96797
3.0764 | 1.0268
3.0833 | 0.78701
3.0903 | 0.9443
3.0972 | 0.98565
3.1042 | 1.15
3.1111 | 1.0251
3.1181 | 1.0545
3.125 | 0.93738
3.1319 | 0.96453
3.1389 | 0.95905
3.1458 | 1.1519
3.1528 | 0.9828
3.1597 | 1.1043
3.1667 | 1.0582
3.1736 | 1.1058
3.1806 | 0.77914
3.1875 | 1.2427
3.1944 | 1.1174
3.2014 | 0.96343
3.2083 | 0.84305
3.2153 | 0.95174
3.2222 | 1.013
3.2292 | 1.0058
3.2361 | 0.98474
3.2431 | 1.1797
3.25 | 1.0152
3.2569 | 1.0522
3.2639 | 1.0202
3.2708 | 0.83275
3.2778 | 0.99117
3.2847 | 1.0621
3.2917 | 1.0534
3.2986 | 0.9097
3.3056 | 1.0135
3.3125 | 1.015
3.3194 | 1.0292
3.3264 | 1.0092
3.3333 | 1.0413
3.3403 | 1.0512
3.3472 | 1.159
3.3542 | 0.96189
3.3611 | 1.0925
3.3681 | 0.9821
3.375 | 1.0564
3.3819 | 0.96686
3.3889 | 0.86092
3.3958 | 1.0713
3.4028 | 0.97679
3.4097 | 1.0132
3.4167 | 0.9096
3.4236 | 0.925
3.4306 | 0.89268
3.4375 | 1.18
3.4444 | 1.1559
3.4514 | 1.2033
3.4583 | 0.97668
3.4653 | 1.1013
3.4722 | 0.96764
3.4792 | 1.1003
3.4861 | 0.98283
3.4931 | 1.0978
3.5 | 0.9024
3.5069 | 1.086
3.5139 | 0.86163
3.5208 | 1.1346
3.5278 | 0.97017
3.5347 | 0.79205
3.5417 | 0.89043
3.5486 | 1.023
3.5556 | 0.98581
3.5625 | 0.93995
3.5694 | 0.93968
3.5764 | 1.0322
3.5833 | 1.0503
3.5903 | 0.92064
3.5972 | 1.1046
3.6042 | 0.88107
3.6111 | 0.93608
3.6181 | 0.78268
3.625 | 1.0027
3.6319 | 1.0805
3.6389 | 1.058
3.6458 | 0.99142
3.6528 | 0.90377
3.6597 | 0.99807
3.6667 | 0.9563
3.6736 | 0.97837
3.6806 | 0.96533
3.6875 | 1.2313
3.6944 | 0.96919
3.7014 | 0.91915
3.7083 | 1.0834
3.7153 | 1.1029
3.7222 | 1.0816
3.7292 | 1.0177
3.7361 | 0.94784
3.7431 | 0.96327
3.75 | 0.98985
3.7569 | 0.92205
3.7639 | 0.9599
3.7708 | 0.82988
3.7778 | 0.88324
3.7847 | 1.1102
3.7917 | 0.90458
3.7986 | 0.98606
3.8056 | 1.0288
3.8125 | 1.0995
3.8194 | 0.94963
3.8264 | 0.92591
3.8333 | 1.1494
3.8403 | 0.98179
3.8472 | 0.92556
3.8542 | 0.93632
3.8611 | 0.97382
3.8681 | 0.88422
3.875 | 0.97284
3.8819 | 0.94937
3.8889 | 1.0598
3.8958 | 0.98794
3.9028 | 1.068
3.9097 | 0.94473
3.9167 | 0.96323
3.9236 | 1.1443
3.9306 | 1.0775
3.9375 | 1.0345
3.9444 | 1.0354
3.9514 | 0.86087
3.9583 | 0.79592
3.9653 | 1.0701
3.9722 | 0.87422
3.9792 | 0.87672
3.9861 | 1.0997
3.9931 | 1.1614
4 | 1.1562
4.0069 | 1.0184
4.0139 | 0.98791
4.0208 | 0.98828
4.0278 | 0.94543
4.0347 | 1.126
4.0417 | 1.0488
4.0486 | 1.1914
4.0556 | 0.88138
4.0625 | 1.0432
4.0694 | 1.0672
4.0764 | 0.96347
4.0833 | 1.0443
4.0903 | 0.90097
4.0972 | 0.95947
4.1042 | 0.92675
4.1111 | 1.0851
4.1181 | 0.94447
4.125 | 0.98148
4.1319 | 0.9709
4.1389 | 0.86569
4.1458 | 1.1178
4.1528 | 1.1051
4.1597 | 0.95787
4.1667 | 1.1745
4.1736 | 1.0789
4.1806 | 1.1732
4.1875 | 0.99099
4.1944 | 0.81053
4.2014 | 0.8474
4.2083 | 1.0406
4.2153 | 1.0496
4.2222 | 0.96032
4.2292 | 1.0123
4.2361 | 1.0147
4.2431 | 1.126
4.25 | 0.76464
4.2569 | 0.82701
4.2639 | 0.9823
4.2708 | 0.88879
4.2778 | 1.1324
4.2847 | 0.94563
4.2917 | 1.0127
4.2986 | 0.98451
4.3056 | 1.0617
4.3125 | 0.92901
4.3194 | 0.94797
4.3264 | 0.99389
4.3333 | 0.9231
4.3403 | 1.0552
4.3472 | 1.0103
4.3542 | 1.0618
4.3611 | 0.98676
4.3681 | 0.89628
4.375 | 0.89606
4.3819 | 0.90447
4.3889 | 1.1037
4.3958 | 1.1137
4.4028 | 0.93937
4.4097 | 0.98066
4.4167 | 0.91078
4.4236 | 1.0391
4.4306 | 1.0187
4.4375 | 0.94242
4.4444 | 0.99462
4.4514 | 1.0718
4.4583 | 0.97665
4.4653 | 1.0107
4.4722 | 0.90505
4.4792 | 1.1039
4.4861 | 0.95435
4.4931 | 0.99803
4.5 | 0.99101
4.5069 | 1.2118
4.5139 | 0.91639
4.5208 | 0.98889
4.5278 | 1.0683
4.5347 | 0.90835
4.5417 | 0.99239
4.5486 | 1.0085
4.5556 | 0.97286
4.5625 | 0.96312
4.5694 | 0.88974
4.5764 | 1.2802
4.5833 | 1.004
4.5903 | 1.0205
4.5972 | 1.0092
4.6042 | 0.93402
4.6111 | 0.98927
4.6181 | 1.0409
4.625 | 1.1134
4.6319 | 1.1607
4.6389 | 0.87091
4.6458 | 0.95642
4.6528 | 0.89526
4.6597 | 1.1033
4.6667 | 1.0386
4.6736 | 1.0958
4.6806 | 0.97294
4.6875 | 0.8961
4.6944 | 0.96522
4.7014 | 0.92232
4.7083 | 1.0058
4.7153 | 1.101
4.7222 | 1.1263
4.7292 | 0.97116
4.7361 | 0.90056
4.7431 | 1.0245
4.75 | 0.98295
4.7569 | 0.91642
4.7639 | 1.048
4.7708 | 0.81316
4.7778 | 0.98259
4.7847 | 0.85593
4.7917 | 0.99291
4.7986 | 0.86319
4.8056 | 0.85375
4.8125 | 0.99788
4.8194 | 1.1288
4.8264 | 0.72086
4.8333 | 0.86888
4.8403 | 1.1475
4.8472 | 1.0414
4.8542 | 1.0495
4.8611 | 1.212
4.8681 | 0.95035
4.875 | 1.0457
4.8819 | 0.96365
4.8889 | 1.0955
4.8958 | 1.04
4.9028 | 0.94832
4.9097 | 1.1054
4.9167 | 0.90986
4.9236 | 1.0349
4.9306 | 0.99717
4.9375 | 1.0325
4.9444 | 1.0304
4.9514 | 1.0499
4.9583 | 1.0016
4.9653 | 0.84054
4.9722 | 1.0789
4.9792 | 0.7687
4.9861 | 1.1121
4.9931 | 0.89184
5 | 1.1342
5.0069 | 1.0552
5.0139 | 0.90247
5.0208 | 1.1384
5.0278 | 0.93434
5.0347 | 0.97866
5.0417 | 0.95051
5.0486 | 0.97806
5.0556 | 0.7944
5.0625 | 1.1491
5.0694 | 0.97661
5.0764 | 1.0899
5.0833 | 0.90003
5.0903 | 0.99265
5.0972 | 1.1288
5.1042 | 1.1879
5.1111 | 0.98968
5.1181 | 0.99403
5.125 | 1.1092
5.1319 | 0.97339
5.1389 | 0.9792
5.1458 | 1.1435
5.1528 | 0.99951
5.1597 | 0.91862
5.1667 | 1.1651
5.1736 | 1.0004
5.1806 | 0.97205
5.1875 | 1.1075
5.1944 | 0.91299
5.2014 | 1.0815
5.2083 | 0.91526
5.2153 | 0.84724
5.2222 | 1.1275
5.2292 | 0.99709
5.2361 | 0.97197
5.2431 | 1.1567
5.25 | 0.95917
5.2569 | 1.1038
5.2639 | 0.98805
5.2708 | 0.96123
5.2778 | 1.0424
5.2847 | 1.1311
5.2917 | 1.1945
5.2986 | 1.0414
5.3056 | 0.93729
5.3125 | 1.1661
5.3194 | 1.1553
5.3264 | 1.0092
5.3333 | 1.0564
5.3403 | 1.1433
5.3472 | 1.1273
5.3542 | 1.0491
5.3611 | 0.94957
5.3681 | 1.0346
5.375 | 0.90226
5.3819 | 0.94771
5.3889 | 0.93786
5.3958 | 0.9832
5.4028 | 0.95561
5.4097 | 1.0838
5.4167 | 0.977
5.4236 | 1.0016
5.4306 | 0.90443
5.4375 | 0.91301
5.4444 | 1.0501
5.4514 | 0.91678
5.4583 | 0.99347
5.4653 | 1.0281
5.4722 | 1.0373
5.4792 | 0.97485
5.4861 | 0.93662
5.4931 | 1.1249
5.5 | 1.0547
5.5069 | 0.93007
5.5139 | 1.1218
5.5208 | 1.0143
5.5278 | 0.9871
5.5347 | 0.9154
5.5417 | 0.89095
5.5486 | 0.91117
5.5556 | 1.0464
5.5625 | 1.0677
5.5694 | 0.9863
5.5764 | 0.67426
5.5833 | 0.88903
5.5903 | 1.1433
5.5972 | 1.1088
5.6042 | 0.98343
5.6111 | 0.83133
5.6181 | 0.98469
5.625 | 0.98427
5.6319 | 0.81226
5.6389 | 1.048
5.6458 | 1.0272
5.6528 | 1.0456
5.6597 | 1.1462
5.6667 | 1.2213
5.6736 | 0.89169
5.6806 | 0.8959
5.6875 | 0.95377
5.6944 | 1.0934
5.7014 | 1.1106
5.7083 | 0.9188
5.7153 | 1.0642
5.7222 | 1.0268
5.7292 | 0.90505
5.7361 | 1.0645
5.7431 | 0.86373
5.75 | 0.92955
5.7569 | 0.85159
5.7639 | 1.0101
5.7708 | 0.97795
5.7778 | 1.0155
5.7847 | 0.75588
5.7917 | 0.97346
5.7986 | 0.84385
5.8056 | 0.95116
5.8125 | 0.88794
5.8194 | 1.0147
5.8264 | 1.0658
5.8333 | 1.1477
5.8403 | 0.99858
5.8472 | 0.94345
5.8542 | 0.87735
5.8611 | 0.94703
5.8681 | 0.9911
5.875 | 1.0216
5.8819 | 0.93721
5.8889 | 1.0189
5.8958 | 0.98804
5.9028 | 0.97239
5.9097 | 1.1526
5.9167 | 1.0351
5.9236 | 0.8455
5.9306 | 1.0902
5.9375 | 0.90333
5.9444 | 0.95306
5.9514 | 0.93746
5.9583 | 0.85539
5.9653 | 0.94699
5.9722 | 0.96161
5.9792 | 0.99128
5.9861 | 0.93983
5.9931 | 0.89295
6 | 1.0202
6.0069 | 1.0543
6.0139 | 1.0701
6.0208 | 0.68702
6.0278 | 0.88057
6.0347 | 1.0401
6.0417 | 0.84189
6.0486 | 0.90243
6.0556 | 0.99194
6.0625 | 0.91277
6.0694 | 1.0458
6.0764 | 0.85319
6.0833 | 0.93897
6.0903 | 0.91006
6.0972 | 0.9838
6.1042 | 0.89692
6.1111 | 0.90887
6.1181 | 1.1242
6.125 | 0.86703
6.1319 | 1.07
6.1389 | 0.97691
6.1458 | 1.1117
6.1528 | 0.98772
6.1597 | 0.9119
6.1667 | 1.1382
6.1736 | 1.1487
6.1806 | 0.86444
6.1875 | 1.0112
6.1944 | 0.92908
6.2014 | 1.138
6.2083 | 0.92876
6.2153 | 1.0267
6.2222 | 1.1862
6.2292 | 1.0379
6.2361 | 1.0981
6.2431 | 1.041
6.25 | 0.95954
6.2569 | 0.80353
6.2639 | 0.86519
6.2708 | 1.1045
6.2778 | 1.0708
6.2847 | 0.90921
6.2917 | 1.2465
6.2986 | 1.0028
6.3056 | 0.9516
6.3125 | 0.99253
6.3194 | 0.9773
6.3264 | 0.93988
6.3333 | 1.0464
6.3403 | 1.0086
6.3472 | 0.93277
6.3542 | 1.1071
6.3611 | 1.0093
6.3681 | 0.95759
6.375 | 0.85534
6.3819 | 0.99974
6.3889 | 0.89887
6.3958 | 1.1932
6.4028 | 0.9985
6.4097 | 1.1466
6.4167 | 0.93546
6.4236 | 0.98629
6.4306 | 1.0051
6.4375 | 1.2016
6.4444 | 0.90046
6.4514 | 0.95341
6.4583 | 0.86668
6.4653 | 1.1423
6.4722 | 1.1472
6.4792 | 0.9543
6.4861 | 1.0631
6.4931 | 1.0032
6.5 | 1.0327
6.5069 | 1.1215
6.5139 | 1.0976
6.5208 | 0.85235
6.5278 | 1.0531
6.5347 | 1.0565
6.5417 | 0.97045
6.5486 | 0.90662
6.5556 | 0.91536
6.5625 | 1.0273
6.5694 | 0.94391
6.5764 | 0.9768
6.5833 | 0.9668
6.5903 | 1.0673
6.5972 | 1.1963
6.6042 | 1.1271
6.6111 | 0.99134
6.6181 | 1.0756
6.625 | 1.0342
6.6319 | 0.92013
6.6389 | 1.0625
6.6458 | 1.06
6.6528 | 0.95934
6.6597 | 0.99909
6.6667 | 0.88139
6.6736 | 1.0026
6.6806 | 1.0139
6.6875 | 0.91929
6.6944 | 0.86647
6.7014 | 0.91941
6.7083 | 0.99604
6.7153 | 0.88875
6.7222 | 0.86418
6.7292 | 0.8273
6.7361 | 0.96958
6.7431 | 1.0149
6.75 | 0.95968
6.7569 | 1.0392
6.7639 | 1.2786
6.7708 | 0.94598
6.7778 | 1.316
6.7847 | 1.0214
6.7917 | 0.9324
6.7986 | 1.0282
6.8056 | 1.0851
6.8125 | 1.1238
6.8194 | 1.0228
6.8264 | 1.0225
6.8333 | 0.87176
6.8403 | 1.1276
6.8472 | 1.1524
6.8542 | 1.0268
6.8611 | 1.0136
6.8681 | 0.90247
6.875 | 0.94344
6.8819 | 0.94692
6.8889 | 0.86068
6.8958 | 0.95317
6.9028 | 0.80977
6.9097 | 0.97574
6.9167 | 0.78865
6.9236 | 1.0145
6.9306 | 0.83601
6.9375 | 0.80359
6.9444 | 1.0325
6.9514 | 0.9605
6.9583 | 1.0383
6.9653 | 1.0085
6.9722 | 1.0488
6.9792 | 0.95453
6.9861 | 1.0464
6.9931 | 0.99863
7 | 1.0314
DOsine | Disabled
No interpolation | Repeated every 168 hours
Time | SO2
d | g O2/m3
0 | 1.7376
0.0069444 | 1.5083
0.013889 | 1.8027
0.020833 | 1.7678
0.027778 | 1.7802
0.034722 | 1.7817
0.041667 | 1.7118
0.048611 | 1.8566
0.055556 | 1.7889
0.0625 | 1.7791
0.069444 | 1.9279
0.076389 | 1.8977
0.083333 | 1.7868
0.090278 | 1.916
0.097222 | 1.7998
0.10417 | 1.9997
0.11111 | 2.0627
0.11806 | 1.9588
0.125 | 2.0386
0.13194 | 1.7301
0.13889 | 1.998
0.14583 | 1.9072
0.15278 | 2.0093
0.15972 | 1.9552
0.16667 | 1.9308
0.17361 | 2.0886
0.18056 | 2.0113
0.1875 | 1.9173
0.19444 | 1.9984
0.20139 | 2.0758
0.20833 | 2.1069
0.21528 | 2.0386
0.22222 | 2.1896
0.22917 | 2.1426
0.23611 | 2.1632
0.24306 | 2.1333
0.25 | 2.3865
0.25694 | 2.2081
0.26389 | 2.146
0.27083 | 2.3106
0.27778 | 2.3728
0.28472 | 2.2392
0.29167 | 2.5347
0.29861 | 2.2222
0.30556 | 2.2865
0.3125 | 2.2503
0.31944 | 2.2763
0.32639 | 2.3849
0.33333 | 2.3215
0.34028 | 2.5192
0.34722 | 2.3532
0.35417 | 2.1106
0.36111 | 2.2944
0.36806 | 2.4733
0.375 | 2.3539
0.38194 | 2.1916
0.38889 | 2.3209
0.39583 | 2.1894
0.40278 | 2.6816
0.40972 | 2.5661
0.41667 | 2.5454
0.42361 | 2.4785
0.43056 | 2.5282
0.4375 | 2.2656
0.44444 | 2.4073
0.45139 | 2.4804
0.45833 | 2.4239
0.46528 | 2.2479
0.47222 | 2.6877
0.47917 | 2.4896
0.48611 | 2.518
0.49306 | 2.4664
0.5 | 2.4517
0.50694 | 2.5089
0.51389 | 2.7235
0.52083 | 2.5681
0.52778 | 2.5141
0.53472 | 2.4432
0.54167 | 2.6373
0.54861 | 2.5232
0.55556 | 2.6299
0.5625 | 2.4727
0.56944 | 2.6533
0.57639 | 2.5631
0.58333 | 2.6145
0.59028 | 2.5841
0.59722 | 2.5868
0.60417 | 2.6522
0.61111 | 2.7596
0.61806 | 2.5422
0.625 | 2.5414
0.63194 | 2.4907
0.63889 | 2.7995
0.64583 | 2.7348
0.65278 | 2.6111
0.65972 | 2.6358
0.66667 | 2.7299
0.67361 | 2.754
0.68056 | 2.5845
0.6875 | 2.9212
0.69444 | 2.791
0.70139 | 2.5919
0.70833 | 2.809
0.71528 | 2.7946
0.72222 | 2.7594
0.72917 | 2.7273
0.73611 | 2.6613
0.74306 | 2.9043
0.75 | 2.7646
0.75694 | 2.6775
0.76389 | 2.6124
0.77083 | 2.9525
0.77778 | 2.6843
0.78472 | 2.7577
0.79167 | 2.7507
0.79861 | 2.8704
0.80556 | 2.8039
0.8125 | 2.5968
0.81944 | 2.7743
0.82639 | 2.7435
0.83333 | 2.7602
0.84028 | 2.7941
0.84722 | 2.6112
0.85417 | 2.6569
0.86111 | 2.5687
0.86806 | 2.7035
0.875 | 2.7113
0.88194 | 2.6522
0.88889 | 2.5533
0.89583 | 2.6579
0.90278 | 2.6581
0.90972 | 2.6989
0.91667 | 2.7446
0.92361 | 2.7698
0.93056 | 2.8242
0.9375 | 2.8299
0.94444 | 2.6025
0.95139 | 2.6735
0.95833 | 2.7652
0.96528 | 2.6663
0.97222 | 2.903
0.97917 | 2.6216
0.98611 | 2.7592
0.99306 | 2.7815
1 | 2.7948
1.0069 | 2.5158
1.0139 | 2.6316
1.0208 | 2.7326
1.0278 | 2.6789
1.0347 | 2.4551
1.0417 | 2.6671
1.0486 | 2.748
1.0556 | 2.4999
1.0625 | 2.6298
1.0694 | 2.5716
1.0764 | 2.6768
1.0833 | 2.7299
1.0903 | 2.6468
1.0972 | 2.7573
1.1042 | 2.6637
1.1111 | 2.5904
1.1181 | 2.7358
1.125 | 2.7805
1.1319 | 2.632
1.1389 | 2.4995
1.1458 | 2.6115
1.1528 | 2.6059
1.1597 | 2.6253
1.1667 | 2.6224
1.1736 | 2.4269
1.1806 | 2.5382
1.1875 | 2.5883
1.1944 | 2.604
1.2014 | 2.6565
1.2083 | 2.5948
1.2153 | 2.5704
1.2222 | 2.6614
1.2292 | 2.4914
1.2361 | 2.5402
1.2431 | 2.6609
1.25 | 2.5963
1.2569 | 2.4763
1.2639 | 2.5985
1.2708 | 2.4858
1.2778 | 2.5643
1.2847 | 2.4003
1.2917 | 2.2708
1.2986 | 2.6164
1.3056 | 2.3635
1.3125 | 2.5311
1.3194 | 2.4262
1.3264 | 2.3997
1.3333 | 2.3907
1.3403 | 2.5729
1.3472 | 2.441
1.3542 | 2.5218
1.3611 | 2.4874
1.3681 | 2.3835
1.375 | 2.3771
1.3819 | 2.2454
1.3889 | 2.2137
1.3958 | 2.3229
1.4028 | 2.3542
1.4097 | 2.4306
1.4167 | 2.3884
1.4236 | 2.4294
1.4306 | 2.4547
1.4375 | 2.3944
1.4444 | 2.3772
1.4514 | 2.1575
1.4583 | 2.2297
1.4653 | 2.1955
1.4722 | 2.3054
1.4792 | 2.3548
1.4861 | 2.1713
1.4931 | 2.2066
1.5 | 2.2259
1.5069 | 2.2552
1.5139 | 2.041
1.5208 | 2.2136
1.5278 | 2.2625
1.5347 | 2.0227
1.5417 | 1.9294
1.5486 | 2.0637
1.5556 | 1.9779
1.5625 | 2.2927
1.5694 | 2.1108
1.5764 | 2.1981
1.5833 | 2.0744
1.5903 | 1.9868
1.5972 | 1.9276
1.6042 | 2.0314
1.6111 | 1.9806
1.6181 | 2.0626
1.625 | 1.9832
1.6319 | 1.9555
1.6389 | 1.9146
1.6458 | 1.7471
1.6528 | 1.9778
1.6597 | 1.9001
1.6667 | 1.8385
1.6736 | 1.9565
1.6806 | 2.0472
1.6875 | 1.8086
1.6944 | 1.9677
1.7014 | 1.9138
1.7083 | 1.7529
1.7153 | 1.8876
1.7222 | 1.7848
1.7292 | 1.686
1.7361 | 1.7847
1.7431 | 1.6811
1.75 | 1.55
1.7569 | 1.6459
1.7639 | 1.6642
1.7708 | 1.6928
1.7778 | 1.7556
1.7847 | 1.4959
1.7917 | 1.7305
1.7986 | 1.5587
1.8056 | 1.5687
1.8125 | 1.6967
1.8194 | 1.6744
1.8264 | 1.6939
1.8333 | 1.649
1.8403 | 1.5778
1.8472 | 1.5006
1.8542 | 1.5874
1.8611 | 1.4858
1.8681 | 1.5462
1.875 | 1.544
1.8819 | 1.6025
1.8889 | 1.4435
1.8958 | 1.6367
1.9028 | 1.6086
1.9097 | 1.6647
1.9167 | 1.5173
1.9236 | 1.5076
1.9306 | 1.4727
1.9375 | 1.524
1.9444 | 1.538
1.9514 | 1.4078
1.9583 | 1.2977
1.9653 | 1.3839
1.9722 | 1.3439
1.9792 | 1.2548
1.9861 | 1.4306
1.9931 | 1.3971
2 | 1.3267
2.0069 | 1.2975
2.0139 | 1.2916
2.0208 | 1.1921
2.0278 | 1.2504
2.0347 | 1.2498
2.0417 | 1.1681
2.0486 | 1.4562
2.0556 | 1.1318
2.0625 | 1.1704
2.0694 | 1.0866
2.0764 | 1.0956
2.0833 | 1.3101
2.0903 | 1.1544
2.0972 | 1.2233
2.1042 | 1.0909
2.1111 | 1.0332
2.1181 | 1.2421
2.125 | 1.1658
2.1319 | 1.0187
2.1389 | 1.2068
2.1458 | 1.1828
2.1528 | 1.089
2.1597 | 1.0429
2.1667 | 0.97569
2.1736 | 1.276
2.1806 | 1.0921
2.1875 | 1.056
2.1944 | 0.90194
2.2014 | 0.98825
2.2083 | 1.1554
2.2153 | 1.0226
2.2222 | 0.93279
2.2292 | 0.7942
2.2361 | 0.91953
2.2431 | 0.87643
2.25 | 0.86615
2.2569 | 0.91847
2.2639 | 0.88724
2.2708 | 0.75405
2.2778 | 0.77054
2.2847 | 0.92944
2.2917 | 0.84169
2.2986 | 1.0669
2.3056 | 0.83594
2.3125 | 0.88459
2.3194 | 0.8751
2.3264 | 0.81454
2.3333 | 0.84857
2.3403 | 0.73398
2.3472 | 0.77509
2.3542 | 0.69378
2.3611 | 0.92911
2.3681 | 0.91502
2.375 | 0.77506
2.3819 | 1.0215
2.3889 | 0.76842
2.3958 | 0.8674
2.4028 | 0.8342
2.4097 | 0.76026
2.4167 | 0.8845
2.4236 | 0.98023
2.4306 | 0.63652
2.4375 | 0.80359
2.4444 | 1.022
2.4514 | 0.71271
2.4583 | 0.70383
2.4653 | 0.79235
2.4722 | 0.85382
2.4792 | 0.73362
2.4861 | 0.74534
2.4931 | 0.80602
2.5 | 0.51712
2.5069 | 0.89203
2.5139 | 0.73115
2.5208 | 0.79494
2.5278 | 0.79645
2.5347 | 0.6055
2.5417 | 0.91827
2.5486 | 0.82956
2.5556 | 0.71292
2.5625 | 0.69554
2.5694 | 0.66725
2.5764 | 0.65623
2.5833 | 0.82447
2.5903 | 0.83719
2.5972 | 0.67829
2.6042 | 0.7115
2.6111 | 0.69778
2.6181 | 0.93398
2.625 | 0.63141
2.6319 | 0.59117
2.6389 | 0.79202
2.6458 | 0.66495
2.6528 | 0.67671
2.6597 | 0.88073
2.6667 | 0.68135
2.6736 | 0.79404
2.6806 | 0.78788
2.6875 | 0.66969
2.6944 | 0.71532
2.7014 | 0.71618
2.7083 | 0.86198
2.7153 | 0.5432
2.7222 | 0.72191
2.7292 | 0.7191
2.7361 | 0.67129
2.7431 | 0.78671
2.75 | 0.78666
2.7569 | 0.77641
2.7639 | 0.70057
2.7708 | 0.78987
2.7778 | 0.84572
2.7847 | 0.84421
2.7917 | 0.80234
2.7986 | 0.891
2.8056 | 0.43781
2.8125 | 0.67213
2.8194 | 0.88991
2.8264 | 0.79249
2.8333 | 0.79271
2.8403 | 0.84017
2.8472 | 0.79363
2.8542 | 0.88756
2.8611 | 0.79868
2.8681 | 0.88301
2.875 | 0.8734
2.8819 | 0.93718
2.8889 | 0.85009
2.8958 | 0.9711
2.9028 | 0.89121
2.9097 | 0.70786
2.9167 | 0.97217
2.9236 | 1.0493
2.9306 | 0.79285
2.9375 | 1.2658
2.9444 | 0.92868
2.9514 | 1.0005
2.9583 | 0.75355
2.9653 | 1.0201
2.9722 | 0.96466
2.9792 | 0.95336
2.9861 | 1.2593
2.9931 | 0.98742
3 | 0.97923
3.0069 | 0.72964
3.0139 | 0.99231
3.0208 | 1.0569
3.0278 | 0.95873
3.0347 | 1.0374
3.0417 | 1.0469
3.0486 | 0.96929
3.0556 | 1.0469
3.0625 | 1.0367
3.0694 | 1.0197
3.0764 | 1.0876
3.0833 | 0.85684
3.0903 | 1.0233
3.0972 | 1.074
3.1042 | 1.2477
3.1111 | 1.1323
3.1181 | 1.1713
3.125 | 1.0639
3.1319 | 1.1008
3.1389 | 1.1052
3.1458 | 1.3081
3.1528 | 1.1491
3.1597 | 1.2807
3.1667 | 1.2449
3.1736 | 1.3028
3.1806 | 0.98659
3.1875 | 1.4607
3.1944 | 1.3459
3.2014 | 1.2027
3.2083 | 1.0931
3.2153 | 1.2126
3.2222 | 1.2848
3.2292 | 1.2885
3.2361 | 1.2785
3.2431 | 1.4847
3.25 | 1.3314
3.2569 | 1.3796
3.2639 | 1.3589
3.2708 | 1.1829
3.2778 | 1.3527
3.2847 | 1.4352
3.2917 | 1.438
3.2986 | 1.306
3.3056 | 1.4215
3.3125 | 1.4348
3.3194 | 1.4607
3.3264 | 1.4525
3.3333 | 1.4965
3.3403 | 1.5184
3.3472 | 1.6382
3.3542 | 1.4531
3.3611 | 1.5957
3.3681 | 1.4974
3.375 | 1.5839
3.3819 | 1.5065
3.3889 | 1.4128
3.3958 | 1.6354
3.4028 | 1.5531
3.4097 | 1.6019
3.4167 | 1.5106
3.4236 | 1.5383
3.4306 | 1.5183
3.4375 | 1.8181
3.4444 | 1.8063
3.4514 | 1.8661
3.4583 | 1.652
3.4653 | 1.789
3.4722 | 1.6678
3.4792 | 1.813
3.4861 | 1.7079
3.4931 | 1.8353
3.5 | 1.6524
3.5069 | 1.8484
3.5139 | 1.6366
3.5208 | 1.922
3.5278 | 1.77
3.5347 | 1.6043
3.5417 | 1.7152
3.5486 | 1.8602
3.5556 | 1.8354
3.5625 | 1.8019
3.5694 | 1.814
3.5764 | 1.9189
3.5833 | 1.9494
3.5903 | 1.832
3.5972 | 2.0283
3.6042 | 1.817
3.6111 | 1.8842
3.6181 | 1.743
3.625 | 1.9752
3.6319 | 2.0652
3.6389 | 2.0547
3.6458 | 2.0002
3.6528 | 1.9246
3.6597 | 2.0309
3.6667 | 2.0011
3.6736 | 2.035
3.6806 | 2.0338
3.6875 | 2.3116
3.6944 | 2.0612
3.7014 | 2.0229
3.7083 | 2.1988
3.7153 | 2.2298
3.7222 | 2.2201
3.7292 | 2.1676
3.7361 | 2.1091
3.7431 | 2.1359
3.75 | 2.1737
3.7569 | 2.1171
3.7639 | 2.1661
3.7708 | 2.0471
3.7778 | 2.1115
3.7847 | 2.3493
3.7917 | 2.1546
3.7986 | 2.2468
3.8056 | 2.3003
3.8125 | 2.3815
3.8194 | 2.2422
3.8264 | 2.2289
3.8333 | 2.4627
3.8403 | 2.3054
3.8472 | 2.2593
3.8542 | 2.2801
3.8611 | 2.3276
3.8681 | 2.2479
3.875 | 2.3463
3.8819 | 2.3326
3.8889 | 2.4526
3.8958 | 2.3902
3.9028 | 2.4797
3.9097 | 2.3657
3.9167 | 2.3934
3.9236 | 2.5835
3.9306 | 2.5258
3.9375 | 2.4916
3.9444 | 2.5013
3.9514 | 2.3354
3.9583 | 2.279
3.9653 | 2.5616
3.9722 | 2.374
3.9792 | 2.3847
3.9861 | 2.6158
3.9931 | 2.6854
4 | 2.6881
4.0069 | 2.5579
4.0139 | 2.535
4.0208 | 2.5429
4.0278 | 2.5074
4.0347 | 2.6951
4.0417 | 2.625
4.0486 | 2.7746
4.0556 | 2.4714
4.0625 | 2.6399
4.0694 | 2.6705
4.0764 | 2.5732
4.0833 | 2.6604
4.0903 | 2.5232
4.0972 | 2.5877
4.1042 | 2.5609
4.1111 | 2.7249
4.1181 | 2.59
4.125 | 2.6324
4.1319 | 2.6272
4.1389 | 2.5272
4.1458 | 2.7844
4.1528 | 2.7766
4.1597 | 2.6341
4.1667 | 2.8554
4.1736 | 2.7643
4.1806 | 2.8629
4.1875 | 2.6849
4.1944 | 2.5085
4.2014 | 2.5492
4.2083 | 2.7462
4.2153 | 2.7588
4.2222 | 2.6729
4.2292 | 2.7282
4.2361 | 2.7337
4.2431 | 2.8481
4.25 | 2.4896
4.2569 | 2.5546
4.2639 | 2.7125
4.2708 | 2.6214
4.2778 | 2.8672
4.2847 | 2.6825
4.2917 | 2.7515
4.2986 | 2.7251
4.3056 | 2.804
4.3125 | 2.6727
4.3194 | 2.693
4.3264 | 2.7401
4.3333 | 2.6703
4.3403 | 2.8032
4.3472 | 2.7591
4.3542 | 2.8111
4.3611 | 2.7364
4.3681 | 2.6462
4.375 | 2.6461
4.3819 | 2.6544
4.3889 | 2.8534
4.3958 | 2.863
4.4028 | 2.6881
4.4097 | 2.7287
4.4167 | 2.658
4.4236 | 2.7853
4.4306 | 2.7637
4.4375 | 2.6861
4.4444 | 2.7369
4.4514 | 2.8124
4.4583 | 2.7155
4.4653 | 2.7476
4.4722 | 2.6399
4.4792 | 2.8365
4.4861 | 2.6845
4.4931 | 2.7257
4.5 | 2.7159
4.5069 | 2.9339
4.5139 | 2.6355
4.5208 | 2.7048
4.5278 | 2.7809
4.5347 | 2.6175
4.5417 | 2.698
4.5486 | 2.7103
4.5556 | 2.6708
4.5625 | 2.657
4.5694 | 2.5794
4.5764 | 2.9656
4.5833 | 2.6849
4.5903 | 2.6968
4.5972 | 2.6807
4.6042 | 2.6006
4.6111 | 2.6508
4.6181 | 2.6972
4.625 | 2.7644
4.6319 | 2.8062
4.6389 | 2.5108
4.6458 | 2.5905
4.6528 | 2.5235
4.6597 | 2.7255
4.6667 | 2.6547
4.6736 | 2.7055
4.6806 | 2.5762
4.6875 | 2.4928
4.6944 | 2.5552
4.7014 | 2.5055
4.7083 | 2.582
4.7153 | 2.6701
4.7222 | 2.6882
4.7292 | 2.5258
4.7361 | 2.4477
4.7431 | 2.564
4.75 | 2.5148
4.7569 | 2.4404
4.7639 | 2.564
4.7708 | 2.3211
4.7778 | 2.4824
4.7847 | 2.3474
4.7917 | 2.476
4.7986 | 2.3377
4.8056 | 2.3196
4.8125 | 2.455
4.8194 | 2.577
4.8264 | 2.1601
4.8333 | 2.2991
4.8403 | 2.5685
4.8472 | 2.4531
4.8542 | 2.4518
4.8611 | 2.6048
4.8681 | 2.3335
4.875 | 2.4192
4.8819 | 2.3273
4.8889 | 2.4493
4.8958 | 2.3838
4.9028 | 2.2821
4.9097 | 2.429
4.9167 | 2.2232
4.9236 | 2.3378
4.9306 | 2.2897
4.9375 | 2.3145
4.9444 | 2.3018
4.9514 | 2.3107
4.9583 | 2.2516
4.9653 | 2.0797
4.9722 | 2.3072
4.9792 | 1.986
4.9861 | 2.3183
4.9931 | 2.0869
5 | 2.3181
5.0069 | 2.2278
5.0139 | 2.0638
5.0208 | 2.2882
5.0278 | 2.0728
5.0347 | 2.1056
5.0417 | 2.0659
5.0486 | 2.0818
5.0556 | 1.8864
5.0625 | 2.2294
5.0694 | 2.0451
5.0764 | 2.1466
5.0833 | 1.9448
5.0903 | 2.0255
5.0972 | 2.1496
5.1042 | 2.1967
5.1111 | 1.9864
5.1181 | 1.9787
5.125 | 2.0817
5.1319 | 1.9337
5.1389 | 1.9273
5.1458 | 2.0794
5.1528 | 1.9232
5.1597 | 1.83
5.1667 | 2.0642
5.1736 | 1.8871
5.1806 | 1.8464
5.1875 | 1.9694
5.1944 | 1.7626
5.2014 | 1.9186
5.2083 | 1.74
5.2153 | 1.6595
5.2222 | 1.9273
5.2292 | 1.7845
5.2361 | 1.7469
5.2431 | 1.9192
5.25 | 1.7092
5.2569 | 1.8413
5.2639 | 1.7131
5.2708 | 1.6738
5.2778 | 1.7426
5.2847 | 1.8188
5.2917 | 1.8698
5.2986 | 1.7043
5.3056 | 1.5877
5.3125 | 1.8042
5.3194 | 1.781
5.3264 | 1.6225
5.3333 | 1.6574
5.3403 | 1.7319
5.3472 | 1.7036
5.3542 | 1.6132
5.3611 | 1.5014
5.3681 | 1.5743
5.375 | 1.4297
5.3819 | 1.4631
5.3889 | 1.4411
5.3958 | 1.4744
5.4028 | 1.4348
5.4097 | 1.5509
5.4167 | 1.4322
5.4236 | 1.445
5.4306 | 1.3359
5.4375 | 1.3327
5.4444 | 1.458
5.4514 | 1.3131
5.4583 | 1.3781
5.4653 | 1.4012
5.4722 | 1.3989
5.4792 | 1.325
5.4861 | 1.2753
5.4931 | 1.4523
5.5 | 1.3708
5.5069 | 1.235
5.5139 | 1.4156
5.5208 | 1.297
5.5278 | 1.2588
5.5347 | 1.1762
5.5417 | 1.1409
5.5486 | 1.1504
5.5556 | 1.275
5.5625 | 1.2857
5.5694 | 1.1938
5.5764 | 0.87129
5.5833 | 1.0757
5.5903 | 1.3197
5.5972 | 1.275
5.6042 | 1.1396
5.6111 | 0.97753
5.6181 | 1.121
5.625 | 1.1108
5.6319 | 0.92907
5.6389 | 1.1552
5.6458 | 1.1249
5.6528 | 1.1339
5.6597 | 1.2252
5.6667 | 1.2911
5.6736 | 0.95243
5.6806 | 0.94767
5.6875 | 0.99666
5.6944 | 1.1276
5.7014 | 1.1361
5.7083 | 0.93574
5.7153 | 1.0727
5.7222 | 1.027
5.7292 | 0.89708
5.7361 | 1.0484
5.7431 | 0.83973
5.75 | 0.89772
5.7569 | 0.81205
5.7639 | 0.96297
5.7708 | 0.92335
5.7778 | 0.95353
5.7847 | 0.68673
5.7917 | 0.89722
5.7986 | 0.76066
5.8056 | 0.86113
5.8125 | 0.79122
5.8194 | 0.91144
5.8264 | 0.95608
5.8333 | 1.0316
5.8403 | 0.87638
5.8472 | 0.81523
5.8542 | 0.74323
5.8611 | 0.80716
5.8681 | 0.84561
5.875 | 0.8706
5.8819 | 0.7809
5.8889 | 0.85735
5.8958 | 0.82147
5.9028 | 0.80091
5.9097 | 0.9764
5.9167 | 0.85427
5.9236 | 0.66015
5.9306 | 0.90055
5.9375 | 0.70945
5.9444 | 0.75513
5.9514 | 0.73564
5.9583 | 0.64981
5.9653 | 0.73782
5.9722 | 0.74899
5.9792 | 0.77535
5.9861 | 0.72076
5.9931 | 0.67088
6 | 0.7953
6.0069 | 0.82666
6.0139 | 0.83992
6.0208 | 0.45445
6.0278 | 0.64576
6.0347 | 0.80315
6.0417 | 0.60306
6.0486 | 0.66182
6.0556 | 0.7497
6.0625 | 0.66906
6.0694 | 0.80075
6.0764 | 0.60699
6.0833 | 0.69176
6.0903 | 0.662
6.0972 | 0.73504
6.1042 | 0.64762
6.1111 | 0.65918
6.1181 | 0.87426
6.125 | 0.61703
6.1319 | 0.82009
6.1389 | 0.72722
6.1458 | 0.86236
6.1528 | 0.73897
6.1597 | 0.66384
6.1667 | 0.89103
6.1736 | 0.90251
6.1806 | 0.61941
6.1875 | 0.76751
6.1944 | 0.68684
6.2014 | 0.89741
6.2083 | 0.68993
6.2153 | 0.7898
6.2222 | 0.95144
6.2292 | 0.80534
6.2361 | 0.86795
6.2431 | 0.81336
6.25 | 0.73461
6.2569 | 0.58145
6.2639 | 0.64611
6.2708 | 0.88856
6.2778 | 0.85818
6.2847 | 0.70004
6.2917 | 1.0409
6.2986 | 0.80093
6.3056 | 0.75367
6.3125 | 0.79865
6.3194 | 0.78761
6.3264 | 0.75452
6.3333 | 0.86556
6.3403 | 0.83238
6.3472 | 0.7613
6.3542 | 0.94055
6.3611 | 0.84784
6.3681 | 0.80128
6.375 | 0.70438
6.3819 | 0.85425
6.3889 | 0.759
6.3958 | 1.0591
6.4028 | 0.87027
6.4097 | 1.0244
6.4167 | 0.81943
6.4236 | 0.87657
6.4306 | 0.90179
6.4375 | 1.1048
6.4444 | 0.81044
6.4514 | 0.87022
6.4583 | 0.79045
6.4653 | 1.0731
6.4722 | 1.0852
6.4792 | 0.89971
6.4861 | 1.016
6.4931 | 0.96369
6.5 | 1.0008
6.5069 | 1.0975
6.5139 | 1.0816
6.5208 | 0.84438
6.5278 | 1.0533
6.5347 | 1.065
6.5417 | 0.9874
6.5486 | 0.9321
6.5556 | 0.9495
6.5625 | 1.0702
6.5694 | 0.99568
6.5764 | 1.0375
6.5833 | 1.0366
6.5903 | 1.1464
6.5972 | 1.2846
6.6042 | 1.2248
6.6111 | 1.0986
6.6181 | 1.1925
6.625 | 1.1607
6.6319 | 1.0564
6.6389 | 1.2087
6.6458 | 1.2162
6.6528 | 1.1256
6.6597 | 1.1755
6.6667 | 1.0681
6.6736 | 1.1997
6.6806 | 1.2214
6.6875 | 1.1373
6.6944 | 1.095
6.7014 | 1.1587
6.7083 | 1.246
6.7153 | 1.1496
6.7222 | 1.1359
6.7292 | 1.11
6.7361 | 1.2634
6.7431 | 1.3199
6.75 | 1.2758
6.7569 | 1.3666
6.7639 | 1.6173
6.7708 | 1.2961
6.7778 | 1.6776
6.7847 | 1.3945
6.7917 | 1.3171
6.7986 | 1.4245
6.8056 | 1.493
6.8125 | 1.5435
6.8194 | 1.4543
6.8264 | 1.4659
6.8333 | 1.327
6.8403 | 1.5948
6.8472 | 1.6316
6.8542 | 1.518
6.8611 | 1.5168
6.8681 | 1.4178
6.875 | 1.4709
6.8819 | 1.4866
6.8889 | 1.4125
6.8958 | 1.5173
6.9028 | 1.3861
6.9097 | 1.5644
6.9167 | 1.3896
6.9236 | 1.6278
6.9306 | 1.4617
6.9375 | 1.4416
6.9444 | 1.6829
6.9514 | 1.6233
6.9583 | 1.7135
6.9653 | 1.6962
6.9722 | 1.7489
6.9792 | 1.6671
6.9861 | 1.7715
6.9931 | 1.7362
7 | 1.7814

## CSTR4
Unit overview
Name: | CSTR4
Sumo name: | CSTR4
Category: | Bioreactors
Unit: | CSTR
Type: | CSTR with diffused aeration and input DO
Settings
Reactor settings
Symbol | Name | Value | Unit | Comment
L.Vtrain | Volume per train | 2000 | m3
Ntrain | Number of trains | 1
htank | Tank depth | 5 | m
Aeration settings
Symbol | Name | Value | Unit | Comment
SO2 | Dissolved oxygen (O2) setpoint | 3 | g O2/m3 | List of Set SVs will appear here.
hsea | Elevation above sea level | 200 | m
hdiff,floor | Diffuser height from floor | 0.2 | m
ddiff | Diffuser floor density (diffuser area/tank area) | 0.1 | m2/m2
Adiff | Area per diffuser | 0.0373 | m2
Initial concentrations
Symbol | Name | Value | Unit | Comment
SVFA_0 | Volatile fatty acids (VFA) initial concentration | 0.01 | g COD/m3
SB_0 | Readily biodegradable substrate (non-VFA) initial concentration | 1 | g COD/m3
SMEOL_0 | Methanol (MEOL) initial concentration | 1e-40 | g COD/m3
CB_0 | Colloidal biodegradable substrate initial concentration | 0.01 | g COD/m3
XB_0 | Slowly biodegradable substrate initial concentration | 14 | g COD/m3
SU_0 | Soluble unbiodegradable organics initial concentration | 7 | g COD/m3
CU_0 | Colloidal unbiodegradable organics initial concentration | 0.01 | g COD/m3
XU_0 | Particulate unbiodegradable organics initial concentration | 1000 | g COD/m3
XPHA_0 | Stored polyhydroxyalkanoates (PHA) initial concentration | 222 | g COD/m3
XGLY_0 | Stored glycogen (GLY) initial concentration | 30 | g COD/m3
XE_0 | Endogenous decay products initial concentration | 300 | g COD/m3
XE,ana_0 | Anaerobic endogenous decay products initial concentration | 0.1 | g COD/m3
XOHO_0 | Ordinary heterotrophic organisms (OHO) initial concentration | 500 | g COD/m3
XCASTO_0 | Carbon storing organisms (CASTO) initial concentration | 700 | g COD/m3
XMEOLO_0 | Anoxic methanol utilizers (MEOLO) initial concentration | 1 | g COD/m3
XNITO_0 | Aerobic nitrifying organisms (NITO) initial concentration | 90 | g COD/m3
XAMETO_0 | Acidoclastic methanogens (AMETO) initial concentration | 0.3 | g COD/m3
XHMETO_0 | Hydrogenotrophic methanogens (HMETO) initial concentration | 0.2 | g COD/m3
SNHx_0 | Total ammonia (NHx) initial concentration | 1 | g N/m3
SNOx_0 | Nitrate and nitrite (NOx) initial concentration | 5 | g N/m3
SN2_0 | Dissolved nitrogen (N2) initial concentration | 18 | g N/m3
SN,B_0 | Soluble biodegradable organic N (from SB) initial concentration | 0.5 | g N/m3
XN,B_0 | Particulate biodegradable organic N (from XB) initial concentration | 1 | g N/m3
XN,U_0 | Particulate unbiodegradable organic N initial concentration | 10 | g N/m3
SPO4_0 | Orthophosphate (PO4) initial concentration | 0.5 | g P/m3
XPP_0 | Stored polyphosphate (PP) initial concentration | 140 | g P/m3
SP,B_0 | Soluble biodegradable organic P (from SB) initial concentration | 0.01 | g P/m3
XP,B_0 | Particulate biodegradable organic P (from XB) initial concentration | 0.5 | g P/m3
XP,U_0 | Particulate unbiodegradable organic P initial concentration | 2 | g P/m3
SCH4_0 | Dissolved methane (CH4) initial concentration | 0.01 | g COD/m3
SH2_0 | Dissolved hydrogen (H2) initial concentration | 0.01 | g COD/m3
SCO2_0 | Total inorganic carbon (CO2) initial concentration | 74 | g TIC/m3
XINORG_0 | Inorganics in influent and biomass initial concentration | 460 | g TSS/m3
SCAT_0 | Other strong cations (as Na+) initial concentration | 35 | g Na/m3
SAN_0 | Other strong anions (as Cl-) initial concentration | 150 | g Cl/m3
SCa_0 | Calcium initial concentration | 150 | g Ca/m3
SMg_0 | Magnesium initial concentration | 15 | g Mg/m3
SK_0 | Potassium initial concentration | 15 | g K/m3
SFe2_0 | Ferrous ion (Fe2) initial concentration | 1e-40 | g Fe/m3
XHFO,H_0 | Active hydrous ferric oxide, high surface (HFO,H) initial concentration | 1e-40 | g Fe/m3
XHFO,L_0 | Active hydrous ferric oxide, low surface (HFO,L) initial concentration | 1e-40 | g Fe/m3
XHFO,old_0 | Aged unused hydrous ferric oxide (HFO,old) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P_0 | P-bound hydrous ferric oxide, high surface (HFO,H,P) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P_0 | P-bound hydrous ferric oxide, low surface (HFO,L,P) initial concentration | 1e-40 | g Fe/m3
XHFO,H,P,old_0 | Aged used hydrous ferric oxide, high surface (HFO,H,P,old) initial concentration | 1e-40 | g Fe/m3
XHFO,L,P,old_0 | Aged used hydrous ferric oxide, low surface (HFO,L,P,old) initial concentration | 1e-40 | g Fe/m3
XHAO,H_0 | Active hydrous aluminium oxide, high surface (HAO,H) initial concentration | 1e-40 | g Al/m3
XHAO,L_0 | Active hydrous aluminium oxide, low surface (HAO,L) initial concentration | 1e-40 | g Al/m3
XHAO,old_0 | Aged unused hydrous aluminium oxide (HAO,old) initial concentration | 1e-40 | g Al/m3
XHAO,H,P_0 | P-bound hydrous aluminium oxide, high surface (HAO,H,P) initial concentration | 1e-40 | g Al/m3
XHAO,L,P_0 | P-bound hydrous aluminium oxide, low surface (HAO,L,P) initial concentration | 1e-40 | g Al/m3
XHAO,H,P,old_0 | Aged P-bound hydrous aluminium oxide, high surface (HAO,H,P,old) initial concentration | 1e-40 | g Al/m3
XHAO,L,P,old_0 | Aged P-bound hydrous aluminium oxide, low surface (HAO,L,P,old) initial concentration | 1e-40 | g Al/m3
XCaCO3_0 | Calcium carbonate (CaCO3) initial concentration | 1e-40 | g TSS/m3
XACP_0 | Amorphous calcium phosphate (ACP) initial concentration | 1e-40 | g TSS/m3
XBSH_0 | Brushite (BSH) initial concentration | 1e-40 | g TSS/m3
XSTR_0 | Struvite (STR) initial concentration | 1e-40 | g TSS/m3
XVivi_0 | Vivianite (Vivi) initial concentration | 1e-40 | g TSS/m3
H_0 | Enthalpy initial concentration | 83626 | kJ.m-3
SALPHA_0 | Alpha indicator initial concentration | 0.5
Off-gas concentrations
Symbol | Name | Value | Unit | Comment
GCO2,aer | Carbon dioxide gas (CO2) off-gas concentration under aerated conditions | 1.54 | %v/v
GCH4,aer | Methane gas (CH4) off-gas concentration under aerated conditions | 1e-40 | %v/v
GH2,aer | Hydrogen gas (H2) off-gas concentration under aerated conditions | 1e-40 | %v/v
GO2,aer | Oxygen gas (O2) off-gas concentration under aerated conditions | 18.84 | %v/v
GNH3,aer | Ammonia gas (NH3) off-gas concentration under aerated conditions | 1e-40 | %v/v
GN2,aer | Nitrogen gas (N2) off-gas concentration under aerated conditions | 79.62 | %v/v
GCO2,nonaer | Carbon dioxide gas (CO2) off-gas concentration under non-aerated conditions | 2.3 | %v/v
GCH4,nonaer | Methane gas (CH4) off-gas concentration under non-aerated conditions | 0.04 | %v/v
GH2,nonaer | Hydrogen gas (H2) off-gas concentration under non-aerated conditions | 3.16 | %v/v
GO2,nonaer | Oxygen gas (O2) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GNH3,nonaer | Ammonia gas (NH3) off-gas concentration under non-aerated conditions | 1e-40 | %v/v
GN2,nonaer | Nitrogen gas (N2) off-gas concentration under non-aerated conditions | 94.5 | %v/v
Aeration gas composition
Symbol | Name | Value | Unit | Comment
GCO2,air,inp | Carbon dioxide gas (CO2) in air input | 0.04 | %v/v
GCH4,air,inp | Methane gas (CH4) in air input | 1e-40 | %v/v
GH2,air,inp | Hydrogen gas (H2) in air input | 1e-40 | %v/v
GO2,air,inp | Oxygen gas (O2) in air input | 20.95 | %v/v
GNH3,air,inp | Ammonia gas (NH3) in air input | 1e-40 | %v/v
GN2,air,inp | Nitrogen gas (N2) in air input | 79.01 | %v/v
Advanced aeration settings
Symbol | Name | Value | Unit | Comment
fcover | Covered fraction of reactor surface | 0 | %
fwave | Waviness factor | 1.9
Tair | Field air temperature | 20 | °C
β | Beta correction factor | 0.95
Ffouling | Diffuser fouling factor | 0.8
fd,sat,eff | Effective saturation depth fraction | 0.5
Lair | Temperature lapse rate for air pressure calculations | 0.0065 | K/m
dbubble,aer | Bubble Sauter mean diameter under aerated conditions | 0.003 | m
dbubble,nonaer | Bubble Sauter mean diameter under non-aerated conditions | 0.01 | m
εgas,aer | Gas hold up under aerated conditions | 0.01 | m3 gas.m-3
εgas,nonaer | Gas hold up under non-aerated conditions | 0.001 | m3 gas.m-3
Oxygen transfer efficiency correlation parameters
Symbol | Name | Value | Unit | Comment
SSOTE0 | Intercept in SSOTE correlation | 7.77 | %/m
expSSOTE | Exponent (absolute value) in SSOTE correlation | 0.01041
SSOTEasym | Asymptote in SSOTE correlation | 5.75 | %/m
divd,diff | Divisor value in diffuser density correction term | 0.1173 | m2/m2
powd,diff | Power value in diffuser density correction term | 0.1329
coefflead,h,diff | Leading coefficient in diffuser submergence correction term | 0.011 | 1/m
powh,diff | Power value in diffuser submergence correction term | 1.6031
coefflin,h,diff | Linear coefficient in diffuser submergence correction term | -0.0229 | 1/m
Model specific parameters
Symbol | Name | Value | Unit | Comment
ηFLOC,Process,aer | Flocculation factor under aerated conditions | 0.25 |  | Only relevant for Sumo2C model
ηFLOC,Process,nonaer | Flocculation factor under non-aerated (mixed) conditions | 0.5 |  | Only relevant for Sumo2C model
Sanity check
Symbol | Name | Value | Unit | Comment
MLSScheckflag | MLSS sanity check | 10000 | g TSS/m3 | Above the value the graphics change as warning.
SO2,checkflag | Anoxic/Anaerobic tank section sign | 0.02 | g O2/m3 | Below the value the grapchics change as infromation about the condition.
Sumo1 - Key parameters
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.2 | g O2/m3
Sumo1 - Aerobic nitrifying organism kinetics (NITO)
Symbol | Name | Value | Unit | Comment
KO2,NITO,AS | Half-saturation of O2 for NITOs (AS) | 0.2 | g O2/m3
DOrand | Enabled
No interpolation | Repeated every 168 hours
Time | SO2
d | g O2/m3
0 | 1.4452
0.0069444 | 2.312
0.013889 | 2.8695
0.020833 | 3
0.027778 | 2.8021
0.034722 | 2.5238
0.041667 | 0.78561
0.048611 | 0.5
0.055556 | 0.5
0.0625 | 0.5
0.069444 | 0.5
0.076389 | 0.5
0.083333 | 1.2184
0.090278 | 1.9349
0.097222 | 1.5477
0.10417 | 0.83427
0.11111 | 0.5
0.11806 | 0.5
0.125 | 0.5
0.13194 | 0.52335
0.13889 | 0.93964
0.14583 | 0.72713
0.15278 | 0.80631
0.15972 | 1.2023
0.16667 | 1.2861
0.17361 | 0.98448
0.18056 | 0.62944
0.1875 | 0.67116
0.19444 | 1.6757
0.20139 | 3
0.20833 | 3
0.21528 | 3
0.22222 | 3
0.22917 | 2.738
0.23611 | 1.4879
0.24306 | 0.79548
0.25 | 0.57316
0.25694 | 0.7703
0.26389 | 0.77351
0.27083 | 0.5
0.27778 | 0.5
0.28472 | 0.5
0.29167 | 0.5
0.29861 | 0.71107
0.30556 | 1.7612
0.3125 | 2.3374
0.31944 | 2.0722
0.32639 | 1.1117
0.33333 | 0.5
0.34028 | 0.5
0.34722 | 0.5
0.35417 | 0.5
0.36111 | 0.5
0.36806 | 0.5
0.375 | 0.5
0.38194 | 1.3651
0.38889 | 2.7672
0.39583 | 3
0.40278 | 3
0.40972 | 2.8247
0.41667 | 2.0274
0.42361 | 1.5201
0.43056 | 1.3216
0.4375 | 1.1143
0.44444 | 0.5
0.45139 | 0.5
0.45833 | 0.5
0.46528 | 0.5
0.47222 | 1.2138
0.47917 | 2.3763
0.48611 | 2.8688
0.49306 | 2.864
0.5 | 3
0.50694 | 2.1872
0.51389 | 0.5
0.52083 | 0.5
0.52778 | 0.5
0.53472 | 0.5
0.54167 | 0.5
0.54861 | 0.5
0.55556 | 0.5
0.5625 | 0.5
0.56944 | 1.7606
0.57639 | 2.9749
0.58333 | 3
0.59028 | 2.7899
0.59722 | 2.2823
0.60417 | 2.7102
0.61111 | 3
0.61806 | 3
0.625 | 3
0.63194 | 3
0.63889 | 3
0.64583 | 3
0.65278 | 3
0.65972 | 3
0.66667 | 2.9557
0.67361 | 1.5757
0.68056 | 0.5
0.6875 | 0.5
0.69444 | 0.5
0.70139 | 2.3215
0.70833 | 3
0.71528 | 3
0.72222 | 3
0.72917 | 1.7324
0.73611 | 1.0324
0.74306 | 1.7099
0.75 | 3
0.75694 | 3
0.76389 | 2.6811
0.77083 | 0.5
0.77778 | 0.5
0.78472 | 0.5
0.79167 | 0.5
0.79861 | 1.3564
0.80556 | 1.7557
0.8125 | 0.62263
0.81944 | 0.5
0.82639 | 0.5
0.83333 | 0.5
0.84028 | 1.387
0.84722 | 1.8045
0.85417 | 1.8856
0.86111 | 2.1599
0.86806 | 2.6355
0.875 | 2.5366
0.88194 | 0.96148
0.88889 | 0.5
0.89583 | 0.5
0.90278 | 0.5
0.90972 | 2.0757
0.91667 | 3
0.92361 | 2.1356
0.93056 | 1.0576
0.9375 | 1.3265
0.94444 | 1.7685
0.95139 | 1.918
0.95833 | 1.7299
0.96528 | 1.0424
0.97222 | 0.86016
0.97917 | 1.1885
0.98611 | 1.488
0.99306 | 1.8599
1 | 2.5712
1.0069 | 3
1.0139 | 3
1.0208 | 2.4134
1.0278 | 0.64632
1.0347 | 0.5
1.0417 | 0.5
1.0486 | 0.66611
1.0556 | 1.5426
1.0625 | 2.8589
1.0694 | 3
1.0764 | 3
1.0833 | 3
1.0903 | 1.4183
1.0972 | 0.5
1.1042 | 0.95087
1.1111 | 2.9069
1.1181 | 3
1.125 | 3
1.1319 | 2.542
1.1389 | 2.3879
1.1458 | 2.1597
1.1528 | 1.5691
1.1597 | 1.3506
1.1667 | 1.4538
1.1736 | 1.8311
1.1806 | 2.2946
1.1875 | 1.9512
1.1944 | 0.60598
1.2014 | 0.5
1.2083 | 0.5
1.2153 | 1.3505
1.2222 | 1.9517
1.2292 | 2.2254
1.2361 | 2.8478
1.2431 | 2.9642
1.25 | 2.7778
1.2569 | 3
1.2639 | 3
1.2708 | 3
1.2778 | 3
1.2847 | 1.8598
1.2917 | 0.5
1.2986 | 0.5
1.3056 | 0.5
1.3125 | 0.5
1.3194 | 1.1617
1.3264 | 1.7088
1.3333 | 2.5843
1.3403 | 2.9389
1.3472 | 1.9982
1.3542 | 0.5
1.3611 | 0.5
1.3681 | 0.65425
1.375 | 0.8417
1.3819 | 0.5
1.3889 | 0.5
1.3958 | 0.5
1.4028 | 0.5
1.4097 | 0.5
1.4167 | 0.5
1.4236 | 0.5
1.4306 | 1.3487
1.4375 | 2.1671
1.4444 | 2.2006
1.4514 | 1.3681
1.4583 | 0.52294
1.4653 | 0.5
1.4722 | 0.50909
1.4792 | 0.5
1.4861 | 0.5
1.4931 | 0.5
1.5 | 0.5
1.5069 | 0.5
1.5139 | 0.5
1.5208 | 0.5
1.5278 | 0.5
1.5347 | 0.6077
1.5417 | 2.2913
1.5486 | 3
1.5556 | 3
1.5625 | 1.9801
1.5694 | 0.5
1.5764 | 0.5
1.5833 | 0.5
1.5903 | 0.5
1.5972 | 0.5
1.6042 | 0.5
1.6111 | 0.5
1.6181 | 0.55898
1.625 | 1.7911
1.6319 | 2.0649
1.6389 | 1.2422
1.6458 | 1.0275
1.6528 | 1.2183
1.6597 | 1.2862
1.6667 | 1.5997
1.6736 | 1.3048
1.6806 | 0.5
1.6875 | 0.5
1.6944 | 0.5
1.7014 | 0.5
1.7083 | 0.5
1.7153 | 0.5
1.7222 | 2.0098
1.7292 | 3
1.7361 | 3
1.7431 | 3
1.75 | 3
1.7569 | 2.5667
1.7639 | 2.5292
1.7708 | 2.163
1.7778 | 1.4241
1.7847 | 1.2909
1.7917 | 1.6198
1.7986 | 2.1679
1.8056 | 2.4941
1.8125 | 2.7496
1.8194 | 2.5514
1.8264 | 1.7132
1.8333 | 1.1745
1.8403 | 1.4829
1.8472 | 2.4918
1.8542 | 2.8555
1.8611 | 2.7449
1.8681 | 2.4398
1.875 | 1.3326
1.8819 | 0.52055
1.8889 | 0.68792
1.8958 | 0.78434
1.9028 | 0.86925
1.9097 | 1.7573
1.9167 | 2.4758
1.9236 | 1.8639
1.9306 | 1.0409
1.9375 | 1.0003
1.9444 | 1.6233
1.9514 | 2.9476
1.9583 | 3
1.9653 | 3
1.9722 | 3
1.9792 | 3
1.9861 | 3
1.9931 | 3
2 | 2.7008
2.0069 | 1.5569
2.0139 | 0.6589
2.0208 | 0.63627
2.0278 | 0.5
2.0347 | 0.5
2.0417 | 0.5
2.0486 | 0.5
2.0556 | 0.5
2.0625 | 2.1855
2.0694 | 3
2.0764 | 3
2.0833 | 2.9758
2.0903 | 2.236
2.0972 | 1.6593
2.1042 | 1.6675
2.1111 | 2.3928
2.1181 | 2.9001
2.125 | 2.7846
2.1319 | 2.85
2.1389 | 2.8049
2.1458 | 2.0791
2.1528 | 1.0603
2.1597 | 0.5
2.1667 | 0.5
2.1736 | 0.5
2.1806 | 0.5
2.1875 | 0.5
2.1944 | 0.5
2.2014 | 0.5
2.2083 | 1.1126
2.2153 | 2.4664
2.2222 | 3
2.2292 | 3
2.2361 | 3
2.2431 | 2.9068
2.25 | 2.5634
2.2569 | 1.9658
2.2639 | 2.2457
2.2708 | 2.7546
2.2778 | 2.4029
2.2847 | 2.3544
2.2917 | 2.5781
2.2986 | 1.7138
2.3056 | 1.1459
2.3125 | 1.2107
2.3194 | 0.5
2.3264 | 0.5
2.3333 | 1.0385
2.3403 | 1.8783
2.3472 | 2.4905
2.3542 | 3
2.3611 | 3
2.3681 | 2.9756
2.375 | 1.8337
2.3819 | 0.5
2.3889 | 0.5
2.3958 | 0.86501
2.4028 | 2.9808
2.4097 | 3
2.4167 | 2.8987
2.4236 | 0.5
2.4306 | 0.5
2.4375 | 0.5
2.4444 | 0.5
2.4514 | 1.4839
2.4583 | 2.2969
2.4653 | 1.3302
2.4722 | 0.5
2.4792 | 0.5
2.4861 | 1.6164
2.4931 | 3
2.5 | 3
2.5069 | 3
2.5139 | 2.2114
2.5208 | 1.9274
2.5278 | 1.9047
2.5347 | 1.297
2.5417 | 0.5
2.5486 | 0.5
2.5556 | 0.5
2.5625 | 0.5
2.5694 | 0.5
2.5764 | 0.5
2.5833 | 0.82196
2.5903 | 1.9792
2.5972 | 2.0941
2.6042 | 1.7506
2.6111 | 1.5523
2.6181 | 0.93591
2.625 | 0.74238
2.6319 | 1.0749
2.6389 | 1.0126
2.6458 | 0.99401
2.6528 | 1.1542
2.6597 | 1.2549
2.6667 | 1.5349
2.6736 | 2.211
2.6806 | 2.5029
2.6875 | 2.6429
2.6944 | 2.9905
2.7014 | 3
2.7083 | 3
2.7153 | 2.6252
2.7222 | 1.2849
2.7292 | 0.5
2.7361 | 0.5
2.7431 | 0.5
2.75 | 0.5
2.7569 | 0.5
2.7639 | 0.5
2.7708 | 0.95133
2.7778 | 2.0396
2.7847 | 3
2.7917 | 3
2.7986 | 2.8257
2.8056 | 2.453
2.8125 | 1.935
2.8194 | 2.0024
2.8264 | 3
2.8333 | 3
2.8403 | 3
2.8472 | 3
2.8542 | 3
2.8611 | 1.9938
2.8681 | 1.7339
2.875 | 2.0297
2.8819 | 1.942
2.8889 | 0.87213
2.8958 | 0.5
2.9028 | 0.5
2.9097 | 0.5
2.9167 | 0.62851
2.9236 | 1.7089
2.9306 | 1.6189
2.9375 | 1.0841
2.9444 | 0.5
2.9514 | 0.5
2.9583 | 0.5
2.9653 | 0.5
2.9722 | 0.5
2.9792 | 0.5
2.9861 | 1.4332
2.9931 | 3
3 | 3
3.0069 | 3
3.0139 | 2.9655
3.0208 | 1.6947
3.0278 | 0.98056
3.0347 | 1.8171
3.0417 | 2.5825
3.0486 | 2.3511
3.0556 | 2.1042
3.0625 | 2.3665
3.0694 | 3
3.0764 | 3
3.0833 | 3
3.0903 | 2.3502
3.0972 | 1.8181
3.1042 | 2.5042
3.1111 | 3
3.1181 | 3
3.125 | 2.5504
3.1319 | 1.1255
3.1389 | 1.1188
3.1458 | 1.4277
3.1528 | 1.125
3.1597 | 1.1783
3.1667 | 1.4275
3.1736 | 0.58073
3.1806 | 0.5
3.1875 | 0.5
3.1944 | 0.5
3.2014 | 0.7248
3.2083 | 2.4068
3.2153 | 2.39
3.2222 | 1.6025
3.2292 | 1.3704
3.2361 | 1.3661
3.2431 | 1.9553
3.25 | 3
3.2569 | 2.9436
3.2639 | 1.8411
3.2708 | 1.5188
3.2778 | 2.1281
3.2847 | 2.9604
3.2917 | 3
3.2986 | 2.5241
3.3056 | 1.3736
3.3125 | 0.5
3.3194 | 0.5
3.3264 | 0.5
3.3333 | 0.5
3.3403 | 0.5
3.3472 | 0.61345
3.3542 | 1.047
3.3611 | 0.94651
3.3681 | 0.5
3.375 | 0.5
3.3819 | 0.5
3.3889 | 0.5
3.3958 | 1.1775
3.4028 | 2.8847
3.4097 | 3
3.4167 | 3
3.4236 | 2.6595
3.4306 | 2.4935
3.4375 | 2.6209
3.4444 | 2.1673
3.4514 | 1.4636
3.4583 | 0.73043
3.4653 | 0.5
3.4722 | 1.2601
3.4792 | 2.1659
3.4861 | 2.2497
3.4931 | 2.5422
3.5 | 3
3.5069 | 2.9393
3.5139 | 2.857
3.5208 | 2.5795
3.5278 | 1.1519
3.5347 | 0.5
3.5417 | 1.3072
3.5486 | 1.8557
3.5556 | 1.9073
3.5625 | 2.1863
3.5694 | 1.674
3.5764 | 0.64647
3.5833 | 0.5
3.5903 | 0.5
3.5972 | 0.5
3.6042 | 0.5
3.6111 | 0.5
3.6181 | 0.5
3.625 | 2.1885
3.6319 | 3
3.6389 | 3
3.6458 | 3
3.6528 | 2.292
3.6597 | 0.66448
3.6667 | 0.5
3.6736 | 0.5
3.6806 | 1.231
3.6875 | 1.8185
3.6944 | 1.4321
3.7014 | 0.5
3.7083 | 0.5
3.7153 | 1.6629
3.7222 | 3
3.7292 | 3
3.7361 | 3
3.7431 | 3
3.75 | 2.926
3.7569 | 1.9263
3.7639 | 1.6959
3.7708 | 2.4496
3.7778 | 2.9982
3.7847 | 2.531
3.7917 | 1.6964
3.7986 | 1.3617
3.8056 | 1.6186
3.8125 | 2.0961
3.8194 | 2.4539
3.8264 | 2.5546
3.8333 | 2.7068
3.8403 | 2.2446
3.8472 | 1.2419
3.8542 | 0.5
3.8611 | 0.5
3.8681 | 0.56873
3.875 | 1.5218
3.8819 | 2.6335
3.8889 | 3
3.8958 | 3
3.9028 | 2.3144
3.9097 | 2.1752
3.9167 | 1.7425
3.9236 | 1.5993
3.9306 | 2.1472
3.9375 | 2.0993
3.9444 | 2.054
3.9514 | 2.1554
3.9583 | 1.9402
3.9653 | 1.4528
3.9722 | 0.88002
3.9792 | 0.62558
3.9861 | 1.1912
3.9931 | 2.5272
4 | 3
4.0069 | 3
4.0139 | 3
4.0208 | 1.1205
4.0278 | 0.5
4.0347 | 0.5
4.0417 | 0.5
4.0486 | 0.5
4.0556 | 0.5
4.0625 | 0.5
4.0694 | 0.5
4.0764 | 0.71234
4.0833 | 1.7308
4.0903 | 1.5106
4.0972 | 0.5
4.1042 | 0.5
4.1111 | 0.5
4.1181 | 0.5
4.125 | 0.5
4.1319 | 1.1661
4.1389 | 1.7237
4.1458 | 1.4579
4.1528 | 0.7983
4.1597 | 0.5
4.1667 | 0.5
4.1736 | 0.5
4.1806 | 0.5
4.1875 | 1.4984
4.1944 | 3
4.2014 | 3
4.2083 | 3
4.2153 | 3
4.2222 | 3
4.2292 | 2.1674
4.2361 | 1.6311
4.2431 | 1.135
4.25 | 1.1168
4.2569 | 2.0314
4.2639 | 2.5472
4.2708 | 2.1696
4.2778 | 1.9883
4.2847 | 2.0384
4.2917 | 2.2458
4.2986 | 2.1828
4.3056 | 1.3793
4.3125 | 0.55535
4.3194 | 0.5
4.3264 | 1.3863
4.3333 | 2.7206
4.3403 | 2.7965
4.3472 | 1.7533
4.3542 | 0.91048
4.3611 | 0.5
4.3681 | 0.58587
4.375 | 0.76907
4.3819 | 0.5
4.3889 | 0.5
4.3958 | 0.5
4.4028 | 0.5
4.4097 | 0.60914
4.4167 | 1.9268
4.4236 | 2.9224
4.4306 | 3
4.4375 | 3
4.4444 | 2.2516
4.4514 | 0.5
4.4583 | 0.5
4.4653 | 0.5
4.4722 | 0.5
4.4792 | 0.55072
4.4861 | 1.8079
4.4931 | 2.4649
4.5 | 1.9615
4.5069 | 1.3539
4.5139 | 1.0408
4.5208 | 0.5
4.5278 | 0.5
4.5347 | 1.7688
4.5417 | 2.6467
4.5486 | 3
4.5556 | 3
4.5625 | 3
4.5694 | 1.3854
4.5764 | 0.82521
4.5833 | 1.1805
4.5903 | 1.0709
4.5972 | 1.4612
4.6042 | 1.6488
4.6111 | 0.75459
4.6181 | 0.5
4.625 | 1.428
4.6319 | 2.3384
4.6389 | 2.5337
4.6458 | 2.5674
4.6528 | 1.8832
4.6597 | 1.7029
4.6667 | 2.1238
4.6736 | 2.1211
4.6806 | 1.7339
4.6875 | 1.4134
4.6944 | 1.3067
4.7014 | 1.9099
4.7083 | 2.1399
4.7153 | 1.242
4.7222 | 0.93393
4.7292 | 1.1011
4.7361 | 0.62577
4.7431 | 0.5
4.75 | 0.5
4.7569 | 0.5
4.7639 | 1.6353
4.7708 | 3
4.7778 | 3
4.7847 | 2.5563
4.7917 | 1.0321
4.7986 | 0.5
4.8056 | 0.5
4.8125 | 0.5
4.8194 | 0.5
4.8264 | 0.5
4.8333 | 0.5
4.8403 | 0.5
4.8472 | 0.5
4.8542 | 0.5
4.8611 | 0.5
4.8681 | 0.5
4.875 | 0.78651
4.8819 | 1.8619
4.8889 | 2.4126
4.8958 | 1.6909
4.9028 | 0.5
4.9097 | 0.5
4.9167 | 0.5
4.9236 | 0.5
4.9306 | 0.5
4.9375 | 0.62658
4.9444 | 1.9135
4.9514 | 3
4.9583 | 3
4.9653 | 3
4.9722 | 3
4.9792 | 2.38
4.9861 | 0.87435
4.9931 | 0.51673
5 | 1.1659
5.0069 | 0.99422
5.0139 | 0.5
5.0208 | 0.5
5.0278 | 0.5
5.0347 | 1.2862
5.0417 | 2.3421
5.0486 | 2.8346
5.0556 | 2.4434
5.0625 | 1.4701
5.0694 | 0.5
5.0764 | 0.5
5.0833 | 0.63383
5.0903 | 1.769
5.0972 | 2.9935
5.1042 | 3
5.1111 | 2.0054
5.1181 | 1.171
5.125 | 1.0443
5.1319 | 0.58978
5.1389 | 0.5
5.1458 | 0.5
5.1528 | 0.83483
5.1597 | 2.3008
5.1667 | 3
5.1736 | 3
5.1806 | 1.9723
5.1875 | 1.0718
5.1944 | 1.3002
5.2014 | 1.874
5.2083 | 1.7757
5.2153 | 1.5894
5.2222 | 1.6672
5.2292 | 1.7411
5.2361 | 1.543
5.2431 | 1.6124
5.25 | 2.172
5.2569 | 2.4767
5.2639 | 2.5674
5.2708 | 2.9382
5.2778 | 2.5122
5.2847 | 1.5044
5.2917 | 1.801
5.2986 | 2.3848
5.3056 | 1.8087
5.3125 | 1.3412
5.3194 | 1.8291
5.3264 | 2.1513
5.3333 | 1.9267
5.3403 | 1.886
5.3472 | 1.6453
5.3542 | 1.4754
5.3611 | 2.3414
5.3681 | 3
5.375 | 3
5.3819 | 3
5.3889 | 2.4726
5.3958 | 1.9981
5.4028 | 1.6943
5.4097 | 1.0625
5.4167 | 1.0256
5.4236 | 1.7557
5.4306 | 2.0229
5.4375 | 2.0786
5.4444 | 1.9828
5.4514 | 1.2718
5.4583 | 1.0822
5.4653 | 1.4517
5.4722 | 1.4773
5.4792 | 0.5
5.4861 | 0.5
5.4931 | 0.5
5.5 | 0.5
5.5069 | 0.5
5.5139 | 0.5251
5.5208 | 1.5978
5.5278 | 2.5656
5.5347 | 3
5.5417 | 3
5.5486 | 3
5.5556 | 2.1846
5.5625 | 0.89205
5.5694 | 0.77696
5.5764 | 2.1789
5.5833 | 3
5.5903 | 3
5.5972 | 3
5.6042 | 2.5184
5.6111 | 0.5
5.6181 | 0.5
5.625 | 0.5
5.6319 | 0.5
5.6389 | 0.61642
5.6458 | 2.6405
5.6528 | 3
5.6597 | 3
5.6667 | 3
5.6736 | 2.933
5.6806 | 2.3885
5.6875 | 2.7814
5.6944 | 2.6604
5.7014 | 2.4455
5.7083 | 2.8032
5.7153 | 2.8728
5.7222 | 2.3172
5.7292 | 1.8045
5.7361 | 1.3173
5.7431 | 0.98746
5.75 | 1.1211
5.7569 | 1.5129
5.7639 | 2.1233
5.7708 | 2.2073
5.7778 | 2.1021
5.7847 | 2.4967
5.7917 | 3
5.7986 | 3
5.8056 | 3
5.8125 | 2.8005
5.8194 | 1.8793
5.8264 | 2.0961
5.8333 | 2.5637
5.8403 | 2.9448
5.8472 | 3
5.8542 | 3
5.8611 | 2.2901
5.8681 | 1.062
5.875 | 0.5
5.8819 | 0.5
5.8889 | 0.92738
5.8958 | 1.9102
5.9028 | 1.5107
5.9097 | 0.70207
5.9167 | 0.5
5.9236 | 0.84541
5.9306 | 1.0507
5.9375 | 0.67973
5.9444 | 0.87372
5.9514 | 2.1562
5.9583 | 2.6997
5.9653 | 1.7063
5.9722 | 0.5
5.9792 | 0.5
5.9861 | 0.5
5.9931 | 2.605
6 | 3
6.0069 | 3
6.0139 | 2.5125
6.0208 | 2.5752
6.0278 | 2.3883
6.0347 | 2.1933
6.0417 | 1.9762
6.0486 | 1.351
6.0556 | 0.68019
6.0625 | 0.5
6.0694 | 0.5
6.0764 | 0.5
6.0833 | 0.5
6.0903 | 0.5
6.0972 | 0.5
6.1042 | 1.7213
6.1111 | 3
6.1181 | 3
6.125 | 2.6133
6.1319 | 1.3369
6.1389 | 1.1599
6.1458 | 2.5535
6.1528 | 3
6.1597 | 3
6.1667 | 3
6.1736 | 3
6.1806 | 3
6.1875 | 2.0575
6.1944 | 2.224
6.2014 | 2.7431
6.2083 | 3
6.2153 | 3
6.2222 | 3
6.2292 | 3
6.2361 | 3
6.2431 | 3
6.25 | 3
6.2569 | 2.716
6.2639 | 2.4259
6.2708 | 3
6.2778 | 3
6.2847 | 3
6.2917 | 3
6.2986 | 3
6.3056 | 1.4784
6.3125 | 1.1643
6.3194 | 1.6393
6.3264 | 2.0165
6.3333 | 2.041
6.3403 | 1.0037
6.3472 | 0.5
6.3542 | 0.5
6.3611 | 0.5
6.3681 | 0.5
6.375 | 0.86691
6.3819 | 1.094
6.3889 | 1.281
6.3958 | 1.8065
6.4028 | 2.4446
6.4097 | 3
6.4167 | 3
6.4236 | 3
6.4306 | 2.2981
6.4375 | 1.3389
6.4444 | 0.5
6.4514 | 0.53198
6.4583 | 1.2974
6.4653 | 1.5432
6.4722 | 1.5508
6.4792 | 1.0895
6.4861 | 0.5
6.4931 | 0.5
6.5 | 0.5
6.5069 | 1.3769
6.5139 | 2.0024
6.5208 | 2.4137
6.5278 | 2.3379
6.5347 | 2.145
6.5417 | 1.783
6.5486 | 0.72316
6.5556 | 0.5
6.5625 | 1.2402
6.5694 | 3
6.5764 | 3
6.5833 | 3
6.5903 | 1.5638
6.5972 | 0.5
6.6042 | 0.5
6.6111 | 0.81787
6.6181 | 2.1526
6.625 | 2.8757
6.6319 | 2.4804
6.6389 | 1.4075
6.6458 | 0.5
6.6528 | 0.5
6.6597 | 0.6009
6.6667 | 1.3864
6.6736 | 2.1793
6.6806 | 2.6917
6.6875 | 3
6.6944 | 3
6.7014 | 3
6.7083 | 3
6.7153 | 2.2218
6.7222 | 1.3639
6.7292 | 0.62769
6.7361 | 0.9498
6.7431 | 0.83239
6.75 | 0.5
6.7569 | 0.65599
6.7639 | 1.8275
6.7708 | 2.8698
6.7778 | 3
6.7847 | 2.4445
6.7917 | 1.3558
6.7986 | 0.75106
6.8056 | 1.1512
6.8125 | 2.4812
6.8194 | 3
6.8264 | 2.4266
6.8333 | 0.95844
6.8403 | 0.5
6.8472 | 0.65726
6.8542 | 2.3515
6.8611 | 3
6.8681 | 3
6.875 | 3
6.8819 | 3
6.8889 | 2.8544
6.8958 | 0.77248
6.9028 | 0.5
6.9097 | 0.5
6.9167 | 0.5
6.9236 | 0.5
6.9306 | 0.5
6.9375 | 0.5
6.9444 | 0.5
6.9514 | 0.5
6.9583 | 0.79719
6.9653 | 1.9135
6.9722 | 2.7362
6.9792 | 3
6.9861 | 3
6.9931 | 2.6662
7 | 1.6622
DOsmallrange | Disabled
No interpolation
Time | SO2
d | g O2/m3
0 | 0.50685
0.0069444 | 0.59512
0.013889 | 0.46552
0.020833 | 0.50359
0.027778 | 0.61221
0.034722 | 0.53237
0.041667 | 0.45888
0.048611 | 0.43582
0.055556 | 0.43385
0.0625 | 0.47747
0.069444 | 0.41701
0.076389 | 0.48738
0.083333 | 0.53087
0.090278 | 0.44299
0.097222 | 0.55388
0.10417 | 0.54669
0.11111 | 0.30259
0.11806 | 0.5363
0.125 | 0.43383
0.13194 | 0.4723
0.13889 | 0.44787
0.14583 | 0.56549
0.15278 | 0.48634
0.15972 | 0.39972
0.16667 | 0.51826
0.17361 | 0.624
0.18056 | 0.45698
0.1875 | 0.36231
0.19444 | 0.45622
0.20139 | 0.53819
0.20833 | 0.58313
0.21528 | 0.54271
0.22222 | 0.67635
0.22917 | 0.59457
0.23611 | 0.46565
0.24306 | 0.38682
0.25 | 0.56517
0.25694 | 0.5225
0.26389 | 0.48789
0.27083 | 0.43302
0.27778 | 0.4691
0.28472 | 0.48742
0.29167 | 0.41973
0.29861 | 0.45789
0.30556 | 0.48458
0.3125 | 0.63254
0.31944 | 0.54107
0.32639 | 0.40522
0.33333 | 0.44136
0.34028 | 0.49376
0.34722 | 0.37898
0.35417 | 0.46138
0.36111 | 0.50641
0.36806 | 0.34291
0.375 | 0.49525
0.38194 | 0.46416
0.38889 | 0.56519
0.39583 | 0.57244
0.40278 | 0.58323
0.40972 | 0.54609
0.41667 | 0.44191
0.42361 | 0.55117
0.43056 | 0.44841
0.4375 | 0.53254
0.44444 | 0.44509
0.45139 | 0.49042
0.45833 | 0.39502
0.46528 | 0.38792
0.47222 | 0.61555
0.47917 | 0.47643
0.48611 | 0.55776
0.49306 | 0.51395
0.5 | 0.56937
0.50694 | 0.48699
0.51389 | 0.51955
0.52083 | 0.27196
0.52778 | 0.40191
0.53472 | 0.44259
0.54167 | 0.25983
0.54861 | 0.34781
0.55556 | 0.34912
0.5625 | 0.50857
0.56944 | 0.45471
0.57639 | 0.66692
0.58333 | 0.54525
0.59028 | 0.51067
0.59722 | 0.5656
0.60417 | 0.43352
0.61111 | 0.68876
0.61806 | 0.61308
0.625 | 0.60984
0.63194 | 0.49148
0.63889 | 0.58758
0.64583 | 0.60198
0.65278 | 0.57996
0.65972 | 0.67586
0.66667 | 0.53106
0.67361 | 0.43494
0.68056 | 0.5171
0.6875 | 0.36426
0.69444 | 0.43435
0.70139 | 0.54528
0.70833 | 0.66493
0.71528 | 0.69578
0.72222 | 0.5687
0.72917 | 0.51297
0.73611 | 0.37348
0.74306 | 0.4979
0.75 | 0.60186
0.75694 | 0.56517
0.76389 | 0.49267
0.77083 | 0.48621
0.77778 | 0.40599
0.78472 | 0.41825
0.79167 | 0.35169
0.79861 | 0.56391
0.80556 | 0.51486
0.8125 | 0.22103
0.81944 | 0.48054
0.82639 | 0.39982
0.83333 | 0.43331
0.84028 | 0.55092
0.84722 | 0.57537
0.85417 | 0.4905
0.86111 | 0.46024
0.86806 | 0.61125
0.875 | 0.61809
0.88194 | 0.47905
0.88889 | 0.36917
0.89583 | 0.42531
0.90278 | 0.30379
0.90972 | 0.59516
0.91667 | 0.51822
0.92361 | 0.76395
0.93056 | 0.27237
0.9375 | 0.45638
0.94444 | 0.55714
0.95139 | 0.65321
0.95833 | 0.45965
0.96528 | 0.3336
0.97222 | 0.64752
0.97917 | 0.40749
0.98611 | 0.61142
0.99306 | 0.45208
1 | 0.54695
1.0069 | 0.61237
1.0139 | 0.61861
1.0208 | 0.47889
1.0278 | 0.56231
1.0347 | 0.38436
1.0417 | 0.43243
1.0486 | 0.48052
1.0556 | 0.67237
1.0625 | 0.39367
1.0694 | 0.64658
1.0764 | 0.61182
1.0833 | 0.66615
1.0903 | 0.39652
1.0972 | 0.4463
1.1042 | 0.38524
1.1111 | 0.5785
1.1181 | 0.57282
1.125 | 0.54648
1.1319 | 0.49319
1.1389 | 0.45396
1.1458 | 0.62755
1.1528 | 0.53451
1.1597 | 0.28332
1.1667 | 0.42613
1.1736 | 0.64304
1.1806 | 0.63671
1.1875 | 0.43608
1.1944 | 0.45295
1.2014 | 0.48006
1.2083 | 0.5142
1.2153 | 0.32903
1.2222 | 0.64454
1.2292 | 0.50927
1.2361 | 0.57595
1.2431 | 0.45787
1.25 | 0.63349
1.2569 | 0.61669
1.2639 | 0.40498
1.2708 | 0.67605
1.2778 | 0.55538
1.2847 | 0.55884
1.2917 | 0.46023
1.2986 | 0.40732
1.3056 | 0.5628
1.3125 | 0.41743
1.3194 | 0.50488
1.3264 | 0.39677
1.3333 | 0.65002
1.3403 | 0.50072
1.3472 | 0.57407
1.3542 | 0.31541
1.3611 | 0.48941
1.3681 | 0.38616
1.375 | 0.68772
1.3819 | 0.48695
1.3889 | 0.39975
1.3958 | 0.413
1.4028 | 0.51087
1.4097 | 0.42916
1.4167 | 0.26889
1.4236 | 0.48191
1.4306 | 0.49923
1.4375 | 0.55245
1.4444 | 0.52851
1.4514 | 0.46283
1.4583 | 0.53232
1.4653 | 0.3544
1.4722 | 0.42125
1.4792 | 0.60172
1.4861 | 0.44279
1.4931 | 0.47303
1.5 | 0.44521
1.5069 | 0.49846
1.5139 | 0.38543
1.5208 | 0.49118
1.5278 | 0.45358
1.5347 | 0.54119
1.5417 | 0.69603
1.5486 | 0.52201
1.5556 | 0.57713
1.5625 | 0.46191
1.5694 | 0.4127
1.5764 | 0.47557
1.5833 | 0.46653
1.5903 | 0.54061
1.5972 | 0.34307
1.6042 | 0.40285
1.6111 | 0.62932
1.6181 | 0.41555
1.625 | 0.46731
1.6319 | 0.43235
1.6389 | 0.58378
1.6458 | 0.50622
1.6528 | 0.51443
1.6597 | 0.38652
1.6667 | 0.47207
1.6736 | 0.4246
1.6806 | 0.58929
1.6875 | 0.44085
1.6944 | 0.4067
1.7014 | 0.68495
1.7083 | 0.57771
1.7153 | 0.4942
1.7222 | 0.60831
1.7292 | 0.54653
1.7361 | 0.47493
1.7431 | 0.58946
1.75 | 0.34951
1.7569 | 0.59072
1.7639 | 0.28587
1.7708 | 0.65743
1.7778 | 0.52755
1.7847 | 0.47887
1.7917 | 0.57712
1.7986 | 0.48586
1.8056 | 0.57092
1.8125 | 0.42433
1.8194 | 0.5027
1.8264 | 0.53445
1.8333 | 0.5514
1.8403 | 0.37693
1.8472 | 0.38969
1.8542 | 0.53535
1.8611 | 0.47002
1.8681 | 0.33498
1.875 | 0.60956
1.8819 | 0.46656
1.8889 | 0.59997
1.8958 | 0.49668
1.9028 | 0.50016
1.9097 | 0.4573
1.9167 | 0.41352
1.9236 | 0.58105
1.9306 | 0.53598
1.9375 | 0.64405
1.9444 | 0.6596
1.9514 | 0.43
1.9583 | 0.75891
1.9653 | 0.72362
1.9722 | 0.50075
1.9792 | 0.52187
1.9861 | 0.31887
1.9931 | 0.58926
2 | 0.33703
2.0069 | 0.51099
2.0139 | 0.3293
2.0208 | 0.34761
2.0278 | 0.54654
2.0347 | 0.499
2.0417 | 0.53986
2.0486 | 0.6029
2.0556 | 0.66507
2.0625 | 0.23177
2.0694 | 0.54583
2.0764 | 0.52566
2.0833 | 0.55834
2.0903 | 0.51064
2.0972 | 0.516
2.1042 | 0.62286
2.1111 | 0.49085
2.1181 | 0.51343
2.125 | 0.55555
2.1319 | 0.38607
2.1389 | 0.45945
2.1458 | 0.45217
2.1528 | 0.35784
2.1597 | 0.32386
2.1667 | 0.41982
2.1736 | 0.44742
2.1806 | 0.50425
2.1875 | 0.5156
2.1944 | 0.61221
2.2014 | 0.49241
2.2083 | 0.68999
2.2153 | 0.46287
2.2222 | 0.5907
2.2292 | 0.52631
2.2361 | 0.54651
2.2431 | 0.43012
2.25 | 0.67729
2.2569 | 0.55831
2.2639 | 0.4762
2.2708 | 0.50534
2.2778 | 0.65359
2.2847 | 0.36214
2.2917 | 0.42934
2.2986 | 0.58062
2.3056 | 0.43664
2.3125 | 0.56714
2.3194 | 0.51969
2.3264 | 0.55837
2.3333 | 0.51609
2.3403 | 0.64033
2.3472 | 0.45073
2.3542 | 0.5291
2.3611 | 0.37592
2.3681 | 0.51835
2.375 | 0.49146
2.3819 | 0.6341
2.3889 | 0.73079
2.3958 | 0.32087
2.4028 | 0.28566
2.4097 | 0.40549
2.4167 | 0.45542
2.4236 | 0.55728
2.4306 | 0.50252
2.4375 | 0.5042
2.4444 | 0.47974
2.4514 | 0.29146
2.4583 | 0.46536
2.4653 | 0.87084
2.4722 | 0.43669
2.4792 | 0.69433
2.4861 | 0.46294
2.4931 | 0.536
2.5 | 0.43716
2.5069 | 0.4287
2.5139 | 0.4804
2.5208 | 0.48029
2.5278 | 0.38561
2.5347 | 0.51699
2.5417 | 0.24188
2.5486 | 0.53686
2.5556 | 0.53367
2.5625 | 0.55599
2.5694 | 0.43412
2.5764 | 0.41651
2.5833 | 0.61424
2.5903 | 0.46778
2.5972 | 0.39422
2.6042 | 0.59474
2.6111 | 0.43901
2.6181 | 0.46863
2.625 | 0.66782
2.6319 | 0.46885
2.6389 | 0.58288
2.6458 | 0.49006
2.6528 | 0.57452
2.6597 | 0.53619
2.6667 | 0.49249
2.6736 | 0.38962
2.6806 | 0.45493
2.6875 | 0.49496
2.6944 | 0.41079
2.7014 | 0.51031
2.7083 | 0.46705
2.7153 | 0.49823
2.7222 | 0.51034
2.7292 | 0.52515
2.7361 | 0.55452
2.7431 | 0.54144
2.75 | 0.47545
2.7569 | 0.4745
2.7639 | 0.62188
2.7708 | 0.44662
2.7778 | 0.59779
2.7847 | 0.62105
2.7917 | 0.55731
2.7986 | 0.51566
2.8056 | 0.46671
2.8125 | 0.51775
2.8194 | 0.53515
2.8264 | 0.50922
2.8333 | 0.44827
2.8403 | 0.48333
2.8472 | 0.34015
2.8542 | 0.41385
2.8611 | 0.42215
2.8681 | 0.54821
2.875 | 0.5688
2.8819 | 0.31949
2.8889 | 0.44819
2.8958 | 0.61871
2.9028 | 0.47372
2.9097 | 0.50089
2.9167 | 0.25218
2.9236 | 0.42699
2.9306 | 0.54763
2.9375 | 0.52607
2.9444 | 0.58708
2.9514 | 0.76795
2.9583 | 0.45399
2.9653 | 0.53127
2.9722 | 0.49086
2.9792 | 0.50196
2.9861 | 0.4649
2.9931 | 0.64724
3 | 0.57065
3.0069 | 0.36069
3.0139 | 0.53703
3.0208 | 0.67123
3.0278 | 0.63275
3.0347 | 0.51348
3.0417 | 0.27824
3.0486 | 0.58848
3.0556 | 0.70438
3.0625 | 0.57057
3.0694 | 0.48694
3.0764 | 0.47181
3.0833 | 0.58728
3.0903 | 0.41821
3.0972 | 0.62154
3.1042 | 0.4998
3.1111 | 0.34727
3.1181 | 0.62135
3.125 | 0.46086
3.1319 | 0.44109
3.1389 | 0.42098
3.1458 | 0.54544
3.1528 | 0.34697
3.1597 | 0.60495
3.1667 | 0.53098
3.1736 | 0.27402
3.1806 | 0.48462
3.1875 | 0.69069
3.1944 | 0.49877
3.2014 | 0.62624
3.2083 | 0.46501
3.2153 | 0.55296
3.2222 | 0.3676
3.2292 | 0.57755
3.2361 | 0.69643
3.2431 | 0.52882
3.25 | 0.46122
3.2569 | 0.42228
3.2639 | 0.52972
3.2708 | 0.38286
3.2778 | 0.50419
3.2847 | 0.40071
3.2917 | 0.44275
3.2986 | 0.4725
3.3056 | 0.63072
3.3125 | 0.40516
3.3194 | 0.42826
3.3264 | 0.41733
3.3333 | 0.35503
3.3403 | 0.46479
3.3472 | 0.68992
3.3542 | 0.59358
3.3611 | 0.49419
3.3681 | 0.47596
3.375 | 0.58342
3.3819 | 0.50633
3.3889 | 0.51751
3.3958 | 0.54104
3.4028 | 0.31002
3.4097 | 0.59667
3.4167 | 0.32084
3.4236 | 0.51041
3.4306 | 0.70953
3.4375 | 0.52039
3.4444 | 0.46379
3.4514 | 0.54084
3.4583 | 0.68223
3.4653 | 0.54666
3.4722 | 0.43146
3.4792 | 0.60716
3.4861 | 0.31972
3.4931 | 0.55114
3.5 | 0.59746
3.5069 | 0.33886
3.5139 | 0.5112
3.5208 | 0.53658
3.5278 | 0.43756
3.5347 | 0.40131
3.5417 | 0.33928
3.5486 | 0.40217
3.5556 | 0.38275
3.5625 | 0.38558
3.5694 | 0.65776
3.5764 | 0.5709
3.5833 | 0.57218
3.5903 | 0.56352
3.5972 | 0.58955
3.6042 | 0.35712
3.6111 | 0.50988
3.6181 | 0.3895
3.625 | 0.49824
3.6319 | 0.71179
3.6389 | 0.48994
3.6458 | 0.45737
3.6528 | 0.45128
3.6597 | 0.46328
3.6667 | 0.69828
3.6736 | 0.57526
3.6806 | 0.62477
3.6875 | 0.63465
3.6944 | 0.54866
3.7014 | 0.44447
3.7083 | 0.48929
3.7153 | 0.55089
3.7222 | 0.57663
3.7292 | 0.55446
3.7361 | 0.49543
3.7431 | 0.44492
3.75 | 0.74002
3.7569 | 0.42307
3.7639 | 0.66534
3.7708 | 0.47868
3.7778 | 0.6462
3.7847 | 0.43159
3.7917 | 0.59212
3.7986 | 0.41679
3.8056 | 0.48652
3.8125 | 0.45663
3.8194 | 0.57213
3.8264 | 0.57578
3.8333 | 0.49568
3.8403 | 0.51808
3.8472 | 0.60123
3.8542 | 0.41773
3.8611 | 0.50359
3.8681 | 0.54457
3.875 | 0.52448
3.8819 | 0.39592
3.8889 | 0.60557
3.8958 | 0.44536
3.9028 | 0.68166
3.9097 | 0.49312
3.9167 | 0.27989
3.9236 | 0.556
3.9306 | 0.31242
3.9375 | 0.6241
3.9444 | 0.53538
3.9514 | 0.61059
3.9583 | 0.58294
3.9653 | 0.44247
3.9722 | 0.36928
3.9792 | 0.37987
3.9861 | 0.4142
3.9931 | 0.40584
4 | 0.35765
4.0069 | 0.4704
4.0139 | 0.5647
4.0208 | 0.47932
4.0278 | 0.50159
4.0347 | 0.32803
4.0417 | 0.45379
4.0486 | 0.40713
4.0556 | 0.56957
4.0625 | 0.28201
4.0694 | 0.56321
4.0764 | 0.56541
4.0833 | 0.50095
4.0903 | 0.43502
4.0972 | 0.38361
4.1042 | 0.40525
4.1111 | 0.38942
4.1181 | 0.36293
4.125 | 0.66373
4.1319 | 0.61327
4.1389 | 0.5857
4.1458 | 0.56498
4.1528 | 0.42182
4.1597 | 0.62973
4.1667 | 0.49527
4.1736 | 0.42293
4.1806 | 0.60372
4.1875 | 0.408
4.1944 | 0.62073
4.2014 | 0.58956
4.2083 | 0.47227
4.2153 | 0.48387
4.2222 | 0.59515
4.2292 | 0.58702
4.2361 | 0.50366
4.2431 | 0.41106
4.25 | 0.469
4.2569 | 0.54123
4.2639 | 0.49366
4.2708 | 0.56988
4.2778 | 0.59118
4.2847 | 0.47399
4.2917 | 0.37635
4.2986 | 0.56369
4.3056 | 0.41847
4.3125 | 0.52289
4.3194 | 0.37011
4.3264 | 0.43621
4.3333 | 0.47958
4.3403 | 0.54837
4.3472 | 0.39025
4.3542 | 0.58539
4.3611 | 0.59186
4.3681 | 0.56656
4.375 | 0.60656
4.3819 | 0.44505
4.3889 | 0.41539
4.3958 | 0.39242
4.4028 | 0.46528
4.4097 | 0.47333
4.4167 | 0.53377
4.4236 | 0.46574
4.4306 | 0.62221
4.4375 | 0.49064
4.4444 | 0.37937
4.4514 | 0.54886
4.4583 | 0.46392
4.4653 | 0.4309
4.4722 | 0.50693
4.4792 | 0.57242
4.4861 | 0.58149
4.4931 | 0.44547
4.5 | 0.61806
4.5069 | 0.32169
4.5139 | 0.48523
4.5208 | 0.45376
4.5278 | 0.72847
4.5347 | 0.42138
4.5417 | 0.50181
4.5486 | 0.4157
4.5556 | 0.56438
4.5625 | 0.53381
4.5694 | 0.61511
4.5764 | 0.31217
4.5833 | 0.57555
4.5903 | 0.44572
4.5972 | 0.60923
4.6042 | 0.5138
4.6111 | 0.32242
4.6181 | 0.51999
4.625 | 0.5204
4.6319 | 0.47188
4.6389 | 0.54715
4.6458 | 0.48621
4.6528 | 0.40708
4.6597 | 0.74221
4.6667 | 0.42926
4.6736 | 0.48518
4.6806 | 0.41489
4.6875 | 0.55801
4.6944 | 0.61912
4.7014 | 0.49037
4.7083 | 0.66543
4.7153 | 0.45853
4.7222 | 0.44901
4.7292 | 0.39892
4.7361 | 0.44254
4.7431 | 0.50351
4.75 | 0.45615
4.7569 | 0.26722
4.7639 | 0.58744
4.7708 | 0.43702
4.7778 | 0.46057
4.7847 | 0.35243
4.7917 | 0.3828
4.7986 | 0.53802
4.8056 | 0.4726
4.8125 | 0.646
4.8194 | 0.43138
4.8264 | 0.59148
4.8333 | 0.42061
4.8403 | 0.40046
4.8472 | 0.34339
4.8542 | 0.50245
4.8611 | 0.45547
4.8681 | 0.43057
4.875 | 0.58374
4.8819 | 0.51891
4.8889 | 0.62689
4.8958 | 0.64057
4.9028 | 0.43589
4.9097 | 0.53655
4.9167 | 0.40965
4.9236 | 0.46992
4.9306 | 0.53047
4.9375 | 0.51457
4.9444 | 0.25275
4.9514 | 0.31339
4.9583 | 0.59588
4.9653 | 0.54585
4.9722 | 0.56312
4.9792 | 0.33369
4.9861 | 0.54957
4.9931 | 0.51116
5 | 0.43515
5.0069 | 0.33351
5.0139 | 0.5272
5.0208 | 0.65474
5.0278 | 0.55212
5.0347 | 0.38805
5.0417 | 0.57082
5.0486 | 0.40846
5.0556 | 0.53561
5.0625 | 0.49247
5.0694 | 0.35783
5.0764 | 0.50362
5.0833 | 0.50043
5.0903 | 0.54816
5.0972 | 0.6067
5.1042 | 0.46501
5.1111 | 0.52865
5.1181 | 0.42221
5.125 | 0.55317
5.1319 | 0.51791
5.1389 | 0.52931
5.1458 | 0.27497
5.1528 | 0.5895
5.1597 | 0.50769
5.1667 | 0.6422
5.1736 | 0.45361
5.1806 | 0.55933
5.1875 | 0.82907
5.1944 | 0.52819
5.2014 | 0.37953
5.2083 | 0.71606
5.2153 | 0.52206
5.2222 | 0.42737
5.2292 | 0.5589
5.2361 | 0.54642
5.2431 | 0.33983
5.25 | 0.51784
5.2569 | 0.52318
5.2639 | 0.63085
5.2708 | 0.28778
5.2778 | 0.5029
5.2847 | 0.56643
5.2917 | 0.56353
5.2986 | 0.57869
5.3056 | 0.52515
5.3125 | 0.51624
5.3194 | 0.52223
5.3264 | 0.31069
5.3333 | 0.64304
5.3403 | 0.50709
5.3472 | 0.30056
5.3542 | 0.56166
5.3611 | 0.56586
5.3681 | 0.56319
5.375 | 0.34865
5.3819 | 0.55175
5.3889 | 0.44893
5.3958 | 0.63697
5.4028 | 0.41573
5.4097 | 0.44537
5.4167 | 0.36136
5.4236 | 0.40896
5.4306 | 0.46239
5.4375 | 0.58728
5.4444 | 0.4672
5.4514 | 0.46471
5.4583 | 0.64793
5.4653 | 0.55865
5.4722 | 0.59154
5.4792 | 0.42125
5.4861 | 0.35052
5.4931 | 0.64192
5.5 | 0.38609
5.5069 | 0.55774
5.5139 | 0.71431
5.5208 | 0.56111
5.5278 | 0.51926
5.5347 | 0.47663
5.5417 | 0.42252
5.5486 | 0.3563
5.5556 | 0.46379
5.5625 | 0.5009
5.5694 | 0.37473
5.5764 | 0.6272
5.5833 | 0.52044
5.5903 | 0.65874
5.5972 | 0.5248
5.6042 | 0.46008
5.6111 | 0.59923
5.6181 | 0.50847
5.625 | 0.56394
5.6319 | 0.57544
5.6389 | 0.45265
5.6458 | 0.59096
5.6528 | 0.4013
5.6597 | 0.55214
5.6667 | 0.42821
5.6736 | 0.61274
5.6806 | 0.42331
5.6875 | 0.59386
5.6944 | 0.36325
5.7014 | 0.57455
5.7083 | 0.61633
5.7153 | 0.67464
5.7222 | 0.51566
5.7292 | 0.51717
5.7361 | 0.48092
5.7431 | 0.62834
5.75 | 0.59123
5.7569 | 0.50241
5.7639 | 0.50129
5.7708 | 0.61305
5.7778 | 0.50712
5.7847 | 0.41279
5.7917 | 0.4233
5.7986 | 0.62183
5.8056 | 0.50887
5.8125 | 0.51557
5.8194 | 0.48385
5.8264 | 0.38042
5.8333 | 0.54543
5.8403 | 0.48902
5.8472 | 0.48522
5.8542 | 0.4762
5.8611 | 0.39883
5.8681 | 0.24184
5.875 | 0.27113
5.8819 | 0.4817
5.8889 | 0.61938
5.8958 | 0.4959
5.9028 | 0.65808
5.9097 | 0.45139
5.9167 | 0.49832
5.9236 | 0.66894
5.9306 | 0.55132
5.9375 | 0.46057
5.9444 | 0.48328
5.9514 | 0.53345
5.9583 | 0.46161
5.9653 | 0.44194
5.9722 | 0.41956
5.9792 | 0.54828
5.9861 | 0.40592
5.9931 | 0.32028
6 | 0.4609
6.0069 | 0.61914
6.0139 | 0.60991
6.0208 | 0.49435
6.0278 | 0.40719
6.0347 | 0.48048
6.0417 | 0.64447
6.0486 | 0.52007
6.0556 | 0.64416
6.0625 | 0.60861
6.0694 | 0.52913
6.0764 | 0.64611
6.0833 | 0.50493
6.0903 | 0.41931
6.0972 | 0.62299
6.1042 | 0.6094
6.1111 | 0.5541
6.1181 | 0.43016
6.125 | 0.64456
6.1319 | 0.64864
6.1389 | 0.56907
6.1458 | 0.5179
6.1528 | 0.67281
6.1597 | 0.4451
6.1667 | 0.50902
6.1736 | 0.73071
6.1806 | 0.59769
6.1875 | 0.64332
6.1944 | 0.51759
6.2014 | 0.51756
6.2083 | 0.49058
6.2153 | 0.37537
6.2222 | 0.65845
6.2292 | 0.54305
6.2361 | 0.44674
6.2431 | 0.46292
6.25 | 0.45248
6.2569 | 0.36621
6.2639 | 0.5299
6.2708 | 0.39492
6.2778 | 0.43921
6.2847 | 0.58165
6.2917 | 0.33381
6.2986 | 0.68804
6.3056 | 0.45848
6.3125 | 0.5553
6.3194 | 0.61363
6.3264 | 0.5509
6.3333 | 0.32525
6.3403 | 0.54542
6.3472 | 0.47406
6.3542 | 0.40017
6.3611 | 0.50207
6.3681 | 0.52995
6.375 | 0.46145
6.3819 | 0.47961
6.3889 | 0.39932
6.3958 | 0.40431
6.4028 | 0.5344
6.4097 | 0.54402
6.4167 | 0.51177
6.4236 | 0.52288
6.4306 | 0.54765
6.4375 | 0.44323
6.4444 | 0.48974
6.4514 | 0.59692
6.4583 | 0.69471
6.4653 | 0.61648
6.4722 | 0.46394
6.4792 | 0.44568
6.4861 | 0.41463
6.4931 | 0.56401
6.5 | 0.39831
6.5069 | 0.61364
6.5139 | 0.60146
6.5208 | 0.50997
6.5278 | 0.46684
6.5347 | 0.37384
6.5417 | 0.51647
6.5486 | 0.52058
6.5556 | 0.46131
6.5625 | 0.53994
6.5694 | 0.73651
6.5764 | 0.55262
6.5833 | 0.5671
6.5903 | 0.64526
6.5972 | 0.46104
6.6042 | 0.40142
6.6111 | 0.58842
6.6181 | 0.46222
6.625 | 0.38119
6.6319 | 0.54099
6.6389 | 0.49297
6.6458 | 0.33169
6.6528 | 0.58809
6.6597 | 0.49238
6.6667 | 0.62708
6.6736 | 0.45866
6.6806 | 0.39028
6.6875 | 0.57271
6.6944 | 0.45814
6.7014 | 0.63594
6.7083 | 0.49715
6.7153 | 0.61708
6.7222 | 0.31251
6.7292 | 0.43846
6.7361 | 0.53502
6.7431 | 0.60892
6.75 | 0.62905
6.7569 | 0.58624
6.7639 | 0.60639
6.7708 | 0.59395
6.7778 | 0.38706
6.7847 | 0.45998
6.7917 | 0.41313
6.7986 | 0.51767
6.8056 | 0.48221
6.8125 | 0.28516
6.8194 | 0.43588
6.8264 | 0.41488
6.8333 | 0.4746
6.8403 | 0.4335
6.8472 | 0.53393
6.8542 | 0.5201
6.8611 | 0.56919
6.8681 | 0.44996
6.875 | 0.64049
6.8819 | 0.41795
6.8889 | 0.47996
6.8958 | 0.4754
6.9028 | 0.58163
6.9097 | 0.54016
6.9167 | 0.48065
6.9236 | 0.45039
6.9306 | 0.39311
6.9375 | 0.37035
6.9444 | 0.40631
6.9514 | 0.44791
6.9583 | 0.36188
6.9653 | 0.55827
6.9722 | 0.56471
6.9792 | 0.496
6.9861 | 0.49315
6.9931 | 0.46042
7 | 0.57477
DOsine | Disabled
No interpolation | Repeated every 168 hours
Time | SO2
d | g O2/m3
0 | 1.7569
0.0069444 | 1.8638
0.013889 | 1.7529
0.020833 | 1.8097
0.027778 | 1.9369
0.034722 | 1.8757
0.041667 | 1.8208
0.048611 | 1.8163
0.055556 | 1.8329
0.0625 | 1.895
0.069444 | 1.8529
0.076389 | 1.9416
0.083333 | 2.0034
0.090278 | 1.9337
0.097222 | 2.0627
0.10417 | 2.0735
0.11111 | 1.8473
0.11806 | 2.0989
0.125 | 2.0141
0.13194 | 2.0702
0.13889 | 2.0632
0.14583 | 2.1982
0.15278 | 2.1362
0.15972 | 2.0667
0.16667 | 2.2021
0.17361 | 2.3247
0.18056 | 2.1742
0.1875 | 2.096
0.19444 | 2.2062
0.20139 | 2.3043
0.20833 | 2.3652
0.21528 | 2.3405
0.22222 | 2.4897
0.22917 | 2.4232
0.23611 | 2.3095
0.24306 | 2.2456
0.25 | 2.4387
0.25694 | 2.4105
0.26389 | 2.3902
0.27083 | 2.3494
0.27778 | 2.3993
0.28472 | 2.4312
0.29167 | 2.3768
0.29861 | 2.4281
0.30556 | 2.4676
0.3125 | 2.6282
0.31944 | 2.549
0.32639 | 2.4253
0.33333 | 2.4732
0.34028 | 2.5371
0.34722 | 2.4336
0.35417 | 2.5269
0.36111 | 2.5827
0.36806 | 2.4295
0.375 | 2.592
0.38194 | 2.5707
0.38889 | 2.6812
0.39583 | 2.6977
0.40278 | 2.7173
0.40972 | 2.6888
0.41667 | 2.5929
0.42361 | 2.7101
0.43056 | 2.615
0.4375 | 2.7064
0.44444 | 2.626
0.45139 | 2.678
0.45833 | 2.5889
0.46528 | 2.5878
0.47222 | 2.8211
0.47917 | 2.6873
0.48611 | 2.7737
0.49306 | 2.7345
0.5 | 2.7943
0.50694 | 2.7159
0.51389 | 2.7521
0.52083 | 2.5078
0.52778 | 2.6407
0.53472 | 2.684
0.54167 | 2.5035
0.54861 | 2.5934
0.55556 | 2.5963
0.5625 | 2.757
0.56944 | 2.704
0.57639 | 2.9167
0.58333 | 2.7952
0.59028 | 2.7605
0.59722 | 2.8149
0.60417 | 2.6819
0.61111 | 2.936
0.61806 | 2.8587
0.625 | 2.8536
0.63194 | 2.7329
0.63889 | 2.8264
0.64583 | 2.8379
0.65278 | 2.8125
0.65972 | 2.9048
0.66667 | 2.756
0.67361 | 2.6555
0.68056 | 2.733
0.6875 | 2.5752
0.69444 | 2.6399
0.70139 | 2.7452
0.70833 | 2.8588
0.71528 | 2.8833
0.72222 | 2.7496
0.72917 | 2.6869
0.73611 | 2.54
0.74306 | 2.6568
0.75 | 2.7528
0.75694 | 2.7079
0.76389 | 2.6268
0.77083 | 2.6114
0.77778 | 2.522
0.78472 | 2.5248
0.79167 | 2.4484
0.79861 | 2.6505
0.80556 | 2.5911
0.8125 | 2.2866
0.81944 | 2.5351
0.82639 | 2.4432
0.83333 | 2.4651
0.84028 | 2.571
0.84722 | 2.5833
0.85417 | 2.4861
0.86111 | 2.4433
0.86806 | 2.5815
0.875 | 2.5752
0.88194 | 2.4228
0.88889 | 2.2993
0.89583 | 2.3417
0.90278 | 2.2061
0.90972 | 2.4832
0.91667 | 2.3917
0.92361 | 2.6227
0.93056 | 2.1162
0.9375 | 2.2851
0.94444 | 2.3705
0.95139 | 2.451
0.95833 | 2.2417
0.96528 | 2.0997
0.97222 | 2.3975
0.97917 | 2.1412
0.98611 | 2.3287
0.99306 | 2.1527
1 | 2.2308
1.0069 | 2.2793
1.0139 | 2.2685
1.0208 | 2.1116
1.0278 | 2.1777
1.0347 | 1.9822
1.0417 | 2.0127
1.0486 | 2.0431
1.0556 | 2.2171
1.0625 | 1.9205
1.0694 | 2.1554
1.0764 | 2.1025
1.0833 | 2.1387
1.0903 | 1.8508
1.0972 | 1.8822
1.1042 | 1.8027
1.1111 | 1.9775
1.1181 | 1.9533
1.125 | 1.9084
1.1319 | 1.8366
1.1389 | 1.7787
1.1458 | 1.9336
1.1528 | 1.8219
1.1597 | 1.552
1.1667 | 1.6761
1.1736 | 1.8743
1.1806 | 1.8493
1.1875 | 1.63
1.1944 | 1.6282
1.2014 | 1.6367
1.2083 | 1.6522
1.2153 | 1.4485
1.2222 | 1.7455
1.2292 | 1.5918
1.2361 | 1.64
1.2431 | 1.5036
1.25 | 1.661
1.2569 | 1.626
1.2639 | 1.3962
1.2708 | 1.6492
1.2778 | 1.5106
1.2847 | 1.4963
1.2917 | 1.38
1.2986 | 1.3094
1.3056 | 1.4475
1.3125 | 1.2848
1.3194 | 1.355
1.3264 | 1.2298
1.3333 | 1.4661
1.3403 | 1.3001
1.3472 | 1.3568
1.3542 | 1.0817
1.3611 | 1.2394
1.3681 | 1.1201
1.375 | 1.4057
1.3819 | 1.1892
1.3889 | 1.0864
1.3958 | 1.0843
1.4028 | 1.1671
1.4097 | 1.0704
1.4167 | 0.8954
1.4236 | 1.0939
1.4306 | 1.0969
1.4375 | 1.1361
1.4444 | 1.0983
1.4514 | 1.0191
1.4583 | 1.0752
1.4653 | 0.88419
1.4722 | 0.9382
1.4792 | 1.1061
1.4861 | 0.93482
1.4931 | 0.95299
1.5 | 0.91337
1.5069 | 0.95511
1.5139 | 0.83083
1.5208 | 0.92562
1.5278 | 0.87734
1.5347 | 0.95456
1.5417 | 1.0993
1.5486 | 0.91548
1.5556 | 0.96111
1.5625 | 0.83669
1.5694 | 0.77859
1.5764 | 0.83287
1.5833 | 0.81556
1.5903 | 0.88169
1.5972 | 0.67651
1.6042 | 0.72897
1.6111 | 0.94845
1.6181 | 0.72801
1.625 | 0.77343
1.6319 | 0.73246
1.6389 | 0.87821
1.6458 | 0.7953
1.6528 | 0.79851
1.6597 | 0.66593
1.6667 | 0.74714
1.6736 | 0.69568
1.6806 | 0.85673
1.6875 | 0.70498
1.6944 | 0.66787
1.7014 | 0.94351
1.7083 | 0.83399
1.7153 | 0.74857
1.7222 | 0.86111
1.7292 | 0.79811
1.7361 | 0.72563
1.7431 | 0.83963
1.75 | 0.59951
1.7569 | 0.84089
1.7639 | 0.53657
1.7708 | 0.909
1.7778 | 0.78034
1.7847 | 0.73323
1.7917 | 0.8334
1.7986 | 0.74441
1.8056 | 0.83209
1.8125 | 0.68846
1.8194 | 0.77013
1.8264 | 0.80553
1.8333 | 0.82647
1.8403 | 0.65634
1.8472 | 0.67376
1.8542 | 0.82444
1.8611 | 0.76444
1.8681 | 0.63508
1.875 | 0.91568
1.8819 | 0.77902
1.8889 | 0.91909
1.8958 | 0.8228
1.9028 | 0.8336
1.9097 | 0.79838
1.9167 | 0.76255
1.9236 | 0.93835
1.9306 | 0.90187
1.9375 | 1.0188
1.9444 | 1.0436
1.9514 | 0.82347
1.9583 | 1.1622
1.9653 | 1.137
1.9722 | 0.92451
1.9792 | 0.95631
1.9861 | 0.76427
1.9931 | 1.0459
2 | 0.8052
2.0069 | 0.99096
2.0139 | 0.82133
2.0208 | 0.85197
2.0278 | 1.0635
2.0347 | 1.0288
2.0417 | 1.0828
2.0486 | 1.1591
2.0556 | 1.2349
2.0625 | 0.81542
2.0694 | 1.1435
2.0764 | 1.1377
2.0833 | 1.1849
2.0903 | 1.1519
2.0972 | 1.1722
2.1042 | 1.2942
2.1111 | 1.1775
2.1181 | 1.2157
2.125 | 1.2735
2.1319 | 1.12
2.1389 | 1.2094
2.1458 | 1.2184
2.1528 | 1.1406
2.1597 | 1.1232
2.1667 | 1.2359
2.1736 | 1.2805
2.1806 | 1.3544
2.1875 | 1.3829
2.1944 | 1.4969
2.2014 | 1.3945
2.2083 | 1.6097
2.2153 | 1.4003
2.2222 | 1.5459
2.2292 | 1.4995
2.2361 | 1.5377
2.2431 | 1.4394
2.25 | 1.7048
2.2569 | 1.6041
2.2639 | 1.5403
2.2708 | 1.5878
2.2778 | 1.7545
2.2847 | 1.4816
2.2917 | 1.5674
2.2986 | 1.7373
2.3056 | 1.6119
2.3125 | 1.7611
2.3194 | 1.7323
2.3264 | 1.7897
2.3333 | 1.7661
2.3403 | 1.909
2.3472 | 1.7381
2.3542 | 1.8352
2.3611 | 1.7007
2.3681 | 1.8617
2.375 | 1.8534
2.3819 | 2.0146
2.3889 | 2.1298
2.3958 | 1.7384
2.4028 | 1.7216
2.4097 | 1.8597
2.4167 | 1.9279
2.4236 | 2.048
2.4306 | 2.0113
2.4375 | 2.031
2.4444 | 2.0245
2.4514 | 1.854
2.4583 | 2.0456
2.4653 | 2.4687
2.4722 | 2.052
2.4792 | 2.327
2.4861 | 2.1128
2.4931 | 2.203
2.5 | 2.121
2.5069 | 2.1294
2.5139 | 2.1977
2.5208 | 2.214
2.5278 | 2.1356
2.5347 | 2.2831
2.5417 | 2.0239
2.5486 | 2.3346
2.5556 | 2.347
2.5625 | 2.3847
2.5694 | 2.2779
2.5764 | 2.2753
2.5833 | 2.4877
2.5903 | 2.3558
2.5972 | 2.2965
2.6042 | 2.5111
2.6111 | 2.3692
2.6181 | 2.4124
2.625 | 2.6249
2.6319 | 2.4391
2.6389 | 2.5659
2.6458 | 2.4857
2.6528 | 2.5825
2.6597 | 2.5562
2.6667 | 2.5243
2.6736 | 2.433
2.6806 | 2.5095
2.6875 | 2.5605
2.6944 | 2.487
2.7014 | 2.5969
2.7083 | 2.5638
2.7153 | 2.6048
2.7222 | 2.6264
2.7292 | 2.6504
2.7361 | 2.6886
2.7431 | 2.6841
2.75 | 2.6264
2.7569 | 2.6334
2.7639 | 2.7884
2.7708 | 2.6205
2.7778 | 2.7787
2.7847 | 2.8086
2.7917 | 2.7512
2.7986 | 2.7156
2.8056 | 2.6723
2.8125 | 2.7287
2.8194 | 2.7511
2.8264 | 2.7298
2.8333 | 2.6732
2.8403 | 2.7122
2.8472 | 2.5727
2.8542 | 2.6497
2.8611 | 2.661
2.8681 | 2.7897
2.875 | 2.8125
2.8819 | 2.5651
2.8889 | 2.6954
2.8958 | 2.8671
2.9028 | 2.723
2.9097 | 2.7507
2.9167 | 2.5022
2.9236 | 2.6768
2.9306 | 2.7969
2.9375 | 2.7745
2.9444 | 2.8343
2.9514 | 3.0136
2.9583 | 2.6977
2.9653 | 2.7727
2.9722 | 2.7297
2.9792 | 2.7378
2.9861 | 2.6975
2.9931 | 2.8762
3 | 2.7956
3.0069 | 2.5813
3.0139 | 2.753
3.0208 | 2.8821
3.0278 | 2.8383
3.0347 | 2.7134
3.0417 | 2.4721
3.0486 | 2.776
3.0556 | 2.8853
3.0625 | 2.7444
3.0694 | 2.6535
3.0764 | 2.6307
3.0833 | 2.7382
3.0903 | 2.5609
3.0972 | 2.7557
3.1042 | 2.625
3.1111 | 2.4633
3.1181 | 2.7279
3.125 | 2.5576
3.1319 | 2.5277
3.1389 | 2.4972
3.1458 | 2.611
3.1528 | 2.4016
3.1597 | 2.6483
3.1667 | 2.5628
3.1736 | 2.2941
3.1806 | 2.4926
3.1875 | 2.6863
3.1944 | 2.4818
3.2014 | 2.5964
3.2083 | 2.4221
3.2153 | 2.4967
3.2222 | 2.2978
3.2292 | 2.4939
3.2361 | 2.5987
3.2431 | 2.4168
3.25 | 2.3347
3.2569 | 2.281
3.2639 | 2.3735
3.2708 | 2.2115
3.2778 | 2.3175
3.2847 | 2.1985
3.2917 | 2.2248
3.2986 | 2.2386
3.3056 | 2.3807
3.3125 | 2.1389
3.3194 | 2.1455
3.3264 | 2.118
3.3333 | 2.0389
3.3403 | 2.1318
3.3472 | 2.3398
3.3542 | 2.2263
3.3611 | 2.1095
3.3681 | 2.0738
3.375 | 2.1637
3.3819 | 2.0689
3.3889 | 2.0623
3.3958 | 2.0679
3.4028 | 1.8188
3.4097 | 2.0874
3.4167 | 1.7934
3.4236 | 1.9647
3.4306 | 2.1454
3.4375 | 1.9379
3.4444 | 1.8628
3.4514 | 1.9214
3.4583 | 2.0442
3.4653 | 1.89
3.4722 | 1.7562
3.4792 | 1.9132
3.4861 | 1.6071
3.4931 | 1.8198
3.5 | 1.8475
3.5069 | 1.5702
3.5139 | 1.7238
3.5208 | 1.7305
3.5278 | 1.6128
3.5347 | 1.5579
3.5417 | 1.4773
3.5486 | 1.5216
3.5556 | 1.4837
3.5625 | 1.4681
3.5694 | 1.7218
3.5764 | 1.6166
3.5833 | 1.5997
3.5903 | 1.5728
3.5972 | 1.5807
3.6042 | 1.3303
3.6111 | 1.4651
3.6181 | 1.3269
3.625 | 1.418
3.6319 | 1.6139
3.6389 | 1.3746
3.6458 | 1.3247
3.6528 | 1.3014
3.6597 | 1.2963
3.6667 | 1.5144
3.6736 | 1.3746
3.6806 | 1.4075
3.6875 | 1.4009
3.6944 | 1.2987
3.7014 | 1.1784
3.7083 | 1.2073
3.7153 | 1.2531
3.7222 | 1.2633
3.7292 | 1.2258
3.7361 | 1.1516
3.7431 | 1.0862
3.75 | 1.3665
3.7569 | 1.0351
3.7639 | 1.263
3.7708 | 1.0623
3.7778 | 1.216
3.7847 | 0.98783
3.7917 | 1.135
3.7986 | 0.94658
3.8056 | 1.0035
3.8125 | 0.96099
3.8194 | 1.0642
3.8264 | 1.0557
3.8333 | 0.96385
3.8403 | 0.97473
3.8472 | 1.0466
3.8542 | 0.85217
3.8611 | 0.92735
3.8681 | 0.95794
3.875 | 0.92776
3.8819 | 0.78939
3.8889 | 0.98954
3.8958 | 0.82014
3.9028 | 1.0475
3.9097 | 0.85042
3.9167 | 0.62892
3.9236 | 0.89707
3.9306 | 0.64586
3.9375 | 0.95022
3.9444 | 0.85451
3.9514 | 0.92304
3.9583 | 0.88905
3.9653 | 0.74258
3.9722 | 0.66371
3.9792 | 0.66895
3.9861 | 0.69827
3.9931 | 0.68524
4 | 0.63272
4.0069 | 0.74148
4.0139 | 0.83213
4.0208 | 0.74345
4.0278 | 0.76276
4.0347 | 0.58659
4.0417 | 0.71008
4.0486 | 0.66149
4.0556 | 0.82237
4.0625 | 0.53359
4.0694 | 0.81391
4.0764 | 0.81558
4.0833 | 0.75095
4.0903 | 0.6852
4.0972 | 0.63431
4.1042 | 0.65682
4.1111 | 0.64222
4.1181 | 0.6173
4.125 | 0.92002
4.1319 | 0.87182
4.1389 | 0.84687
4.1458 | 0.82911
4.1528 | 0.68925
4.1597 | 0.90081
4.1667 | 0.77034
4.1736 | 0.70233
4.1806 | 0.88779
4.1875 | 0.69708
4.1944 | 0.91515
4.2014 | 0.88966
4.2083 | 0.77839
4.2153 | 0.79633
4.2222 | 0.91427
4.2292 | 0.91314
4.2361 | 0.83709
4.2431 | 0.75213
4.25 | 0.81803
4.2569 | 0.89853
4.2639 | 0.85954
4.2708 | 0.94466
4.2778 | 0.97515
4.2847 | 0.86746
4.2917 | 0.77963
4.2986 | 0.97706
4.3056 | 0.84223
4.3125 | 0.95733
4.3194 | 0.81552
4.3264 | 0.89286
4.3333 | 0.94774
4.3403 | 1.0283
4.3472 | 0.88228
4.3542 | 1.0898
4.3611 | 1.1088
4.3681 | 1.0964
4.375 | 1.1495
4.3819 | 1.0013
4.3889 | 0.98522
4.3958 | 0.97608
4.4028 | 1.063
4.4097 | 1.0853
4.4167 | 1.1603
4.4236 | 1.107
4.4306 | 1.2784
4.4375 | 1.162
4.4444 | 1.066
4.4514 | 1.2511
4.4583 | 1.1819
4.4653 | 1.1648
4.4722 | 1.2569
4.4792 | 1.3387
4.4861 | 1.3642
4.4931 | 1.2448
4.5 | 1.4342
4.5069 | 1.1547
4.5139 | 1.3353
4.5208 | 1.3211
4.5278 | 1.6131
4.5347 | 1.3235
4.5417 | 1.4215
4.5486 | 1.3531
4.5556 | 1.5196
4.5625 | 1.507
4.5694 | 1.6063
4.5764 | 1.3215
4.5833 | 1.603
4.5903 | 1.4915
4.5972 | 1.6733
4.6042 | 1.5963
4.6111 | 1.4234
4.6181 | 1.6395
4.625 | 1.6584
4.6319 | 1.6285
4.6389 | 1.7224
4.6458 | 1.6801
4.6528 | 1.6197
4.6597 | 1.9735
4.6667 | 1.6793
4.6736 | 1.7539
4.6806 | 1.7023
4.6875 | 1.8641
4.6944 | 1.9438
4.7014 | 1.8337
4.7083 | 2.0274
4.7153 | 1.8391
4.7222 | 1.8481
4.7292 | 1.8164
4.7361 | 1.8784
4.7431 | 1.9578
4.75 | 1.9287
4.7569 | 1.7579
4.7639 | 2.0963
4.7708 | 1.9639
4.7778 | 2.0053
4.7847 | 1.915
4.7917 | 1.9631
4.7986 | 2.1359
4.8056 | 2.0879
4.8125 | 2.2787
4.8194 | 2.0813
4.8264 | 2.2584
4.8333 | 2.1045
4.8403 | 2.1011
4.8472 | 2.0607
4.8542 | 2.2362
4.8611 | 2.2055
4.8681 | 2.1967
4.875 | 2.3658
4.8819 | 2.3167
4.8889 | 2.4402
4.8958 | 2.4692
4.9028 | 2.2797
4.9097 | 2.3953
4.9167 | 2.2831
4.9236 | 2.3579
4.9306 | 2.4328
4.9375 | 2.4309
4.9444 | 2.1829
4.9514 | 2.2572
4.9583 | 2.553
4.9653 | 2.5161
4.9722 | 2.5462
4.9792 | 2.3293
4.9861 | 2.5575
4.9931 | 2.5312
5 | 2.467
5.0069 | 2.3769
5.0139 | 2.5818
5.0208 | 2.7203
5.0278 | 2.6284
5.0347 | 2.4747
5.0417 | 2.6675
5.0486 | 2.515
5.0556 | 2.6516
5.0625 | 2.6177
5.0694 | 2.4919
5.0764 | 2.6463
5.0833 | 2.6514
5.0903 | 2.7071
5.0972 | 2.7733
5.1042 | 2.6389
5.1111 | 2.7095
5.1181 | 2.6098
5.125 | 2.747
5.1319 | 2.7178
5.1389 | 2.7349
5.1458 | 2.4859
5.1528 | 2.8054
5.1597 | 2.7283
5.1667 | 2.8671
5.1736 | 2.6825
5.1806 | 2.7919
5.1875 | 3.0649
5.1944 | 2.767
5.2014 | 2.621
5.2083 | 2.9598
5.2153 | 2.7677
5.2222 | 2.6746
5.2292 | 2.8073
5.2361 | 2.7957
5.2431 | 2.5897
5.25 | 2.7678
5.2569 | 2.773
5.2639 | 2.8801
5.2708 | 2.5362
5.2778 | 2.7501
5.2847 | 2.8121
5.2917 | 2.8072
5.2986 | 2.8201
5.3056 | 2.764
5.3125 | 2.7521
5.3194 | 2.7548
5.3264 | 2.5396
5.3333 | 2.868
5.3403 | 2.7277
5.3472 | 2.5165
5.3542 | 2.7726
5.3611 | 2.7714
5.3681 | 2.7631
5.375 | 2.5425
5.3819 | 2.7393
5.3889 | 2.6298
5.3958 | 2.8108
5.4028 | 2.5823
5.4097 | 2.6043
5.4167 | 2.5123
5.4236 | 2.5517
5.4306 | 2.5965
5.4375 | 2.7125
5.4444 | 2.5832
5.4514 | 2.5712
5.4583 | 2.7447
5.4653 | 2.6453
5.4722 | 2.6678
5.4792 | 2.4868
5.4861 | 2.4051
5.4931 | 2.6853
5.5 | 2.4179
5.5069 | 2.5778
5.5139 | 2.7223
5.5208 | 2.5567
5.5278 | 2.5023
5.5347 | 2.4468
5.5417 | 2.3796
5.5486 | 2.3001
5.5556 | 2.394
5.5625 | 2.4172
5.5694 | 2.277
5.5764 | 2.5152
5.5833 | 2.3939
5.5903 | 2.5175
5.5972 | 2.3686
5.6042 | 2.2887
5.6111 | 2.4126
5.6181 | 2.3062
5.625 | 2.346
5.6319 | 2.3415
5.6389 | 2.2026
5.6458 | 2.3247
5.6528 | 2.1186
5.6597 | 2.2528
5.6667 | 2.1121
5.6736 | 2.2797
5.6806 | 2.0732
5.6875 | 2.2265
5.6944 | 1.9786
5.7014 | 2.1724
5.7083 | 2.1966
5.7153 | 2.2372
5.7222 | 2.0604
5.7292 | 2.044
5.7361 | 1.9897
5.7431 | 2.119
5.75 | 2.0638
5.7569 | 1.9567
5.7639 | 1.9372
5.7708 | 2.0306
5.7778 | 1.9062
5.7847 | 1.7933
5.7917 | 1.7853
5.7986 | 1.9652
5.8056 | 1.8336
5.8125 | 1.8216
5.8194 | 1.7712
5.8264 | 1.6491
5.8333 | 1.7954
5.8403 | 1.7203
5.8472 | 1.6978
5.8542 | 1.6701
5.8611 | 1.5741
5.8681 | 1.3985
5.875 | 1.4092
5.8819 | 1.6012
5.8889 | 1.7203
5.8958 | 1.5784
5.9028 | 1.7222
5.9097 | 1.4971
5.9167 | 1.5258
5.9236 | 1.6782
5.9306 | 1.5425
5.9375 | 1.4337
5.9444 | 1.4385
5.9514 | 1.4709
5.9583 | 1.3813
5.9653 | 1.3441
5.9722 | 1.3042
5.9792 | 1.4156
5.9861 | 1.256
5.9931 | 1.1533
6 | 1.277
6.0069 | 1.4185
6.0139 | 1.3926
6.0208 | 1.2606
6.0278 | 1.1572
6.0347 | 1.2144
6.0417 | 1.3624
6.0486 | 1.2223
6.0556 | 1.3308
6.0625 | 1.2799
6.0694 | 1.1853
6.0764 | 1.2874
6.0833 | 1.1314
6.0903 | 1.0313
6.0972 | 1.2207
6.1042 | 1.1931
6.1111 | 1.1239
6.1181 | 0.9864
6.125 | 1.1874
6.1319 | 1.1784
6.1389 | 1.086
6.1458 | 1.0223
6.1528 | 1.1648
6.1597 | 0.92506
6.1667 | 0.97718
6.1736 | 1.1874
6.1806 | 1.0431
6.1875 | 1.0778
6.1944 | 0.94135
6.2014 | 0.93093
6.2083 | 0.89385
6.2153 | 0.76884
6.2222 | 1.0424
6.2292 | 0.91783
6.2361 | 0.81263
6.2431 | 0.82022
6.25 | 0.80151
6.2569 | 0.70728
6.2639 | 0.86334
6.2708 | 0.72104
6.2778 | 0.75833
6.2847 | 0.89411
6.2917 | 0.63993
6.2986 | 0.98815
6.3056 | 0.75291
6.3125 | 0.84439
6.3194 | 0.8977
6.3264 | 0.8303
6.3333 | 0.60032
6.3403 | 0.8165
6.3472 | 0.7415
6.3542 | 0.6643
6.3611 | 0.76324
6.3681 | 0.78851
6.375 | 0.71774
6.3819 | 0.73398
6.3889 | 0.65211
6.3958 | 0.65588
6.4028 | 0.7851
6.4097 | 0.79419
6.4167 | 0.76177
6.4236 | 0.77305
6.4306 | 0.79835
6.4375 | 0.69481
6.4444 | 0.74253
6.4514 | 0.85129
6.4583 | 0.951
6.4653 | 0.87503
6.4722 | 0.72511
6.4792 | 0.70981
6.4861 | 0.68206
6.4931 | 0.83509
6.5 | 0.67338
6.5069 | 0.89305
6.5139 | 0.88554
6.5208 | 0.79905
6.5278 | 0.76126
6.5347 | 0.67395
6.5417 | 0.82258
6.5486 | 0.83303
6.5556 | 0.78043
6.5625 | 0.86606
6.5694 | 1.0699
6.5764 | 0.89369
6.5833 | 0.91613
6.5903 | 1.0026
6.5972 | 0.82692
6.6042 | 0.7762
6.6111 | 0.97239
6.6181 | 0.85569
6.625 | 0.78447
6.6319 | 0.95436
6.6389 | 0.91673
6.6458 | 0.76613
6.6528 | 1.0335
6.6597 | 0.94903
6.6667 | 1.0952
6.6736 | 0.93863
6.6806 | 0.88231
6.6875 | 1.0771
6.6944 | 0.97509
6.7014 | 1.1657
6.7083 | 1.04
6.7153 | 1.1733
6.7222 | 0.88234
6.7292 | 1.0221
6.7361 | 1.1327
6.7431 | 1.2209
6.75 | 1.2556
6.7569 | 1.2275
6.7639 | 1.2626
6.7708 | 1.2653
6.7778 | 1.0737
6.7847 | 1.1622
6.7917 | 1.1311
6.7986 | 1.2516
6.8056 | 1.2322
6.8125 | 1.0514
6.8194 | 1.2186
6.8264 | 1.2142
6.8333 | 1.2907
6.8403 | 1.2665
6.8472 | 1.384
6.8542 | 1.3874
6.8611 | 1.4538
6.8681 | 1.3521
6.875 | 1.5602
6.8819 | 1.3554
6.8889 | 1.4352
6.8958 | 1.4486
6.9028 | 1.5728
6.9097 | 1.5494
6.9167 | 1.5081
6.9236 | 1.4961
6.9306 | 1.4572
6.9375 | 1.4528
6.9444 | 1.5073
6.9514 | 1.5674
6.9583 | 1.4999
6.9653 | 1.7149
6.9722 | 1.74
6.9792 | 1.6899
6.9861 | 1.7058
6.9931 | 1.6917
7 | 1.8248

## Side flow combiner
Unit overview
Name: | Side flow combiner
Sumo name: | Sideflowcombiner1
Category: | Flow elements
Unit: | Side flow combiner
Type: | Simple side flow combiner
Settings

## Clarifier
Unit overview
Name: | Clarifier
Sumo name: | Clarifier1
Category: | Separators
Unit: | Clarifier
Type: | Volumeless clarifier with fixed effluent solids
Settings
Process settings
Symbol | Name | Value | Unit | Comment
Qsludge,target | Sludge flow | 24000 | m3/d
XTSS,eff,target | Effluent solids | 10 | g/m3
Cost settings
Symbol | Name | Value | Unit | Comment
eTSS,polymer | Polymer dosage rate based on TSS load | 3 | g polymer/kg TSS

## Effluent
Unit overview
Name: | Effluent
Sumo name: | Effluent1
Category: | Flow elements
Unit: | Effluent
Type: | Plant effluent
Settings

## Sludge
Unit overview
Name: | Sludge
Sumo name: | Sludge1
Category: | Flow elements
Unit: | Sludge
Type: | Sludge output
Settings

## Sludge2
Unit overview
Name: | Sludge2
Sumo name: | Sludge2
Category: | Flow elements
Unit: | Sludge
Type: | Sludge output
Settings

## Side flow combiner2
Unit overview
Name: | Side flow combiner2
Sumo name: | Sideflowcombiner2
Category: | Flow elements
Unit: | Side flow combiner
Type: | Simple side flow combiner
Settings

## Pipe1
Unit overview
Name: | Pipe1
Sumo name: | Pipe1
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe2
Unit overview
Name: | Pipe2
Sumo name: | Pipe2
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe3
Unit overview
Name: | Pipe3
Sumo name: | Pipe3
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe4
Unit overview
Name: | Pipe4
Sumo name: | Pipe4
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe5
Unit overview
Name: | Pipe5
Sumo name: | Pipe5
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe6
Unit overview
Name: | Pipe6
Sumo name: | Pipe6
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe7
Unit overview
Name: | Pipe7
Sumo name: | Pipe7
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe8
Unit overview
Name: | Pipe8
Sumo name: | Pipe8
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe9
Unit overview
Name: | Pipe9
Sumo name: | Pipe9
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe10
Unit overview
Name: | Pipe10
Sumo name: | Pipe10
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe11
Unit overview
Name: | Pipe11
Sumo name: | Pipe11
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe12
Unit overview
Name: | Pipe12
Sumo name: | Pipe12
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe13
Unit overview
Name: | Pipe13
Sumo name: | Pipe13
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe14
Unit overview
Name: | Pipe14
Sumo name: | Pipe14
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m

## Pipe15
Unit overview
Name: | Pipe15
Sumo name: | Pipe15
Category: | Other units
Unit: | PipeL
Type: | Pipe
Settings
Pipe details
Symbol | Name | Value | Unit | Comment
na | Parallel Pipes | 1
l | Length | 10 | m | Pipe length
D | Diameter | 600 | mm | mind DN inner diameter
rr | Roughness (k) | 0.15 | mm | Sand roughness
z | Additional zetas | 1.126 |  | Default = Input+Output
lz | Equivalent lenght for local friction | 0 | m | alternative to zeta
hinput | Pipe input level | 0 | m
Δhgeom | Geometric head | 0 | m